## Fire Event Summaries
FireID | Event Date_FES | Disposition_FES | Outside PA | Plant Area | Building | System | Component Group | Component | Voltage | Current Type
1 | 12/12/2006 | Undetermined | No | N/A | Main Transformer or Switch Yard | Switchyard System | Generator | Electric Bus Bar or Bus Duct | 13 KV or greater | AC
2 | 1/5/1999 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
3 | 1/14/1999 | Challenging | No | N/A | Other (Specify in comments) | Hydrogen Supply System | Other |  | N/A | N/A
5 | 5/18/1999 | Not Evaluated | Yes | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) |  | Transformers | Oil‐filled Transformer | AC
6 | 7/13/1999 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
7 | 10/9/1999 | Undetermined (NC‐PC) | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 4KV | AC
8 | 5/7/2000 | Potentially Challenging | No | N/A | Turbine Building | Main Generator Output Power System | Electrical pane | Circuit breaker or other distribu | 13 KV or greater | AC
9 | 1/3/1990 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) | Fire in the Service Building. | Transformers | Dry transformer | 110V | AC
11 | 3/15/1990 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Cable/Wiring | Cable/Wiring | 13 KV or greater | AC
12 | 3/30/1990 | Not Challenging | No | N/A | Control building | Low Voltage Power System, Class 1E | Transformers | Other (Capacitor Voltage, Poten | 480V | AC
13 | 4/10/1990 | Potentially Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) |  | Dry transformer | 4KV | AC
14 | 5/24/1990 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical pane | Circuit breaker or other distribu | 13 KV or greater | AC
15 | 5/27/1990 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
16 | 6/10/1990 | Not Challenging | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  |  | AC
17 | 6/28/1990 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Electric Motor | Fans | 480V | AC
18 | 7/13/1990 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
19 | 8/4/1990 | Challenging | No | N/A | Radwaste Building |  | Dryers
20 | 8/25/1990 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
21 | 9/22/1990 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
22 | 12/3/1990 | Challenging | No | Containment/Drywell | Drywell (BWR) |  |  |  |  | AC
23 | 12/19/1990 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator |  | AC
24 | 12/22/1990 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
25 | 1/11/1991 | Undetermined (NC‐PC) | No | N/A | Turbine Building | General Ventillation Systems | General Ventillation Systems |  |  | AC
26 | 2/14/1991 | Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Cable/Wiring |  | 110V | AC
27 | 1/16/1991 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC
28 | 1/23/1991 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
29 | 2/23/1991 | Potentially Challenging | No | N/A | Turbine Building | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC
30 | 4/29/1991 | Challenging | No | N/A | Turbine Building | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
31 | 6/15/1991 | Undetermined (NC‐PC) | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
32 | 6/27/1991 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
33 | 8/1/1991 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
34 | 8/11/1991 | Potentially Challenging | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
35 | 11/2/1991 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
36 | 11/9/1991 | Not Challenging | Yes | N/A | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC
37 | 11/15/1991 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Crane |  | 13 KV or greater | AC
38 | 3/21/1992 | Challenging | No | Switchgear Room | Reactor Building (BWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC
39 | 5/3/1992 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Air Compressors |  | N/A | N/A
40 | 5/22/1992 | Not Challenging | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  | N/A | N/A
41 | 6/17/1992 | Potentially Challenging | No | Switchgear Room | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 4KV | AC
42 | 7/3/1992 | Potentially Challenging | No |  | Other (Specify in comments) |  | Air Compressors
43 | 7/4/1992 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
44 | 7/13/1992 | Challenging | No | N/A | Turbine Building | Feedwater System | Pump | Turbine‐driven pump | N/A | N/A
45 | 7/29/1992 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical pane | Motor control center | 4KV | AC
46 | 8/4/1992 | Potentially Challenging | No | Battery Room | Control building | DC Power System, class 1E | Electrical pane |  | Other (specify) | DC
47 | 8/10/1992 | Not Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
48 | 9/4/1992 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
49 | 9/15/1992 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC
50 | 11/24/1992 | Potentially Challenging | No | N/A | Turbine Building | Main Generator Output Power System | Bus Duct | IsoPhase Bus Duct | 13 KV or greater | AC
51 | 2/5/1993 | Not Challenging | No | Cable Spreading Room |  | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC
52 | 6/19/1993 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Pumps | Electric motor driven pumps
53 | 7/27/1993 | Not Challenging | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  | N/A
54 | 8/16/1993 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Emergency Onsite Power Supply System | Class 1A emergency generator | 4KV | AC
55 | 10/13/1993 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) | Essential Service Water System | Other |  | N/A | N/A
56 | 10/21/1993 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | 13 KV or greater | AC
57 | 11/2/1993 | Not Challenging | Yes | N/A | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  | 220V | AC
58 | 12/25/1993 | Challenging | No |  | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator | 13 KV or greater | AC
59 | 1/29/1994 | Challenging | No | N/A | Turbine Building
60 | 2/3/1994 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other | N/A | N/A
61 | 4/3/1994 | Challenging | No | N/A | Turbine Building | Main Generator System | Other |  | 13 KV or greater | AC
62 | 6/6/1994 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
63 | 6/15/1994 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
64 | 6/1/1994 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
65 | 7/2/1994 | Challenging | No | N/A | Turbine Building | Main Generator Output Power System | Other |  | 13 KV or greater | AC
66 | 7/11/1994 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps | N/A | N/A
67 | 7/29/1994 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Other |  | N/A | N/A
68 | 8/10/1994 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
69 | 8/29/1994 | Undetermined (NC‐PC) | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC
70 | 10/26/1994 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
71 | 3/1/1995 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
72 | 4/14/1995 | Challenging | No | N/A | Auxiliary Building (PWR) | General Ventillation Systems | Other
73 | 6/1/1995 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System |  |  | N/A | N/A
74 | 6/10/1995 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear | 4KV | AC
75 | 8/22/1995 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Other
76 | 10/21/1995 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
77 | 12/10/1995 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Other |  | N/A | N/A
78 | 1/24/1996 | Challenging | No | N/A | Auxiliary Building (PWR) | Essential Service Water System | Other |  | N/A | N/A
79 | 2/5/1996 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
80 | 2/29/1996 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
81 | 3/25/1996 | Undetermined (NC‐PC) | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  | N/A | N/A
82 | 3/27/1996 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Other |  | N/A | N/A
83 | 4/4/1996 | Potentially Challenging | No | Main Control Room | Control building | Low Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 110V | AC
84 | 4/19/1996 | Potentially Challenging | No | Main Control Room | Radwaste Building | Electrical panel | Electrical panel | Main control board (i.e., the ma | 110V | AC
85 | 5/13/1996 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Air Compressors |  | N/A | N/A
86 | 6/23/1996 | Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
87 | 8/19/1996 | Potentially Challenging | No | N/A | Reactor Building (BWR) | Reactor Core Isolation Cooling System (BWR) | Pumps | Turbine‐driven pump | N/A | N/A
88 | 10/5/1996 | Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
89 | 10/15/1996 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Motor control center | 480V | AC
90 | 10/17/1996 | Challenging | No | Containment/Drywell | Containment (PWR) | Feedwater System | Other |  | N/A | N/A
91 | 11/19/1996 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | Instrument and Uninterruptible Power System |  |  | N/A | N/A
92 | 11/22/1996 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
93 | 3/4/1997 | Potentially Challenging | No | Switchgear Room | Control building | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC
94 | 8/1/1997 | Potentially Challenging | No | N/A | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC
95 | 10/9/1997 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
96 | 10/28/1997 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
97 | 6/10/1998 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC
98 | 10/8/1998 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin | N/A | N/A
99 | 10/10/1998 | Not Challenging | No |  | Radwaste Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC
100 | 5/15/2000 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Bus Duct | Segmented Bus Duct | 13 KV or greater | AC
101 | 9/3/2000 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) |  | Other
102 | 9/4/2000 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
103 | 9/22/2000 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
104 | 10/14/2000 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 480V | AC
105 | 11/10/2000 | Potentially Challenging | No | N/A | Radwaste Building
106 | 2/3/2001 | Challenging | No |  | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC
107 | 3/21/2001 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
108 | 4/6/2001 | Not Challenging | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Other
109 | 4/24/2001 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
110 | 6/25/2001 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
111 | 8/2/2001 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
112 | 8/3/2001 | Undetermined (PC‐CH) | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
113 | 6/12/2002 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC
114 | 8/21/2002 | Challenging | No | N/A | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC
115 | 8/22/2002 | Challenging | No | N/A | Turbine Building | Hydrogen Supply System | Other
116 | 10/3/2002 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
117 | 10/9/2002 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC
118 | 1/15/2003 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
119 | 3/18/2003 | Not Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Electric motor driven pumps | 480V | AC
120 | 4/7/2003 | Potentially Challenging | No | Containment/Drywell | Containment (PWR)
121 | 4/26/2003 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 7KV | AC
122 | 4/29/2003 | Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
123 | 10/16/2003 | Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
124 | 10/28/2003 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Other |  | 13 KV or greater | AC
125 | 1/6/2004 | Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Cable/Wiring |  | 110KV | AC
126 | 5/21/2004 | Undetermined (PC‐CH) | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
127 | 6/18/2004 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
128 | 8/31/2004 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
129 | 11/6/2004 | Potentially Challenging | No | N/A | Turbine Building | Heat Rejection System (Circulating Water) | Other |  | N/A | N/A
130 | 12/14/2004 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
131 | 1/14/2005 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Undetermined (PC‐CH) | Low Voltage Power System (600V and less) |  | N/A | N/A
132 | 3/4/2005 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A
133 | 5/4/2005 | Potentially Challenging | No | Fuel handling area | Containment (PWR) | Reactor Coolant System | Cable/Wiring |  | 110KV | AC
134 | 6/27/2005 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
135 | 8/25/2005 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 7KV | AC
136 | 10/25/2005 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
137 | 10/29/2005 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
138 | 2/11/2006 | Potentially Challenging | No | N/A | Reactor Building (BWR) | General Ventillation Systems | Electric Motor | Fans | 480V | AC
139 | 2/24/2006 | Potentially Challenging | No | Cable vault/tunnel area | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 480V | AC
140 | 3/20/2006 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC
141 | 5/1/2006 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Main Generator Output Power System | Bus Duct | IsoPhase Bus Duct | 13 KV or greater | AC
142 | 5/24/2006 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
143 | 8/15/2006 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4 KV | AC
144 | 10/30/2006 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC
145 | 11/11/2006 | Not Challenging | No | Fuel handling area | Auxiliary Building (PWR) |  | Cable/Wiring |  | 110V | AC
146 | 2/27/2007 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Load center | 480V | AC
147 | 4/5/2007 | Not Challenging | No | N/A | Control building | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 4 KV | AC
148 | 4/6/2007 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
149 | 4/8/2007 | Potentially Challenging | No | Switchgear Room | Radwaste Building | Low Voltage Power System, Class 1E | Transformers | Dry transformer | 110V | AC
150 | 4/25/2007 | Challenging | No | N/A | Other (Specify in comments) | Hydrogen Supply System |  |  | N/A | N/A
151 | 8/1/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 4 KV | AC
152 | 10/23/2007 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Motor control center | N/A | N/A
153 | 8/16/2008 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
154 | 9/20/2008 | Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
155 | 11/17/2008 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
156
157 | 2/1/2009 | Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
158 | 6/26/2009 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Generator | Main turbine generator | N/A | N/A
159 | 1/16/1990 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4 KV | AC
160 | 2/7/2009 | Challenging | No | N/A | Turbine Building | Main Generator Output Power System | Other |  | N/A | N/A
161 | 4/22/2009 | Potentially Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 480V | AC
162 | 8/5/2009 | Challenging | No | N/A | Turbine Building | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 7 KV | AC
163 | 10/12/2009 | Potentially Challenging | No | N/A | Turbine Building
164 | 3/28/1990 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
165
166
167
168 | 11/13/2003 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  |  |  | N/A | N/A
169 | 11/13/2003 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 7 KV | AC
170 | 11/21/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
171
172 | 12/7/2003 | Challenging | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | 480V | AC
173 | 12/13/2003 | Not Challenging | No |  | Control building |  | Electrical panel | Main control board (i.e., the ma
174 | 12/30/2003 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
175 | 11/22/2009 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear | 7 KV | AC
176 | 12/12/2009 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
177
178
179
180
181 | 2/13/1997 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC
182
183
184 | 6/27/1997 | Challenging | No | Battery Room | Control building | DC Power System | Electrical pane | Battery charger | 125VDC | DC
185 | 3/23/1998 | Not Challenging | No | Main Control Room | Control building | General Ventillation Systems | Transformers | Other (Capacitor Voltage, Poten | 110V | AC
186 | 5/14/1998 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Other instrument/control cabin | 110V | AC
187 | 8/16/1999 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Electrical panel | Other instrument/control cabin | 110V | AC
188 | 8/24/1999 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Electrical panel | Motor control center | 480V | AC
189 | 10/14/1996 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | General Ventillation Systems | Electric Motor | Fans
190 | 3/18/1998 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma
191 | 11/11/1998 | Not Challenging | No | Switchgear Room | Auxiliary Building (PWR) |  | Electrical panel | Motor control center
192 | 5/15/1999 | Not Challenging | No | Main Control Room | Control building | Main Turbine System | Electrical panel | Main control board (i.e., the ma
193 | 7/31/1991 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin | 480V | AC
194 | 5/22/1990 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
195 | 3/21/1992 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC
196
197
198
199 | 1/22/1990 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Pumps | Electric motor driven pumps | N/A | N/A
200 | 2/6/1990 | Not Challenging | Yes | N/A | Other (Specify in comments) | Other
201 | 3/8/1990 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps
202 | 3/23/1990 | Potentially Challenging | No | Main Control Room | Radwaste Building | Low Voltage Power System, Class 1E | Electrical panel | Main control board (i.e., the ma | 110V | AC
203 | 4/6/1990 | Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
204 | 4/9/1990 | Not Challenging | No | N/A | Radwaste Building |  | Other |  | 480V | AC
205
206 | 6/11/1990 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | N/A | N/A
207 | 7/15/1990 | Undetermined (PC‐CH) | No | Cable vault/tunnel area | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring
208 | 8/8/1990 | Potentially Challenging | No | N/A | Turbine Building
209 | 8/22/1990 | Not Challenging | Yes | Switchgear Room | Control building | Medium Voltage Power System (601V to 35kV) |  | Motor control center
210 | 10/16/1990 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring
211 | 11/2/1990 | Potentially Challenging | No | N/A | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 480V | AC
212 | 12/5/1990 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other
213
214 | 3/8/1991 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Boilers |  | N/A | N/A
215 | 3/11/1991 | Not Challenging | No |  | Other (Specify in comments)
216 | 7/12/1991 | Potentially Challenging | No | N/A |  | General Ventillation Systems | Cable/Wiring
217 | 7/19/1991 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps | N/A | N/A
218 | 9/12/1991 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Turbine Lube Oil System | Lube Oil |  | 480V | AC
219 | 9/27/1991 | Undetermined (PC‐CH) | No | N/A | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
220 | 10/20/1991 | Potentially Challenging | No | Battery Room | Other (Specify in comments) | DC Power System | Transformers | Other (Capacitor Voltage, Poten | 480V | AC
221 | 10/23/1991 | Not Challenging | No | N/A | Control building | Medium Voltage Power System, Class 1E | Transformers | Other (Capacitor Voltage, Poten | 480V | AC
222 | 2/1/1992 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Low Voltage Power System (600V and less) | Other |  | 110V | AC
223 | 3/3/1992 | Not Challenging | No | Switchgear Room |  | Instrument and Uninterruptible Power System | Electrical panel | Inverter
224 | 3/8/1992 | Undetermined (NC‐PC) | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC
225 | 3/23/1992 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
226 | 4/17/1992 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
227 | 6/9/1992 | Not Challenging | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps
228 | 8/14/1992 | Potentially Challenging | No | N/A | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps | 250VDC | DC
229 | 8/21/1992 | Challenging | No |  | Auxiliary Building (PWR)
230 | 8/31/1992 | Potentially Challenging | No |  | Reactor Building (BWR) | Offgas System (BWR) | Other
231 | 10/22/1992 | Potentially Challenging | No |  | Turbine Building
232 | 10/27/1992 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard
233 | 11/29/1992 | Potentially Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans | 480V | AC
234 | 12/16/1992 | Not Challenging | No | Fuel handling area | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
235 | 12/30/1992 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electric Motor | Fans | 480V | AC
236 | 1/6/1993 | Undetermined (NC‐PC) | No | Main Control Room | Control building |  | Other
237 | 3/19/1993 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
238 | 4/1/1993 | Potentially Challenging | No | N/A | Auxiliary Building (PWR)
239 | 7/14/1993 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Other |  | N/A | N/A
240 | 7/19/1993 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) |  |  |  | N/A | N/A
241 | 11/3/1993 | Potentially Challenging | No | Containment/Drywell | Drywell (BWR)
242 | 11/13/1993 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Diesel Fuel Oil System | Boilers | Auxiliary or Heating Boiler
243 | 12/1/1993 | Potentially Challenging | No | Containment/Drywell | Drywell (BWR)
244 | 12/7/1993 | Undetermined (PC‐CH) | No | N/A | Turbine Building
245 | 12/16/1993 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump
246 | 1/12/1994 | Challenging | No | N/A | Auxiliary Building (PWR)
247 | 1/12/1994 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Auxiliary/Emergency Feedwater System (PWR) | Pumps | Electric motor driven pumps | N/A | N/A
248 | 3/5/1994 | Undetermined (PC‐CH) | No | N/A | Turbine Building
249 | 3/7/1994 | Undetermined (PC‐CH) | No | N/A | Auxiliary Building (PWR) |  | Electric Motor | Fans
250 | 7/19/1994 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
251 | 10/11/1994 | Potentially Challenging | No | Switchgear Room |  | Medium Voltage Power System (601V to 35kV) | Transformers | Dry transformer | 4 KV | AC
252 | 3/18/1995 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | Cable/Wiring
253 | 7/6/1995 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear
254 | 9/25/1995 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
255 | 11/19/1995 | Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Transformers | Dry transformer
256 | 7/22/1996 | Undetermined (NC‐PC) | No |  |  |  | Cable/Wiring
257 | 10/22/1997 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Inverter
258 | 11/3/1997 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Turbine Lube Oil System | Lube Oil |  | N/A | N/A
259 | 12/26/1997 | Potentially Challenging | No | N/A | Control building |  | Other
260 | 2/3/1998 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps
261 | 5/11/1998 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4 KV | AC
262 | 2/19/1999 | Undetermined (PC‐CH) | No |  | Turbine Building |  | Air Compressors
263 | 4/25/1999 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps
264 | 10/20/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR)
265 | 9/23/2006 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other |  | N/A | N/A
266 | 11/9/2006 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
267 | 6/1/2000 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments)
268 | 4/7/2000 | Not Challenging | No | N/A | Turbine Building
269 | 12/12/2000 | Potentially Challenging | No | Fuel handling area | Other (Specify in comments) |  | Other |  | N/A | N/A
270 | 11/18/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
271 | 10/5/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
272 | 4/17/2004 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
273 | 5/10/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
274 | 5/7/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
275 | 10/14/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
276 | 11/2/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
277 | 11/2/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
278 | 1/5/2004 | Not Challenging | No | Battery Room |  | DC Power System | Electrical panel | Battery charger | 125VDC | DC
279
280 | 11/19/2005 | Not Challenging | No | Containment/Drywell |  |  | Other |  | N/A | N/A
281
282 | 4/23/2001 | Not Challenging | Yes | N/A |  |  | Other |  | N/A | N/A
283 | 11/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
284 | 11/29/2005 | Not Challenging | No | Containment/Drywell |  |  | Other |  | N/A | N/A
285 | 12/9/2005 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A
286 | 4/20/2006 | Not Challenging | No
287 | 8/10/2006 | Not Challenging | Yes | N/A |  |  | Other |  | N/A | N/A
288 | 10/10/2006 | Potentially Challenging | No | N/A |  |  | Pumps | Other instrument/control cabin | 110V | AC
289 | 5/28/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
290 | 8/22/2007 | Not Challenging | Yes | N/A |  |  | Other |  | N/A | N/A
291
292 | 10/8/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
293 | 10/14/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
294 | 10/13/2007 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
295 | 10/22/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
296 | 10/30/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
297 | 11/30/2007 | Not Challenging | No
298 | 12/16/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
299 | 3/4/2008 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
300 |  | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
301
302 | 12/21/1999 | Not Challenging | No | N/A |  |  | Crane
303 | 3/1/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 480V | AC
304
305 | 6/21/2001 | Not Challenging | No | N/A | Main Control Room
306 | 1/24/2002 | Not Challenging | No |  |  |  | Cable/Wiring
307 | 10/17/2002 | Not Challenging | No |  |  | Hydrogen Supply System | Other
308 | 10/14/2005 | Potentially Challenging | No | N/A | Turbine Building | Condensate System
309 | 10/23/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other
310 | 11/18/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
311 | 12/1/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR)
312 | 10/29/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
313 | 11/9/2008 | Not Challenging | No | N/A | Turbine Building |  | Other
314 | 2/10/2000 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin
315
316 | 8/17/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
317 | 9/27/2003 | Not Challenging | No | N/A |  |  | Other
318 | 10/5/2000 | Potentially Challenging | No | N/A | Containment (PWR) |  | Other
319 | 10/5/2000 | Potentially Challenging | No |  |  |  | Other
320 | 10/24/2000 | Potentially Challenging | No | N/A |  |  | Electrical panel | Circuit breaker or other distribu
321 | 10/31/2000 | Not Challenging | No | N/A | Radwaste Building |  | Batteries |  | Other (specify) | AC
322 | 3/8/2001 | Not Challenging | No
323
324 | 1/12/2005 | Not Challenging | No |  | Turbine Building | Main Turbine System
325 | 3/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR)
326 | 3/25/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR)
327 | 1/1/2006 | Not Challenging | No |  |  | High Pressure Safety Injection System (PWR) | Pumps
328 | 9/24/2006 | Not Challenging | No
329 | 9/25/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
330 | 9/27/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR)
331
332 | 4/15/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
333 | 5/11/2007 | Potentially Challenging | No | N/A | Diesel Generator Building | Diesel Fuel Oil System | Generator | Class 1A emergency generator | 4KV | AC
334
335 | 8/3/2007 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
336
337 | 8/18/2005 | Not Challenging | No | N/A | Diesel Generator Building |  | Other |  | N/A | N/A
338 | 7/25/2007 | Not Challenging | No | Fuel handling area | Other (Specify in comments)
339
340 | 8/7/2009 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC
341 | 2/18/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Electrical panel |  | 480V | AC
342 | 11/4/2006 | Not Challenging | No
343 | 11/4/2006 | Not Challenging | No | Containment/Drywell |  |  | Other |  | N/A | N/A
344 | 10/26/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
345 | 4/25/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
346 | 3/1/2002 | Potentially Challenging | No | N/A | Turbine Building |  | Electric Motor | Other (specify in comments) | 480V | AC
347
348
349 | 4/5/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | Other (specify) | AC
350 | 7/11/2002 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | Other (specify) | stea
351 | 9/26/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
352 | 2/28/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
353 | 1/21/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
354 | 10/1/2005 | Not Challenging | No | N/A |  |  | Electric Motor
355 | 3/7/2006 | Not Challenging | No |  |  | Closed/Component Cooling Water | Electrical panel
356 | 4/19/2006 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans | 480V | AC
357 | 1/10/2007 | Not Challenging | No |  | Other (Specify in comments) |  |  | Other
358 | 5/2/2007 | Not Challenging | No | N/A |  | General Ventillation Systems | Pumps |  | 480V | AC
359 | 3/6/2001 | Not Challenging | No |  |  |  | Electrical panel | Inverter
360 | 7/25/2001 | Not Challenging | No
361 | 2/4/2002 | Not Challenging | No
362 | 4/16/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Air Compressors
363 | 5/27/2003 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Electric Motor | Elevator motor
364 | 10/3/2003 | Not Challenging | No |  |  |  | Cable/Wiring
365 | 8/7/2004 | Not Challenging | Yes | N/A |  |  | Other
366 | 1/25/2006 | Not Challenging | No
367 | 10/12/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
368 | 10/24/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
369
370
371
372 | 9/8/2009 | Not Challenging | No
373 | 10/5/2009 | Not Challenging | No
374 | 10/13/2009 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  |  |  | N/A | N/A
375 | 10/16/2009 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Non Essential Service Water System | Pumps | Electric motor driven pumps | 480V | AC
376 | 6/5/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
377 | 8/27/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
378 | 6/24/2002 | Not Challenging | No | N/A | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps
379 | 10/2/2009 | Not Challenging | No | Containment/Drywell | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps
380 | 10/29/2004 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu | 600V | AC
381 | 3/6/2005 | Potentially Challenging | No | N/A | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
382
383
384 | 3/23/2007 | Not Challenging | No | N/A | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC
385 | 4/14/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers |  | 13 KV or greater | AC
386 | 6/3/2008 | Not Challenging | No | N/A | Turbine Building | General Ventillation Systems | Other |  | N/A | N/A
387 | 7/24/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps | N/A | N/A
388 | 7/25/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers |  | 13 KV or greater | AC
389 | 10/17/2004 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 110V | AC
390 | 10/29/2007 | Not Challenging | No | N/A | Radwaste Building | Reactor Recirculation System (BWR) | Cable/Wiring |  | Other (specify) | DC
391
392 | 10/30/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
393 | 10/30/2004 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A
394 | 2/11/2000 | Not Challenging | No | Containment/Drywell | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 480V | AC
395
396
397 | 5/2/2000 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
398 | 7/7/2000 | Not Challenging | No | N/A | Turbine Building
399 | 12/24/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
400 | 3/28/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
401 | 6/13/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Elevator motor
402
403
404 | 6/12/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) | 480V | AC
405 | 8/13/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
406 | 6/12/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
407 | 12/1/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
408 | 6/1/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten
409 | 9/21/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
410 | 7/25/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC
411 | 3/8/2001 | Potentially Challenging | No | Cable vault/tunnel area | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 480V | AC
412 | 7/15/2009 | Not Challenging | No | N/A | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC
413
414
415
416 | 10/11/2000 | Not Challenging | No | N/A | Turbine Building | Other
417
418 | 10/8/2000 | Not Challenging | No
419 | 4/5/2005 | Not Challenging | No
420 | 6/24/2001 | Undetermined (NC‐PC) | No |  |  |  | Pumps | Electric motor driven pumps
421 | 7/1/2002 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | N/A | N/A
422 | 3/7/2003 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 480V | AC
423 | 6/23/2003 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Fans
424 | 3/10/2005 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) |  | Cable/Wiring
425
426 | 9/17/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
427 | 2/3/2003 | Not Challenging | No
428 | 9/14/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
429 | 3/12/2007 | Not Challenging | No |  |  |  | Other
430 | 10/10/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR)
431 | 4/3/2000 | Not Challenging | No
432
433
434
435
436 | 11/21/2000 | Not Challenging | Yes | N/A |  |  | Other |  | N/A | N/A
437 | 2/3/2001 | Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC
438 | 6/24/2001 | Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
439 | 10/2/2002 | Not Challenging | Yes | N/A | Turbine Building |  | Batteries
440 | 1/2/2003 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
441 | 11/23/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
442 | 2/4/2004 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
443 | 3/3/2004 | Undetermined (NC‐PC) | No | N/A |  |  | Other |  | N/A | N/A
444 | 6/28/2004 | Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
445 | 8/30/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A
446 | 10/5/2004 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
447 | 10/8/2004 | Not Challenging | No | N/A |  |  | Other |  | 110V | AC
448 | 11/17/2004 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
449 | 12/8/2004 | Not Challenging | No | N/A | Radwaste Building |  | Other
450 | 12/13/2004 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
451 | 12/13/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
452 | 12/18/2004 | Not Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps
453 | 6/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
454 | 6/4/2005 | Not Challenging | No | N/A |  |  | Electrical panel | Other instrument/control cabin
455 | 6/6/2005 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
456 | 7/7/2005 | Not Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps
457 | 2/17/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
458 | 5/4/2006 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
459 | 5/10/2006 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
460 | 9/7/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Crane motor
461 | 10/12/2006 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
462 | 10/18/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
463 | 11/1/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
464 | 12/8/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
465 | 1/31/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
466 | 2/2/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
467 | 2/13/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
468 | 2/20/2007 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
469 | 3/19/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | Other (specify) | AC
470 | 6/29/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
471 | 7/10/2007 | Not Challenging | No | N/A |  |  | Electric Motor | Elevator motor
472 | 7/17/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
473 | 8/4/2007 | Potentially Challenging | No | Battery Room |  | Low Voltage Power System (600V and less) | Other |  | 250VDC | DC
474 | 8/21/2007 | Potentially Challenging | No | Switchgear Room |  |  | Electrical panel | Other instrument/control cabin
475 | 9/27/2007 | Potentially Challenging | No | N/A |  |  | Air Compressors
476 | 12/6/2007 | Not Challenging | No | N/A |  |  | Other
477 | 2/23/2008 | Not Challenging | No | N/A |  |  | Electrical panel | Inverter
478 | 3/30/2008 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Circuit breaker or other distribu
479 | 3/17/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Other
480 | 4/7/2000 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
481 | 6/29/2000 | Not Challenging | No | N/A | Radwaste Building |  | Other |  | N/A | N/A
482 | 2/8/2000 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
483 | 11/9/2000 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans
484 | 11/8/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
485 | 9/14/2001 | Not Challenging | No | N/A | Radwaste Building |  | Other |  | N/A | N/A
486 | 8/27/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
487 | 1/13/2001 | Not Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps
488 | 10/16/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
489
490
491 | 4/12/2000 | Undetermined (NC‐PC) | No
492 | 10/19/2000 | Undetermined (NC‐PC) | No
493
494 | 3/8/2000 | Undetermined (NC‐PC) | No |  |  |  | Air Compressors
495 | 3/20/2003 | Undetermined (NC‐PC) | No | Main Control Room | Control building
496 | 5/19/2002 | Undetermined (NC‐PC) | No |  |  |  | Boilers
497 | 8/14/2003 | Not Challenging | No
498 | 12/19/2000 | Undetermined (PC‐CH) | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps
499 | 12/17/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
500 | 3/12/2001 | Undetermined (PC‐CH) | No |  |  |  | Electrical panel | Circuit breaker or other distribu
501 | 1/24/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
502 | 11/18/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring
503 | 5/14/2002 | Not Challenging | No | N/A | Containment (PWR) |  | Electrical panel | Other instrument/control cabin
504 | 10/9/2002 | Undetermined (PC‐CH) | No | N/A | Turbine Building
505 | 9/13/2003 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Circuit breaker or other distribu
506 | 9/12/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
507
508 | 3/14/2005 | Not Challenging | No | N/A | Containment (PWR) |  | Cable/Wiring
509 | 1/19/2005 | Potentially Challenging | No | N/A | Other (Specify in comments)
510 | 7/16/2005
511 | 7/16/2005 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
512 | 7/20/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  |  |  | 24‐48VDC | DC
513 | 11/18/2005 | Undetermined (NC‐PC) | No |  |  |  | Other
514 | 4/27/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Transformers
515 | 10/5/2005 | Undetermined (PC‐CH) | No | N/A | Auxiliary Building (PWR) |  | Air Compressors
516 | 10/25/2005 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Transformers | Dry transformer | 4KV | AC
517 | 3/23/2006 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) |  | Electrical panel | Inverter
518 | 3/30/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | MG set
519 | 5/4/2007 | Undetermined (NC‐PC) | No |  |  |  | Other
520 | 6/6/2006 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Inverter
521 | 12/17/2007 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu
522 | 9/19/2006 | Not Challenging | No | N/A | Turbine Building |  | Crane
523 | 9/27/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
524 | 10/11/2006 | Not Challenging | No | N/A |  |  | Other
525
526 | 1/30/2009 | Undetermined (NC‐PC) | No |  |  |  | Pumps
527 | 11/10/2009 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | N/A | N/A
528
529 | 11/28/2008 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Other instrument/control cabin | 125VDC | DC
530 | 3/5/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
531 | 8/24/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
532
533 | 1/27/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
534 | 4/10/2000 | Not Challenging | No |  |  |  | Electrical panel | Motor control center
535 | 6/16/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
536 | 8/24/2000 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Pumps
537 | 10/13/2000 | Not Challenging | No |  |  | Feedwater System | Other |  | N/A | N/A
538 | 10/20/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
539 | 10/23/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps
540 | 10/23/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Air Compressors
541 | 10/24/2000 | Not Challenging | No |  |  |  | Pumps | Diesel driven pumps
542 | 3/4/2000 | Not Challenging | No | N/A | Turbine Building | Main Generator System | Electric Motor |  | 480V | AC
543 | 8/27/2001 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
544 | 12/13/2001 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments)
545 | 6/5/2002 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
546 | 10/9/2002 | Not Challenging | No |  |  | DC Power System | Electrical panel | Battery charger
547 | 11/5/2002 | Not Challenging | No |  |  | Feedwater System | Pumps
548 | 11/13/2002 | Not Challenging | No |  |  | Feedwater System | Pumps
549 | 7/16/2004 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin
550 | 2/2/2005 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) |  | Cable/Wiring
551 | 2/2/2005 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
552 | 7/31/2003 | Not Challenging | No |  |  | General Ventillation Systems | Pumps | Electric motor driven pumps
553 | 6/24/2004 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
554 | 6/2/2005 | Undetermined (NC‐PC) | No
555 | 7/27/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | Other (specify) | AC
556 | 10/14/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments)
557 | 11/2/2005 | Not Challenging | No |  |  |  | Other
558 | 12/13/2005 | Potentially Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans
559 | 9/12/2006 | Undetermined (NC‐PC) | No |  |  |  | Electric Motor
560 | 5/20/2006 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
561 | 1/3/2005 | Not Challenging | No | N/A | Other (Specify in comments)
562 | 10/9/2006 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Feedwater System | Other | Other (specify in comments)
563 | 10/18/2006 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
564 | 3/13/2007 | Not Challenging | No | N/A | Radwaste Building |  | Electrical panel | Other (specify in comments)
565 | 4/25/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
566 | 7/2/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
567 | 7/31/2007 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
568 | 1/12/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
569 | 5/15/2008 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments)
570 | 6/3/2008 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 13 KV or greater | AC
571 | 9/29/2008 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments)
572 | 12/23/2008 | Undetermined (NC‐PC) | No |  |  |  | Other
573 | 1/29/2009 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 480V | AC
574
575 | 5/18/2009 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other
576 | 8/31/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
577 | 9/16/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts
578 | 11/8/2003 | Not Challenging | No |  |  | General Ventillation Systems | Other
579 | 3/23/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
580 | 1/6/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
581 | 4/17/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
582 | 9/3/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 480V | AC
583
584 | 10/8/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
585 | 12/10/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 220V | AC
586 | 5/5/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Outlets |  | 110V | AC
587 | 5/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) | N/A | N/A
588 | 11/30/2006 | Challenging | No | N/A | Control building | Low Voltage Power System (600V and less) | Electrical panel | Switchgear | 480V | AC
589
590 | 2/20/2005 | Not Challenging | No | Switchgear Room | Other (Specify in comments) |  | Electrical panel | Switchgear | 4KV | AC
591 | 7/19/2006 | Potentially Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu
592 | 6/11/2009 | Undetermined (NC‐PC) | No |  |  |  | Other
593 | 10/16/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
594 | 1/28/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
595 | 2/13/2000 | Undetermined (NC‐PC) | No |  |  |  | Other |  | N/A | N/A
596 | 6/13/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
597 | 7/22/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
598 | 10/12/2000 | Undetermined (NC‐PC) | No |  |  |  | Other |  | N/A | N/A
599 |  | Not Challenging | No |  |  |  | Other |  | N/A | N/A
600 | 1/17/2004 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu
601 | 10/28/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
602 | 9/29/2006 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
603 | 11/14/2007 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Other (specify in comments)
604 | 9/8/2000 | Not Challenging | No |  |  |  | Electric Motor | Other (specify in comments)
605 | 9/14/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
606 | 10/31/2006 | Potentially Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps
607 | 11/13/2008 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
608
609 |  | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10273 | 10/18/2000 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 125VDC | DC
10274 | 10/21/2000 | Not Challenging | No | N/A | Other (Specify in comments) | Transformers | Other (Capacitor Voltage, Poten
10275
10276 | 12/15/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 480V | AC
10277 | 12/22/2000 | Not Challenging | No | N/A | Service Water Pump house | General Ventillation Systems | Electric Motor | Fans
10278 | 4/4/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10279 | 4/14/2001 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10280 | 4/17/2001 | Not Challenging | No | Fuel handling area | Containment (PWR) |  | Electrical panel | Other instrument/control cabin | 480V | AC
10281
10282 | 8/12/2001 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Other
10283 | 2/10/2004 | Not Challenging | No |  |  |  | Electric Motor | Motor operated valve
10284 | 3/10/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10285 | 4/7/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10286 | 5/10/2004 | Potentially Challenging | No | N/A | Turbine Building |  | Other
10287 | 5/19/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
10288 | 5/22/2004 | Not Challenging | No | N/A | Turbine Building |  | Other
10289 | 5/28/2004 | Not Challenging | No | N/A | Turbine Building |  | Other
10290 | 6/3/2004 | Not Challenging | No | N/A | Turbine Building |  | Other
10291 | 9/18/2004 | Undetermined (PC‐CH) | No | N/A | Control building | Low Voltage Power System (600V and less) | Other
10292 | 1/13/2005 | Not Challenging | No | N/A | Turbine Building |  | Other | Other instrument/control cabin
10293 | 8/16/2005 | Not Challenging | No | N/A | Other (Specify in comments)
10294 | 10/9/2005 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Other
10295 | 10/18/2005 | Not Challenging | No | N/A | Containment (PWR) |  | Other
10296 | 8/21/2008 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Circuit breaker or other distribu | 480V | AC
10297 | 12/14/2008 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma
10298 | 2/12/2009 | Not Challenging | No | N/A | Service Water Pump house |  | Electric Motor | Other (specify in comments)
10299 | 2/19/2009 | Not Challenging | No | N/A | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator
10300 | 6/25/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
10301
10302 | 3/10/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
10303 | 5/18/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
10304 | 4/8/2001 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other
10305 | 10/25/2001 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments)
10306
10307 | 10/3/2003 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Lube Oil
10308 | 9/19/2004 | Not Challenging | Yes | N/A | Containment (PWR) |  | Crane
10309 | 4/18/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10310 | 1/29/2007 | Not Challenging | No | N/A |  |  | Electrical panel | Other instrument/control cabin | 110V | AC
10311 | 1/9/2008 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring
10312 | 2/9/2009 | Not Challenging | No | Fuel handling area | Radwaste Building |  | Electrical panel | Circuit breaker or other distribu
10313 | 4/3/2009 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
10314
10315 | 10/18/2002 | Not Challenging | Yes | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
10316 | 11/22/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10317 | 9/23/2004 | Not Challenging | No | N/A | Containment (PWR) |  |  |  | N/A | N/A
10318 | 10/16/2004 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10319 | 1/7/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC
10320 | 5/25/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10321 | 6/1/2005 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10322 | 12/10/2005 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Other
10323 | 12/11/2005 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments)
10324 | 12/30/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10325
10326 | 1/24/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Electrical panel | Other instrument/control cabin
10327 | 6/21/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | Other (specify) | AC
10328 | 7/17/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10329 | 9/22/2008 | Not Challenging | Yes | N/A | Auxiliary Building (PWR) |  | Other
10330 | 9/23/2008 | Not Challenging | No | N/A | Turbine Building |  |  |  | N/A | N/A
10331 | 3/24/2009 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10332
10333
10334 | 3/30/2000 | Undetermined (NC‐PC) | No | N/A | Containment (PWR) |  | Electrical panel | Other instrument/control cabin
10335
10336 | 10/2/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
10337 | 10/11/2000 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Lighting Ballasts
10338 | 9/13/2001 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 600V | AC
10339 | 8/16/2004 | Not Challenging | No |  | Main Transformer or Switch Yard |  | Transformers |  | Other (specify) | AC
10340
10341 | 5/21/2005 | Not Challenging | No | N/A |  | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | N/A | N/A
10342
609 |  | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10343 | 8/25/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  |  |  | 110V | AC
10344 | 10/1/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10345 | 1/25/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
10349 | 9/24/2007 | Not Challenging | : No | N/A | Containment (PWR) |  | Other
10350 | 1/21/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | 110V | : AC
10352 | 12/11/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 480V | : AC
10353 | 1/5/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
10354 | 7/2/2009 | Not Challenging | : No | N/A | Diesel Generator Building |  | Other
10355 | 4/26/2008 | Potentially Challenging | : No | N/A | Other (Specify in comments) | Feedwater System | Other |  | N/A | N/A
10356 | 10/3/2007 | Potentially Challenging | : No | N/A | Auxiliary Building (PWR) | General Ventillation Systems | Pumps | Electric motor driven pumps
10357 | 7/1/2005 | Potentially Challenging | : No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps
10358 | 7/3/2002 | Potentially Challenging | : No |  |  | Instrument and Uninterruptible Power System | Electrical panel | : Inverter | Other (specify) | N/A
10359 | 11/16/2000 | Potentially Challenging | : No | N/A | : Other (Specify in comments) |  | Other |  | N/A | N/A
10360 | 10/13/2000 | Undetermined (NC‐PC) | : No | N/A | Turbine Building |  | Other |  | N/A | N/A
10361 | 5/5/2005 | Potentially Challenging | : No | N/A | Containment (PWR) |  | Cable/Wiring |  | N/A | N/A
10362 | 10/28/2006 | Potentially Challenging | : No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
10363 | 11/5/2009 | Potentially Challenging | : No | N/A | Containment (PWR) |  | Cable/Wiring |  | Other (specify) | AC
10364 | 6/30/2005 | Potentially Challenging | : No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps
10365 | 8/22/2008 | Undetermined (NC‐PC) | : No | N/A | Other (Specify in comments)
10367 | 10/22/2000 | Potentially Challenging | : No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10368 | 6/28/2004 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10369 | 10/4/2002 | Potentially Challenging | No | N/A | Potentially Challenging |  | Electrical panel | Other (specify in comments)
10370 | 4/11/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Other
10371 | 10/20/2009 | Not Challenging | No |  | Turbine Building | Feedwater System | Other
10372 | 10/22/2009 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Other
10373 | 4/14/2005 | Potentially Challenging | No | N/A | Turbine Building | Non Essential Service Water System | Other
10374 | 7/11/2003 | Potentially Challenging | No | N/A | Radwaste Building |  | Other
10376 | 3/23/2004 | Challenging | No | N/A | Other (Specify in comments) |  | Other
10377 | 3/10/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10378 | 3/18/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Wall Mounted or Sealed
10379 | 3/22/2000 | Not Challenging | No | N/A | Turbine Building | Condensate System | Other |  | 480V | AC
10380 | 9/23/2000 | Not Challenging | No | N/A | Control building | DC Power System, class 1E | Other |  | 125VDC | DC
10381 | 10/24/2000 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel |  | 600V | AC
10382 | 3/20/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 220V | AC
10383 | 4/3/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 110V | AC
10384 | 6/26/2001 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Lube Oil |  | 125VDC | DC
10385 | 2/12/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Circuit breaker or other distribu
10386 | 3/1/2003 | Undetermined (NC‐PC) | No | N/A | Radwaste Building |  | Crane
10387 | 3/4/2003 | Not Challenging | No | Battery Room | Control building | DC Power System, class 1E | Electrical panel |  | 250VDC | DC
10389 | 9/8/2003 | Potentially Challenging | No | Main Control Room | Diesel Generator Building | Medium Voltage Power System (601V to 35kV) | Electrical panel |  | 4KV | AC
10390
10391
10392 | 4/5/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
10393 | 11/7/2004 | Not Challenging | No |  | Radwaste Building |  | Other | Other instrument/control cabin
10394 | 2/22/2005 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Other (specify in comments) | 110V | AC
10395 | 7/13/2005 | Not Challenging | No | Switchgear Room | Diesel Generator Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
10396 | 7/14/2005 | Not Challenging | No |  | Turbine Building | Closed/Component Cooling Water | Pumps | Electric motor driven pumps
10397 | 10/12/2005 | Potentially Challenging | No | N/A | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electric Motor | Fans | 600V | AC
10398
10399 | 1/31/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other
10400
10401 | 5/9/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | Other instrument/control cabin
10402 | 6/27/2006 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
10403 | 10/31/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other
10404 | 12/5/2006 | Not Challenging | No |  | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Generator | Other generator (specify in com
10405 | 1/20/2007 | Not Challenging | No |  | Turbine Building | Main Generator System | Generator | Main turbine generator
10406 | 5/5/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) |  | Other | Other (specify) | AC
10407 | 6/3/2007 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Main control board (i.e., the ma | 110V | AC
10408
10409 | 12/12/2007 | Not Challenging | No | N/A | Other (Specify in comments) | Offgas System (BWR) | Electrical panel | Circuit breaker or other distribu | 600V | AC
10410 | 2/13/2008 | Not Challenging | No | N/A | Control building | DC Power System, class 1E | Batteries
10411 | 3/8/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring |  | Other (specify) | AC
10412 | 2/17/2009 | Not Challenging | No | N/A | Reactor Building (BWR) |  |  |  | 250VDC | DC
10413 | 5/17/2009 | Not Challenging | No |  | Radwaste Building |  | Electrical panel | Other instrument/control cabin
10414 | 8/31/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring |  | 110V | AC
10415
10416 | 4/1/2007 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin
10417 | 4/17/2007 | Not Challenging | No |  | Turbine Building | Condensate System | Electrical panel | Wall Mounted or Sealed
10418 | 2/15/2008 | Not Challenging | Yes |  | Main Transformer or Switch Yard |  | Other
10419 | 4/12/2008 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring
10420 | 4/17/2008 | Not Challenging | No | Battery Room | Control building |  | Electric Motor
10421 | 6/20/2008 | Not Challenging | No |  | Turbine Building |  | Other
10422 | 8/25/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10423 | 9/3/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other
10424 | 10/19/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10425 | 11/6/2009 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other
10426 | 4/29/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10427 | 5/3/2001 | Not Challenging | No |  | Turbine Building |  | Other
10428 | 6/1/2000 | Not Challenging | No |  |  |  | Other
10429 | 9/21/2002 | Not Challenging | No |  | Containment (PWR) |  | Other
10430 | 12/21/2000 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
10431
10432 | 10/22/2003 | Not Challenging | No | N/A |  |  | Other
10433 | 12/10/2003 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
10434 | 5/7/2004 | Not Challenging | No | N/A | Turbine Building |  | Crane
10435 | 7/8/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10436 | 8/11/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10437 | 5/9/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10438
10439
10440
10441 | 3/4/2009 | Potentially Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10442 | 3/9/2009 | Potentially Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10443 | 7/25/2009 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
10444 | 10/13/2009 | Not Challenging | No | N/A | Turbine Building |  | Other
10445 | 2/7/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
10446 | 4/11/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
10447 | 3/9/2000 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Generator | Other generator (specify in com
10448 | 10/23/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans | 480V | AC
10449 | 5/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10450 | 6/19/2001 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10451 | 6/5/2001 | Not Challenging | No |  | Turbine Building |  | Pumps | Electric motor driven pumps
10452 | 9/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps | N/A | N/A
10453 | 11/20/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
10454 | 2/17/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans
10455 | 3/22/2002 | Not Challenging | No | N/A | Turbine Building |  | Electric Motor | Fans
10456 | 7/19/2002 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
10457 | 10/22/2002 | Undetermined (NC‐PC) | No | N/A | Containment (PWR) |  | Other
10458 | 1/7/2003 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Switchyard System | Cable/Wiring |  | N/A | N/A
10459 | 2/7/2003 | Potentially Challenging | No | N/A | Containment (PWR) |  | Electric Motor | Other (specify in comments)
10460 | 4/9/2003 | Not Challenging | No |  | Turbine Building | Feedwater System | Other
10461 | 3/6/2003 | Not Challenging | No | N/A | Containment (PWR) |  | Electric Motor | Crane motor | N/A | N/A
10462 | 2/5/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps
10463 | 3/1/2004 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
10464 | 3/30/2005 | Challenging | No | N/A | Other (Specify in comments) |  | Other
10465 | 9/30/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) | N/A | N/A
10466 | 8/31/2005 | Potentially Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
10467 | 4/7/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10468 | 10/27/2005 | Not Challenging | No |  | Radwaste Building |  | Other
10469 | 3/23/2006 | Not Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) |  | Electrical panel | Other instrument/control cabin
10470 | 5/5/2006 | Not Challenging | No | N/A | Turbine Building |  | Other
10471 | 12/26/2007 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Other (specify in comments)
10472 | 9/25/2007 | Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC
10473 | 1/23/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10474 | 2/23/2007 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Other |  | N/A | N/A
10475
10476 | 4/10/2007 | Potentially Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Other (specify in comments) | N/A | N/A
10477 | 6/7/2007 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
10478 | 7/10/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) | 110V | AC
10479 | 7/23/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
10480 | 7/23/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other
10481
10482 | 10/22/2006 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Pumps | Electric motor driven pumps | 480V | AC
10483 | 4/10/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | Other (specify) | AC
10484 | 4/16/2007 | Not Challenging | No | N/A | Turbine Building | Main Generator System | Other
10485 | 4/21/2007 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Circuit breaker or other distribu
10486 | 7/28/2007 | Not Challenging | No | N/A | Turbine Building |  | Other
10487 | 9/4/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10488 | 9/24/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10489 | 4/6/2008 | Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10490 | 4/9/2008 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10491 | 4/29/2008 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10492 | 9/30/2008 | Potentially Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel |  | 480V | AC
10493 | 10/23/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring
10494
10495
10496 | 5/14/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel
10497 | 7/31/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10498 | 9/26/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10499 | 10/16/2009 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
10500
10501
10502
10503
10504 | 3/15/2000 | Not Challenging | No | N/A | Turbine Building |  | Other
10505 | 3/16/2000 | Not Challenging | No | N/A | Turbine Building |  | Other
10506
10507 | 3/14/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10508 | 3/28/2001 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
10509 | 4/1/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10510 | 4/10/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10511
10512 | 6/22/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 110V | AC
10513 | 8/20/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10514 | 8/26/2001 | Potentially Challenging | No | N/A | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator | N/A | N/A
10515 | 9/30/2001 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10516 | 11/20/2001 | Potentially Challenging | No | N/A | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  | N/A | N/A
10517 | 8/5/2002 | Not Challenging | No | N/A | Diesel Generator Building | Lube Oil System | Generator | Class 1A emergency generator | N/A | N/A
10518 | 8/26/2002 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other
10519 | 9/25/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10520 | 11/26/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10521 | 9/10/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10522 | 11/2/2003 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10523 | 11/9/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10524 | 1/7/2004 | Potentially Challenging | No | N/A | Diesel Generator Buildin | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10525 | 5/10/2004 | Not Challenging | No | N/A | Diesel Generator Buildin | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10526 | 5/30/2004 | Not Challenging | No | N/A | Diesel Generator Buildin | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10527
10528 | 9/8/2004 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma | N/A | N/A
10529 | 1/25/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10530 | 3/15/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10531 | 3/31/2006 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Circuit breaker or other distribu
10532 | 6/28/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A
10533 | 2/1/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  |  |  | N/A | N/A
10534 | 3/21/2001 | Not Challenging | No | N/A | Turbine Building |  |  |  | N/A | N/A
10535 | 3/31/2002 | Not Challenging | No | N/A | Turbine Building
10536 | 12/12/2002 | Not Challenging | No | N/A | Drywell (BWR) |  |  |  | N/A | N/A
10537 | 2/17/2003 | Not Challenging | No | N/A | Drywell (BWR)
10538 | 4/1/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10539 | 1/19/2004 | Not Challenging | No | N/A | Turbine Building |  | Other
10540 | 2/4/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10541 | 3/24/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10542 | 7/9/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10543 | 9/3/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10544 | 1/17/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  |  |  | N/A | N/A
10545 | 5/9/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | N/A | N/A
10546 | 3/15/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10547 | 1/22/2004 | Not Challenging | No
10548 | 6/25/2003 | Not Challenging | No | N/A | Drywell (BWR) |  | Other
10549 | 10/8/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10550 | 9/3/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10551 | 7/14/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10552 | 7/8/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10553 | 4/17/2000 | Not Challenging | No | N/A | Turbine Building |  |  |  | N/A | N/A
10554 | 5/3/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10555 | 5/5/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Cable/Wiring |  | N/A | N/A
10556 | 5/11/2004 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10557 | 1/13/2005 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
10558 | 1/19/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Air Compressors |  | N/A | N/A
10559 | 3/7/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10560 | 3/29/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10561 | 4/4/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10562 | 5/23/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10563 | 7/11/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10564 | 8/10/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10565 | 8/15/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10566 | 9/15/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10567 | 12/19/2005 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
10568 | 1/12/2006 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10569 | 2/8/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10570 | 2/13/2006 | Not Challenging | No | N/A | Turbine Building |  |  |  | N/A | N/A
10571 | 3/5/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10572 | 4/13/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Outlets |  | N/A | N/A
10573 | 7/5/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10574 | 7/17/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10575 | 7/18/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10576 | 7/26/2006 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard | Main Generator Hydrogen Cooling System | Other |  | N/A | N/A
10577 | 10/28/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin | Other (specify) | AC
10578
10579 | 4/4/2008 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10580 | 4/26/2008 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10581 | 11/19/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10582 | 12/9/2005 | Undetermined (NC‐PC) | No | Containment/Drywell | Reactor Building (BWR) |  | Other |  | N/A | N/A
10583 | 9/1/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10584 | 7/27/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring |  | Other (specify) | AC
10585 | 4/24/2003 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electric Motor | Other (specify in comments) | N/A | N/A
10586 | 1/19/2000 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Electric Motor | Fans | N/A | N/A
10587 | 8/10/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10588 | 11/21/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10589 | 2/3/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10590 | 10/3/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10591 | 10/8/2002 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Transformers |  | N/A | N/A
10592 | 1/7/2003 | Not Challenging | No | N/A | Reactor Building (BWR) | DC Power System | Cable/Wiring |  | 24‐48VDC | DC
10593 | 7/7/2003 | Not Challenging | No | N/A | Turbine Building | Main Generator System | Electrical panel | Relay rack | N/A | N/A
10594 | 1/25/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Motor control center
10595 | 2/11/2004 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Core Isolation Cooling System (BWR) | Other |  | N/A
10596 | 11/4/2004 | Not Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans | N/A
10597
10598 | 1/3/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A
10599 | 3/25/2006 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 125VDC
10600 | 2/18/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A
10601 | 2/16/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A
10602 | 2/13/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A
10603
10604 | 5/14/2001 | Potentially Challenging | No | N/A | Turbine Building | Main Turbine System | Lube Oil |  | N/A
10605 | 1/31/2006 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans | N/A
10606 | 5/6/2004 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A
10607 | 12/27/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A
10608 |  |  | No | N/A |  |  |  |  | N/A
10609 | 9/7/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A
10610
10611 | 8/20/2009 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) | High Pressure Safety Injection System (PWR) | Pumps
10612
10613
10614 | 2/25/2004 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
10615 | 10/15/2005 | Undetermined (NC‐PC) | No
10616
10617 | 2/14/2003 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps | N/A | N/A
10618 | 2/15/2000 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Dryers |  | 480V | AC
10619 | 5/24/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | 480V | AC
10620 | 8/9/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 220V | AC
10621 | 8/22/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10622 | 6/25/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10623 | 8/8/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring |  | N/A | N/A
10624 | 10/26/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Oil‐filled Transformer | 110V | AC
10625 | 9/28/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers |  | N/A | N/A
10626 | 12/11/2002 | Potentially Challenging | No | N/A | Service Water Pump house |  | Pumps | Electric motor driven pumps | 480V | AC
10627 | 12/12/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10628 | 12/30/2005 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Low Voltage Power System, Class 1E | Cable/Wiring |  | 110V | AC
10629
10630 | 6/6/2007 | Potentially Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Air Compressors |  | N/A | N/A
10631 | 11/28/2001 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
10632 | 3/3/2000 | Challenging | No | N/A | Diesel Generator Building | DC Power System, class 1E | Transformers | Dry transformer | 4KV | AC
10633 | 3/7/2000 | Potentially Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
10634
10635
10636 | 9/26/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10637
10638 | 3/5/2001 | Potentially Challenging | No | N/A | Turbine Building |  | Other
10639 | 2/16/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  |  |  | N/A | N/A
10640
10641 | 3/11/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) | Reactor Recirculation System (BWR) | Electrical panel | Relay rack
10642 | 3/14/2002 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10643 | 5/22/2002 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Air Compressors |  | Other (specify) | AC
10644 | 11/3/2002 | Potentially Challenging | No | N/A | Control building |  | Inverter
10645 | 4/11/2003 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Electric Motor | Other (specify in comments) | 480V | AC
10646 | 7/17/2003 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
10647 | 8/22/2003 | Potentially Challenging | No | N/A | Reactor Building (BWR) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC
10648 | 3/12/2004 | Potentially Challenging | No | N/A | Turbine Building |  | Electrical panel | Other instrument/control cabin
10649 | 3/15/2004 | Potentially Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
10650 | 3/20/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 480V | AC
10651
10652 | 3/10/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10653 | 4/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Motor control center
10654 | 2/5/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10655
10656 | 2/22/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Fans
10657 | 6/29/2009 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps | N/A | N/A
10658 | 12/29/2009 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Electrical panel
10659
10660 | 11/6/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10661
10662
10663
10664 | 10/2/2000 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10665 | 11/3/2000 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10666 | 4/18/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10667 | 4/26/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10668 | 4/22/2001 | Not Challenging | No | N/A | Turbine Building |  | Other
10669 | 5/20/2001 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps
10670 | 6/1/2001 | Not Challenging | No | N/A | Control building |  | Electric Motor | Fans | N/A | N/A
10671 | 6/21/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | High Pressure Core Spray System (BWR) | Pumps | Turbine‐driven pump | N/A | N/A
10672 | 6/26/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A
10673 | 9/4/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Lube Oil |  | N/A | N/A
10674 | 12/5/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
10675 | 12/31/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans
10676 | 3/29/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10677 | 4/4/2003 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
10678 | 5/29/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10679 | 1/9/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10680 | 7/10/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10681 | 11/12/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10682 | 4/2/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10683 | 4/5/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10684 | 4/6/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10685 | 4/11/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10686 | 4/13/2005 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10687 | 5/4/2005 | Not Challenging | No
10688 | 10/31/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10689 | 1/26/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10690 | 2/9/2007 | Not Challenging | No | Cable vault/tunnel area | Other (Specify in comments) | Feedwater System | Other |  | N/A | N/A
10691 | 2/25/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Other generator (specify in com
10692
10693 | 3/4/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10694 | 7/10/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
10695 | 7/27/2007 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | 110V | AC
10696 | 8/30/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10697 | 2/25/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10698 | 4/18/2008 | Not Challenging | No | N/A | Radwaste Building |  | Other |  | 110V | AC
10699 | 4/24/2008 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
10700 | 7/18/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10701 | 8/25/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10702 | 2/8/2009 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Electric bus bar or bus duct
10703 | 11/21/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring
10704 | 3/28/2002 | Not Challenging | No | N/A | Reactor Building (BWR) | High Pressure Core Spray System (BWR) | Pumps | Turbine‐driven pump
10705 | 12/3/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10706 | 12/4/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10707 | 8/8/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10708 | 9/22/2004 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10709 | 2/1/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | DC Power System | Electrical panel | Battery charger | 125VDC | DC
10710 | 11/21/2005 | Not Challenging | No | N/A | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator | N/A | N/A
10711 | 1/8/2006 | Not Challenging | No | N/A | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator | N/A | N/A
10712 | 10/8/2006 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10713 | 3/25/2007 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10714
10715 | 2/5/2009 | Potentially Challenging | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps
10716 | 7/26/2009 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10717 | 4/12/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Fans
10718 | 5/20/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10719 | 6/1/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10720 | 4/8/2006 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Main turbine generator | N/A | N/A
10721 | 8/26/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10722 | 9/3/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10723 | 10/4/2007 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Main turbine generator | N/A | N/A
10724 | 10/7/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10725 | 10/29/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10726 | 11/4/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10727 | 2/5/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
10728 | 8/23/2009 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
10729 | 4/3/2009 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A
10730 | 3/16/2006 | Not Challenging | No | N/A | Containment (PWR) |  | Electric Motor | Other (specify in comments)
10731 | 6/27/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10732 | 4/22/2002 | Not Challenging | No |  | Containment (PWR) |  | Other
10733 | 4/7/2003 | Not Challenging | No | N/A | Turbine Building | Cable Raceway System | Cable/Wiring
10734 | 4/27/2004 | Not Challenging | No | N/A | Turbine Building | Main Generator Hydrogen Cooling System | Other
10735 | 4/28/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
10736 | 12/6/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10737 | 11/30/2006 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Other instrument/control cabin
10738 | 8/22/2001 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Feedwater System | Other
10739 | 4/24/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10740 | 10/8/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other
10741 | 9/21/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Crane |  | N/A | N/A
10742 | 4/11/2004 | Not Challenging | No | N/A | Not Challenging |  | Pumps | Electric motor driven pumps | 480V
10743 | 4/19/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin | 480V | AC
10744 | 8/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
10745 | 7/25/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Fans
10746 | 5/12/2000 | Not Challenging | No | N/A | Control building | Instrument and Uninterruptible Power System, Class 1E | Electrical panel | Other instrument/control cabin | 480V | AC
10747 | 1/15/1999 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
10748 | 5/29/2003 | Not Challenging | No |  |  |  | Electric Motor
10749 | 9/10/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
10750 | 2/28/2009 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Cable/Wiring |  | 480V | AC
10751 | 1/28/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
20264 | 1/19/1990 | Undetermined(NC‐PC) | No | N/A | Turbine Building |  | Electrical panel | Motor control center
20265 | 2/2/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | N/A | N/A
20266 | 2/19/1990 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR)
20267 | 3/12/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electrical panel | Motor control center
20268 | 4/19/1990 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure |  | Electrical panel | Motor control center
20269 | 4/30/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu
20270 | 6/7/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Motor control center
20271 | 7/9/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Transformers | Dry transformer
20272 | 9/10/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electrical panel | Relay rack
20273 | 9/18/1990 | Potentially Challenging | No | Switchgear Room |  |  | Electrical panel | Circuit breaker or other distribu
20274 | 10/9/1990 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor | MG set
20275 | 10/11/1990 | Undetermined (NC‐PC) | No |  |  |  | Electrical panel | Motor control center
20276 | 10/12/1990 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Reactor Coolant System | Electrical panel | Circuit breaker or other distribu
20277 | 11/16/1990 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR)
20278 | 11/24/1990 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Fans
20279 | 11/28/1990 | Undetermined (NC‐PC) | No |  |  |  | Transformers | Dry transformer | 480V | AC
20280 | 12/5/1990 | Undetermined (PC‐CH) | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
20281 | 6/24/1991 | Undetermined (NC‐PC) | No
20282 | 9/17/1991 | Undetermined (NC‐PC) | No |  |  |  | Electrical panel | Motor control center
20283 | 10/3/1991 | Undetermined (NC‐PC) | No | N/A | Radwaste Building |  | Electric Motor
20284 | 10/14/1991 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Bus Duct | Other | 4KV | AC
20285 | 10/25/1991 | Not Challenging | No | N/A | Turbine Building |  | Other
20286 | 1/23/1992 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers |  | 13 KV or greater | AC
20287 | 2/29/1992 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electrical panel | Motor control center
20288 | 3/9/1992 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR)
20289 | 3/16/1992 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR)
20290 | 4/26/1992 | Not Challenging | No
20291 | 4/28/1992 | Potentially Challenging | No | N/A | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC
20292 | 6/25/1992 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator
20293 | 9/1/1992 | Undetermined (NC‐PC) | No | N/A | Turbine Building
20294 | 10/5/1992 | Undetermined (NC‐PC) | No |  | Other (Specify in comments)
20295 | 10/12/1992 | Undetermined (NC‐PC) | No | N/A | Radwaste Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
20296 | 10/23/1992 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR)
20297 | 11/17/1992 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR)
20298 | 1/11/1993 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electric Motor | Elevator motor
20299 | 3/9/1993 | Not Challenging | No | N/A |  |  | Other
20300 | 3/30/1993 | Undetermined (NC‐PC) | No | N/A | Turbine Building
20301 | 4/13/1993 | Undetermined (NC‐PC) | No | N/A | Turbine Building
20302 | 7/25/1993 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electrical panel | Motor control center
20303 | 10/14/1993 | Potentially Challenging | No | N/A | Diesel Generator Building |  | Other
20304 | 11/2/1993 | Potentially Challenging | No | N/A | Reactor Building (BWR) | General Ventillation Systems
20305 | 11/18/1993 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten
20306 | 12/30/1993 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR)
20307 | 1/25/1994 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other
20308 | 3/9/1994 | Undetermined (NC‐PC) | No |  | Turbine Building
20309 | 3/11/1994 | Not Challenging | Yes |  | Turbine Building |  | Other |  | N/A | N/A
20310 | 3/26/1994 | Undetermined (NC‐PC) | No | Containment/Drywell | Reactor Building (BWR)
20311 | 4/4/1994 | Undetermined (NC‐PC) | No | Containment/Drywell
20312 | 7/27/1994 | Undetermined (NC‐PC) | No
20313 | 9/29/1994 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Boilers
20314 | 12/19/1994 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electric Motor | Other (specify in comments)
20315 | 2/20/1995 | Not Challenging | No | N/A | Turbine Building |  | Other
20316 | 2/24/1995 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
20317 | 4/10/1995 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR)
20318 | 8/9/1995 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
20319 | 8/15/1995 | Undetermined (NC‐PC) | No | N/A | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC
20320 | 3/21/1996 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps
20321 | 7/10/1996 | Not Challenging | Yes |  | Turbine Building |  | Pumps | Electric motor driven pumps
20322 | 9/13/1996 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Feedwater System | Lube Oil | Turbine‐driven pump | N/A | N/A
20323 | 1/8/1997 | Challenging | No | N/A | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC
20324 | 8/12/1997 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure | General Ventillation Systems | Electric Motor | Fans | 480V | AC
20325 | 1/16/1998 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure |  | Cable/Wiring
20326 | 10/12/1998 | Undetermined (NC‐PC) | No | N/A | Turbine Building
20327 | 11/2/1998 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin | 4KV | AC
20328 | 5/6/1999 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR) |  | Electrical panel | Circuit breaker or other distribu
20329 | 9/1/1999 | Undetermined (NC‐PC) | No | Switchgear Room |  |  | Electrical panel | Circuit breaker or other distribu
20330 | 10/3/1999 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
20331 | 11/4/1999 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
20332 | 12/14/1999 | Not Challenging | No | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Electric Motor | Fans
20333 | 1/12/1990 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
20334 | 2/20/1990 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
20335 | 4/13/1990 | Not Challenging | No | N/A | Turbine Building
20336 | 2/14/1991 | Undetermined (NC‐PC) | No |  | Other (Specify in comments)
20337 | 4/21/1991 | Undetermined (NC‐PC) | No | N/A | Turbine Building
20338 | 10/11/1991 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | High Pressure Safety Injection System (PWR) | Pumps | Electric motor driven pumps
20339
20340 | 12/1/1992 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR)
20341 | 3/31/1993 | Undetermined (NC‐PC) | No
20342 | 4/30/1993 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR)
20343 | 8/13/1993 | Not Challenging | No | N/A | Reactor Building (BWR)
20344 | 2/20/1994 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electric Motor
20345 | 3/28/1994 | Not Challenging | No | N/A | Turbine Building
20346 | 3/30/1994 | Undetermined (NC‐PC) | No | Switchgear Room | Other (Specify in comments) |  | Electrical panel | Switchgear
20347 | 4/15/1994 | Not Challenging | No | N/A | Turbine Building
20348 | 4/16/1994 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR)
20349 | 4/23/1994 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
20350 | 6/9/1994 | Undetermined (NC‐PC) | No | Fuel handling area | Reactor Building (BWR) |  | Crane
20351 | 6/21/1994 | Undetermined (NC‐PC) | No | Main Control Room | Radwaste Building |  | Electrical panel | Main control board (i.e., the ma
20352 | 6/23/1994 | Potentially Challenging | No | N/A | Main Transformer or Switch Yard |  | Transformers | Oil‐filled Transformer
20353 | 7/13/1994 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Air Compressors |  | 480V | AC
20354 | 10/8/1994 | Not Challenging | Yes | N/A | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  | 110V | AC
20355 | 10/31/1994 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin
20356 | 2/19/1995 | Potentially Challenging | No | N/A | Turbine Building |  | Electrical panel | Circuit breaker or other distribu
20357 | 5/24/1995 | Potentially Challenging | No | N/A | Turbine Building |  | Electrical panel | Motor control center
20358 | 1/23/1996 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | Instrument and Uninterruptible Power System | Air Compressors |  | 600V | AC
20359 | 3/3/1996 | Potentially Challenging | No | N/A | Turbine Building |  | Air Compressors
20360 | 5/25/1996 | Undetermined (PC‐CH) | No | N/A | Turbine Building |  | Transformers | Other (Capacitor Voltage, Poten
20361 | 1/7/1997 | Undetermined (NC‐PC) | No | Fuel handling area | Other (Specify in comments)
20362 | 3/2/1997 | Potentially Challenging | No | N/A | Turbine Building | Electrical panel | Motor control center
20363 | 7/27/1997 | Not Evaluated | No | N/A | Auxiliary Building (PWR) |  | Junction Boxes
20364 | 12/4/1997 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Elevator motor | 220V | AC
20365 | 1/13/1998 | Potentially Challenging | No | N/A | Radwaste Building | Offgas System (BWR)
20366 | 2/6/1998 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
20367 | 2/24/1998 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Diesel driven pumps
20368 | 6/7/1998 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | Instrument and Uninterruptible Power System | Air Compressors |  | 600V | AC
20369 | 6/14/1998 | Potentially Challenging | No | Potentially Challenging |  |  | Transformers | Other (Capacitor Voltage, Poten | 4KV | AC
20370 | 7/1/1998 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure |  | Transformers | Other (Capacitor Voltage, Poten
20371 | 9/9/1998 | Undetermined (NC‐PC) | No | N/A | Radwaste Building | Offgas System (BWR) |  |  | N/A | N/A
20372 | 11/23/1998 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) | Electric Motor | Fans |  | 480V | AC
20373 | 3/16/1999 | Potentially Challenging | No |  | Turbine Building
20374 | 3/19/1999 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans | 600V
20375 | 3/29/1999 | Not Challenging | No |  | Turbine Building
20376 | 7/29/1999 | Not Challenging | No | N/A | Other (Specify in comments)
20377 | 2/8/2000 | Challenging | No |  | Other (Specify in comments)
20378 | 2/25/2000 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
20379 | 6/20/2000 | Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Transformers | Dry transformer | 4KV | AC
20380 | 8/16/2000 | Potentially Challenging | No | N/A | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC
20381 | 10/17/2000 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR)
20382 | 10/23/2000 | Potentially Challenging | No | N/A | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear
20383 | 11/5/2000 | Undetermined (NC‐PC) | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 110V | AC
20384
20385 | 12/27/2000 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Main Turbine System | Pumps | Electric motor driven pumps
30265 | 8/5/2008 | Not Challenging | No |  | Service Water Pump house |  | Pumps | Diesel driven pumps
30266 | 1/20/2009 | Potentially Challenging | No |  | Turbine Building |  | Electric Motor | Fans
30267
30268 | 8/9/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other
30269 | 8/14/2002 | Not Challenging | No |  | Reactor Building (BWR) | General Ventillation Systems | Electric Motor | Fans
30270 | 3/16/2003 | Potentially Challenging | No |  | Turbine Building |  | Other
30271 | 9/11/2003 | Undetermined (PC‐CH) | No |  | Turbine Building | Feedwater System | Lube Oil
30272
30273
30274 | 7/9/2004 | Not Challenging | Yes |  | Other (Specify in comments)
30275 | 1/13/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers
30276 | 7/24/2006 | Potentially Challenging | No | Main Control Room | Control building |  | Electrical panel | Other instrument/control cabin
30277 | 12/3/2007 | Potentially Challenging | No |  | Turbine Building |  | Other
30278 | 10/15/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A
30279 | 5/12/2002 | Not Challenging | No |  | Turbine Building |  | Other
30280
30281 | 6/5/2008 | Potentially Challenging | No | Main Control Room | Control building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | Other (specify) | AC
30282 | 11/26/2001 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Cable/Wiring
30283 | 3/20/2002 | Potentially Challenging | No |  | Diesel Generator Building |  | Generator | Class 1A emergency generator | N/A | N/A
30284 | 3/12/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring
30285 | 11/2/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other
30286 | 6/18/2009 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other
30287 | 10/1/2009 | Potentially Challenging | No |  | Turbine Building |  | Other
30288 | 4/14/2000 | Not Challenging | No |  | Containment (PWR) |  | Other
30289 | 7/8/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30290 | 1/20/2001 | Not Challenging | No |  | Turbine Building | Feedwater System | Other
30291 | 3/14/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers
30292 | 6/17/2001 | Not Challenging | Yes |  |  |  | Cable/Wiring
30293 | 8/20/2001 | Not Challenging | No |  |  |  | Electrical panel
30294 | 11/7/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30295 | 3/15/2002 | Not Challenging | No |  |  |  | Other
30296 | 11/22/2002 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring
30297 | 8/7/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30298 | 4/13/2006 | Not Challenging | No | N/A | Turbine Building |  | Other
30299 | 4/25/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Pumps
30300 | 5/13/2006 | Not Challenging | No |  | Containment (PWR) |  | Other
30301 | 6/7/2006 | Not Challenging | Yes |  |  | General Ventillation Systems | Electric Motor | Fans
30302 | 1/26/2007 | Potentially Challenging | No | N/A | Turbine Building |  | Electric Motor | Other (specify in comments)
30303 | 6/8/2007 | Not Challenging | No | Cable Spreading Room | Control building | Instrument and Uninterruptible Power System, Class 1E | Electrical panel | Inverter | 110V | AC
30304 | 11/29/2007 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring
30305 | 12/14/2007 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Cable/Wiring
30306 | 1/17/2009 | Not Challenging | No |  |  |  | Other
30307 | 3/27/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu
30308 | 4/3/2001 | Not Challenging | No
30309 | 7/21/2001 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Pumps | Electric motor driven pumps
30310 | 9/7/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Pumps
30311 | 9/24/2001 | Not Challenging | No |  | Turbine Building | Feedwater System | Other
30312 | 3/29/2003 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 7KV | AC
30313 | 11/5/2007 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other
30314 | 12/19/2001 | Undetermined (PC‐CH) | No | N/A | Auxiliary Building (PWR) |  | Cable/Wiring
30315
30316 | 3/16/2003 | Not Challenging | Yes |  |  | General Ventillation Systems | Electric Motor | Fans
30317 | 4/18/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30318 | 5/16/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Pumps
30319 | 7/18/2005 | Not Challenging | No |  | Turbine Building
30320 | 5/8/2008 | Not Challenging | No |  | Turbine Building |  | Other
30321 | 11/21/2008 | Not Challenging | No
30322 | 10/28/2006 | Potentially Challenging | No | N/A |  | Lube Oil System | Lube Oil |  | 480V | AC
30323 | 12/9/2006 | Not Challenging | No | N/A |  | General Ventillation Systems | Pumps | Electric motor driven pumps | 480V | AC
30324 | 1/11/2007 | Potentially Challenging | No | N/A |  | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 220V | AC
30325 | 11/6/2007 | Not Challenging | No | N/A |  | Essential Service Water System | Other |  | N/A | N/A
30326 | 5/1/2008 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
30327 | 3/6/2009 | Potentially Challenging | No | N/A |  | Heat Rejection System (Circulating Water) | Pumps |  | 480V | AC
30328
30329
30330 | 4/30/2000 | Potentially Challenging | No | N/A | Turbine Building | Lube Oil System | Lube Oil |  | 480V | AC
30331 | 10/12/2000 | Not Challenging | No | N/A |  | Turbine Lube Oil System | Lube Oil |  | 481V | AC
30332 | 4/6/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Other |  | 13 KV or greater | AC
30333 | 7/31/2003 | Undetermined (PC‐CH) | No | N/A |  | Condensate System | Other |  | N/A | N/A
30334 | 9/27/2003 | Not Challenging | No | N/A |  |  |  |  | 480V | AC
30335 | 1/24/2004 | Not Challenging | No | Main Control Room | Control building | DC Power System, class 1E | Electrical panel | Other instrument/control cabin | 125VDC | DC
30336
30337
30338 | 3/30/2006 | Undetermined (NC‐PC) | No | N/A |  | Condensate System | Electrical panel | Other instrument/control cabin | 110V | AC
30339 | 6/21/2000 | Not Challenging | No | Cable Spreading Room |  |  | Transformers
30340 | 11/10/2000 | Potentially Challenging | No | N/A | Turbine Building |  | Air Compressors |  | 24‐48VDC | DC
30341 | 1/2/2001 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electric Motor |  | 220V | AC
30342 | 2/11/2002 | Undetermined (NC‐PC) | No | Fuel handling area | Auxiliary Building (PWR) |  | Crane |  | 480V | AC
30343 | 5/3/2002 | Not Challenging | No | N/A | Turbine Building |  | Other
30344 | 1/23/2003 | Potentially Challenging | No | N/A | Turbine Building |  | Air Compressors |  | 480V | AC
30345 | 8/29/2003 | Not Challenging | No
30346 | 10/22/2003 | Not Challenging | No | Cable vault/tunnel area | Turbine Building |  | Other
30347 | 3/27/2009 | Not Challenging | No
30348 | 11/22/2004 | Not Challenging | No | N/A | Turbine Building |  | Lube Oil
30349
30350 | 7/26/2004 | Potentially Challenging | No | N/A | Turbine Building |  | Other
30351 | 5/14/2005 | Not Challenging | No | N/A | Turbine Building |  | Other
30352
30353
30354 | 2/8/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel |  | 4KV | AC
30355 | 2/17/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Inverter | 110V | AC
30356 | 11/21/2006 | Not Challenging | No | N/A | Turbine Building | Condensate System | Other
30357 | 6/20/2007 | Undetermined (NC‐PC) | No | N/A | Control building |  | Other
30358 | 8/2/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 480V | AC
30359 | 1/10/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30360 | 4/21/2008 | Not Challenging | No |  | Other (Specify in comments)
30361 | 4/11/2001 | Potentially Challenging | No | N/A | Turbine Building |  | Other | Other instrument/control cabin | 110V | AC
30362 | 12/16/2001 | Potentially Challenging | No | N/A |  | Essential Service Water System | Pumps |  | 4KV | AC
30363 | 5/5/2003 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Cable/Wiring |  |  | 110V | AC
30364 | 5/26/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30365 | 9/8/2003 | Not Challenging | No | N/A |  |  | Other
30366 | 12/2/2003 | Not Challenging | No | N/A |  |  | Other
30367 | 3/30/2004 | Not Challenging | No | N/A
30368 | 7/6/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
30369 | 10/29/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30370 | 10/31/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30371 | 11/8/2005 | Not Challenging | Yes | [5 empty] | N/A | N/A
30372 | 11/18/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30373 | 11/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30374 | 11/30/2005 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Other
30375 | 5/9/2007 | Not Challenging | No |  |  |  | Pumps
30376 | 10/14/2007 | Not Challenging | No
30377 | 11/3/2007 | Not Challenging | No
30378 | 11/6/2007 | Not Challenging | No
30379 | 11/16/2007 | Not Challenging | No | Containment/Drywell |  |  | Other
30380 | 12/17/2007 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
30381 | 4/7/2008 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | 110V | AC
30382 | 5/21/2009 | Not Challenging | No
30383 | 2/11/2009 | Not Challenging | Yes
30384 | 10/18/2000 | Not Challenging | No
30385 | 10/27/2000 | Potentially Challenging | No | N/A | Turbine Building
30386 | 5/11/2001 | Potentially Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu | 4KV | AC
30387 | 5/24/2001 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
30388 | 4/6/2002 | Potentially Challenging | No
30389 | 10/18/2005 | Not Challenging | No
30390 | 5/7/2008 | Potentially Challenging | No |  | Containment (PWR)
30391 | 11/13/2009 | Not Challenging | No
30392 | 3/20/2000 | Undetermined (NC‐PC) | No | Containment/Drywell | Other (Specify in comments) |  | Other
30393 | 3/24/2000 | Undetermined (NC‐PC) | No | Containment/Drywell | Other (Specify in comments) |  | Cable/Wiring |  | 110V
30394 | 2/2/2003 | Potentially Challenging | No | N/A | Reactor Building (BWR) | General Ventillation Systems | Electric Motor
30395 | 3/21/2004 | Undetermined (PC‐CH) | No |  | Turbine Building
30396 | 3/22/2009 | Not Challenging | No | N/A | Turbine Building | Lube Oil System | Lube Oil
30397 | 4/4/2009 | Not Challenging | No | N/A | Turbine Building |  |  |  | N/A
30398 | 10/17/2006 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Cable/Wiring |  | N/A | N/A
30399
30400 | 9/18/2007 | Not Challenging | Yes |  |  |  | Other
30401 | 2/6/2008 | Not Challenging | Yes |  |  |  | Other
30402 | 4/29/2008 | Not Challenging | No | N/A | Turbine Building | Condensate System | Cable/Wiring |  | 480V | AC
30403 | 9/24/2009 | Not Challenging | No | N/A | Turbine Building | Condensate System | Other |  | N/A | N/A
30404 | 4/21/2009 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comment | Hydrogen Supply System | Other
30405 | 10/26/2009 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments)
30406
30407 | 4/30/2002 | Potentially Challenging | No | N/A | Containment (PWR) |  | Cable/Wiring
30408 | 3/19/2001 | Potentially Challenging | No | N/A | Turbine Building |  | Other
30409 | 8/21/2000 | Potentially Challenging | No |  | Main Transformer or Switch Yard |  | Electrical panel | Circuit breaker or other distribu
30410 | 10/25/2000 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps
30411 | 3/28/2000 | Not Challenging | No | N/A | Turbine Building |  | Other
30412 | 4/25/2002 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring
30413 | 4/25/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30414 | 3/28/2002 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
30415 | 4/29/2002 | Not Challenging | No | Containment/Drywell | Other (Specify in comments) |  | Cable/Wiring
30416 | 4/29/2002 | Not Challenging | No | N/A | Turbine Building |  | Other
30417 | 3/20/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30418 | 2/19/2002 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Batteries
30419 | 10/4/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30420 | 3/18/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR)
30421 | 3/5/2002 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
30422 | 11/27/2001 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps
30423 | 3/17/2001 | Not Challenging | No | N/A | Turbine Building |  | Pumps
30424 | 4/11/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC
30425 | 10/7/2002 | Potentially Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
30426 | 10/31/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30427
30428
30429 | 5/6/2004 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps
30430 | 1/13/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC
30431 | 6/18/2006 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
30432
30433 | 6/2/2007 | Not Challenging | No |  |  |  |  | Other
30434 | 8/12/2007 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
30435 | 8/16/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Other
30436 | 9/30/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
30437 | 10/6/2000 | Potentially Challenging | No | Containment/Drywell |  |  | Transformers
30438 | 5/15/2007 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other
30439 | 3/21/2008 | Undetermined (NC‐PC) | No | N/A | Auxiliary Building (PWR) | Auxiliary/Emergency Feedwater System (PWR) | Pumps |  | N/A | N/A
30440 | 10/26/2005 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | Emergency Onsite Power Supply System | Other |  | N/A | N/A
30441 | 9/5/2001 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps |  | N/A | N/A
30442 | 9/5/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30443 | 12/31/2001 | Not Challenging | No
30444 | 3/13/2002 | Not Challenging | No | N/A | Turbine Building |  | Other
30445 | 10/18/2002 | Not Challenging | No |  |  |  | Transformers
30446 | 4/1/2003 | Potentially Challenging | No | N/A |  |  | Electrical panel | Relay rack
30447 | 7/11/2004 | Potentially Challenging | No | N/A
30448
30449 | 10/8/2005 | Not Challenging | No |  |  |  | Pumps
30450
30451
30452 | 8/8/2008 | Not Challenging | No
30453 | 1/30/2009 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water)
30454 | 6/22/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten
30455 | 3/14/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
30456 | 3/7/2001 | Potentially Challenging | No |  |  |  | Crane
30457 | 10/24/2006 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other
30458 | 1/18/2003 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Other
30459 | 3/9/2003 | Potentially Challenging | No | N/A |  |  | Electrical panel | Other instrument/control cabin
30460 | 3/18/2003 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
30461 | 3/23/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30462 | 5/24/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
30463 | 10/28/2009 | Not Challenging | No |  |  |  | Pumps
30464 | 9/23/2008 | Not Challenging | No | N/A | Turbine Building | Condensate System | Pumps |  | 110V | AC
30465 | 9/24/2008 | Potentially Challenging | No | N/A | Turbine Building
30466
30467
30468
30469 | 11/11/2007 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Transformers
30470 |  |  | No | N/A
30471 | 4/4/2008 | Potentially Challenging | No | N/A | Diesel Generator Building |  | Generator | Class 1A emergency generator | 4KV | AC
30472 | 9/29/2006 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Cable/Wiring
30473 | 9/20/2001 | Not Challenging | No
30474 | 8/12/2002 | Not Challenging | No | N/A | Other (Specify in comments)
30475 | 4/26/2003 | Not Challenging | No | N/A | Other (Specify in comments)
30476 | 10/12/2003 | Not Challenging | Yes | N/A | Other (Specify in comments)
30477
30478 | 9/9/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Electrical panel | Relay rack
30479 | 9/24/2005 | Not Challenging | No
30480 | 9/25/2005 | Not Challenging | No
30481 | 9/25/2005 | Not Challenging | No | N/A | Turbine Building
30482 | 10/5/2005 | Not Challenging | No
30483 | 10/9/2005 | Not Challenging | No | N/A | Turbine Building
30484
30485 | 9/17/2006 | Not Challenging | No | N/A | Turbine Building
30486
30487 | 12/4/2006 | Not Challenging | No | N/A | Other (Specify in comments)
30488
30489 | 10/5/2007 | Not Challenging | No | N/A | Turbine Building | Condensate System | Other |  | N/A | N/A
30490
30491
30492
30493 | 7/24/2008 | Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
30494
30495
30496
30497
30498 | 6/21/2009 | Not Challenging | No | N/A | Turbine Building | General Ventillation Systems | Other
30499
30500 | 5/29/2002 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Other
30501
30502 | 10/8/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30503 | 3/8/2002 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Other
30504 | 3/17/2002 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Crane | Other instrument/control cabin | 110V | AC
30505 | 3/11/2003 | Not Challenging | No | N/A | Other (Specify in comments)
30506 | 12/17/2003 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Electric Motor |  | 110V | AC
30507 | 7/26/2005 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
30508 | 3/26/2009 | Potentially Challenging | No | N/A | Turbine Building | Feedwater System | Other
30509 | 8/11/2009 | Not Challenging | No | N/A | Control building
30510 | 1/17/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
30511 | 1/23/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
30512 | 2/15/2006 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | 480V | AC
30513 | 5/27/2008 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Transformers | Other (Capacitor Voltage, Poten | 110V | AC
30514 | 3/7/2003 | Not Challenging | No
30515
30516 | 6/25/2005 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Other |  | 13 KV or greater | AC
30517 | 7/29/2005 | Not Challenging | Yes |  | Other (Specify in comments)
30518
30519 | 1/5/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30520 | 3/1/2000 | Not Challenging | No |  | Turbine Building |  | Electrical panel
30521 | 9/11/2000 | Not Challenging | No |  | Turbine Building
30522 | 9/12/2000 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Closed/Component Cooling Water | Electrical panel | Other instrument/control cabin
30523 | 9/14/2000 | Not Challenging | Yes | N/A |  |  | Other
30524 | 12/14/2000 | Undetermined (NC‐PC) | No |  |  |  | Pumps
30525 | 3/7/2001 | Not Challenging | Yes |  |  |  | Cable/Wiring
30526 | 6/12/2001 | Not Challenging | No | N/A | Turbine Building |  | Other
30527 | 2/1/2002 | Not Challenging | No |  |  |  | Other
30528 | 2/24/2002 | Not Challenging | No | N/A | Turbine Building |  | Other
30529 | 3/8/2002 | Not Challenging | No | N/A | Containment (PWR)
30530 | 3/23/2002 | Not Challenging | Yes | N/A |  |  | Pumps
30531 | 4/17/2002 | Not Challenging | No |  | Radwaste Building |  | Other
30532 | 6/14/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
30533 | 2/10/2003 | Not Challenging | Yes |  |  |  | Other
30534 | 3/4/2004 | Not Challenging | No |  | Turbine Building
30535 | 4/16/2004 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
30536 | 9/13/2004 | Not Challenging | No
30537 | 6/15/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
30538 | 1/23/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers
30539 | 2/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Cable/Wiring
30540 | 5/2/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30541 | 7/6/2005 | Potentially Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans
30542 | 7/28/2005 | Not Challenging | No |  | Other (Specify in comments)
30543 | 8/24/2005 | Not Challenging | Yes
30544 | 10/4/2005 | Not Challenging | No |  |  |  | Other
30545 | 1/16/2006 | Not Challenging | Yes | N/A | Other (Specify in comments)
30546 | 4/26/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30547 | 4/19/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30548 | 7/24/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30549 | 9/5/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Batteries
30550 | 10/5/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30551 | 10/20/2006 | Not Challenging | No |  | Turbine Building |  | Pumps
30552 | 5/8/2007 | Not Challenging | No
30553 | 8/28/2007 | Not Challenging | No
30554 | 10/17/2007 | Not Challenging | No |  |  |  | Pumps
30555 | 4/1/2008 | Not Challenging | Yes |  |  |  | Other
30556 | 4/4/2008 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
30557 | 4/30/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
30558 | 10/20/2008 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | 24‐48VDC | DC
30559 | 11/21/2008 | Not Challenging | No |  |  |  | Electric Motor
30560 | 2/4/2009 | Not Challenging | No
30561 | 4/3/2008 | Not Challenging | No | N/A | Containment (PWR)
30562 | 3/17/2008 | Not Challenging | No
30563 | 3/9/2008 | Not Challenging | No
30564 | 11/18/2003 | Not Challenging | No |  | Radwaste Building |  | Other
30565 | 2/11/2000 | Not Challenging | No
30566 | 9/11/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
30567 | 10/17/2000 | Not Challenging | No
30568 | 1/19/2002 | Not Challenging | No
30569 | 10/16/2006 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
30570 | 3/28/2001 | Not Challenging | No
30571 | 1/12/2001 | Not Challenging | No |  |  |  | Other
30572 | 5/12/2002 | Not Challenging | Yes |  |  |  | Other |  | N/A | N/A
30573 | 6/6/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
30574 | 11/2/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other (Specify in comments) |  | 480V | AC
30575
30576 | 8/15/2006 | Not Challenging | Yes |  |  |  | Other
30577 | 3/3/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30578 | 2/27/2003 | Undetermined (PC‐CH) | No | Fuel handling area | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 480V | AC
30579 | 6/6/2007 | Not Challenging | Yes
30580 | 6/21/2000 | Not Challenging | Yes
30581 | 6/19/2007 | Not Challenging | No
30582 | 6/7/2000 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) |  |  | 110V | AC
30583 | 6/30/2003 | Not Challenging | Yes |  | Containment (PWR)
30584 | 5/24/2001 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) |  |  | 110V | AC
30585 | 5/3/2001 | Not Challenging | No
30586 | 1/11/2006 | Undetermined | No | N/A | Other (Specify in comments) | Emergency Onsite Power Supply System | Generator |  | 24‐48VDC | DC
30587 | 3/4/2009 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 110V | AC
30588 | 5/14/2009 | Not Challenging | No |  | Turbine Building
30589 | 10/11/2009 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring
30590 | 12/22/2009 | Not Challenging | No
30591 | 10/17/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  |  |  | N/A | N/A
30592
30593 | 2/7/2008 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten
30594 | 6/17/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten
30595 | 10/10/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
30596 | 10/17/2008 | Not Challenging | No | N/A | Containment (PWR) |  | Other
30597 | 2/5/2009 | Potentially Challenging | No | N/A | Turbine Building | Hydrogen Supply System | Other |  | N/A | N/A
30598 | 11/20/2009 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
30599 | 3/23/2001 | Not Challenging | No
30600 | 11/9/2001 | Not Challenging | No | Main Control Room | Control building
30601 | 9/14/2001 | Not Challenging | No | N/A | Radwaste Building |  | Other |  | 10V | AC
30602 | 5/19/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps
30603 | 1/13/2005 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  | N/A
30604 | 5/28/2005 | Potentially Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Diesel driven pumps
30605 | 9/19/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Junction Boxes
30606 | 12/19/2007 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin
30607 | 3/20/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
30608 | 1/10/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
30609 | 4/17/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other
30610 | 7/21/2002 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Closed/Component Cooling Water | Pumps | Electric motor driven pumps
30693 | 2/3/2004 | Potentially Challenging | No | N/A | Other (Specify in comments) | Emergency Onsite Power Supply System | Generator | Other generator (specify in com
30694 | 8/10/2004 | Not Challenging | Yes | N/A | Other (Specify in comments)
30695 | 9/21/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
30696 | 9/26/2006 | Not Challenging | No
30697 | 9/29/2006 | Not Challenging | No | N/A | Containment (PWR)
30698 | 2/22/2007 | Not Challenging | Yes |  | Other (Specify in comments)
30699 | 3/7/2007 | Not Challenging | No
30700 | 4/19/2007 | Not Challenging | No
30701 | 8/13/2007 | Not Challenging | No
30702 | 9/11/2007 | Not Challenging | No
30703 | 10/2/2007 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | 110V | AC
30704 | 10/17/2007 | Not Challenging | No |  |  |  | Other
30705 | 9/20/2007 | Not Challenging | No
30706 | 6/28/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Junction Boxes
30707 | 10/1/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
30708 | 2/6/2001 | Not Challenging | No
30709 | 7/13/2001 | Not Challenging | No
30710 | 9/19/2001 | Not Challenging | No
30711 | 11/16/2001 | Not Challenging | No
30712 | 4/24/2002 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A | N/A
30713 | 4/29/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30714
30715
30716 | 9/2/2002 | Not Challenging | No |  |  |  | Cable/Wiring
30717 | 12/10/2002 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other
30718 | 4/15/2003 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Other
30719 | 6/11/2003 | Undetermined (PC‐CH) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System
30720 | 7/2/2003 | Not Challenging | No |  |  |  | Other
30721 | 8/27/2003 | Not Challenging | No
30722 | 10/19/2003 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
30723 | 11/3/2008 | Not Challenging | No |  |  |  | Other
30724 | 11/16/2008 | Not Challenging | No
30725 | 4/12/2000 | Potentially Challenging | No | N/A |  |  | Electric Motor | Fans
30726 | 5/19/2000 | Not Challenging | No |  | Turbine Building |  | Electrical panel | Circuit breaker or other distribu
30727 | 10/30/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
30728 | 12/21/2000 | Not Challenging | No | Containment/Drywell |  |  | Other |  | N/A | N/A
30729 | 12/22/2000 | Not Challenging | No | Containment/Drywell |  |  | Other
30730 | 3/5/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
30731 | 3/19/2001 | Potentially Challenging | No | N/A | Containment (PWR) |  | Other
30732 | 12/3/2001 | Potentially Challenging | No | N/A |  | General Ventillation Systems | Electric Motor | Fans
30733 | 6/27/2002 | Potentially Challenging | No | N/A |  |  | Generator |  | 4KV | AC
30734 | 8/26/2002 | Potentially Challenging | No | N/A |  | DC Power System | Cable/Wiring |  | 125VDC | DC
30735 | 3/4/2003 | Not Challenging | Yes | N/A |  |  | Other
30736 | 3/13/2003 | Undetermined (PC‐CH) | No | N/A | Other (Specify in comments)
30737 | 5/12/2003 | Not Challenging | No | N/A
30738 | 9/23/2003 | Not Challenging | No |  |  |  | Transformers |  | 600V | AC
30739 | 3/29/2001 | Not Challenging | No
30740 | 2/6/2004 | Potentially Challenging | No | N/A |  |  | Other
30741 | 3/24/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
30742 | 4/15/2004 | Not Challenging | No
30743 | 4/27/2004 | Not Challenging | No
30744 | 6/2/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
30745 | 10/10/2004 | Not Challenging | No
30746 | 10/28/2004 | Not Challenging | No | N/A |  |  | Other
30747 | 11/6/2004 | Not Challenging | No | N/A
30748 | 11/27/2004 | Not Challenging | No |  | Other (Specify in comments)
30749 | 1/9/2005 | Not Challenging | No
30750 | 5/9/2005 | Undetermined (PC-CH) | No | N/A
30751 | 3/28/2006 | Not Challenging | No
30752 | 4/3/2007 | Potentially Challenging | No | N/A | Turbine Building |  | Other
30753 | 5/16/2007 | Not Challenging | No | N/A | Other (Specify in comments)
30754 | 2/2/2008 | Not Challenging | No
30755 | 4/7/2008 | Not Challenging | No
30756 | 11/23/2008 | Undetermined (PC-CH) | No | N/A |  |  | Other
30757 | 8/24/2009 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other
30758 | 9/3/2009 | Not Challenging | No |  |  |  | Air Compressors
40730 | 10/27/2000 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A
40731 | 2/13/2001 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A
40732 | 3/8/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
40733 | 3/14/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) | Hydrogen Supply System | Other |  | N/A | N/A
40734 | 3/19/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
40735 | 4/4/2001 | Not Challenging | No | N/A | Other (Specify in comments | Hydrogen Supply System | Other |  | N/A | N/A
40736 | 4/15/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
40737 | 4/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  |  |  | N/A | N/A
40738 | 6/5/2002 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other |  | N/A | N/A
40739 | 7/23/2002 | Not Challenging | No |  | Auxiliary Building (PWR) |  |  |  | N/A | N/A
40740 | 3/3/2003 | Not Challenging | No | N/A | Turbine Building
40741 | 4/16/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
40742 | 7/7/2003 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC
40743 | 10/7/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
40744 | 3/24/2004 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 110V | AC
40745 | 10/20/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | 24‐48VDC | DC
40746 | 8/15/2006 | Potentially Challenging | No |  | Turbine Building
40747 | 4/17/2007 | Not Challenging | No |  | Auxiliary Building (PWR)
40748 | 11/28/2007 | Not Challenging | No |  | Auxiliary Building (PWR)
40749 | 6/13/2008 | Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
40750 | 11/16/2009 | Not Challenging | No |  | Auxiliary Building (PWR)
50356 | 1/11/2000 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Other |  | 110V | AC
50357 | 3/21/2000 | Not Challenging | No | Main Control Room | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 110V | AC
50358 | 6/1/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50359 | 8/24/2000 | Not Challenging | No |  | Control building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center
50360 | 12/20/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel
50361 | 4/11/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC
50362 | 7/16/2001 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans | 480V | AC
50363
50364 | 10/4/2001 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans
50365 | 3/4/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50366 | 3/8/2002 | Not Challenging | No |  | Control building
50367 | 3/14/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | Other (specify) | AC
50368 | 6/6/2002 | Not Challenging | No | Main Control Room |  | General Ventillation Systems | Other |  | 110V | AC
50369 | 8/14/2002 | Not Challenging | No | N/A | Control building | DC Power System | Transformers | Other (Capacitor Voltage, Poten | 125VDC | DC
50370 | 10/23/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 110V | AC
50371 | 11/1/2002 | Not Challenging | No | Switchgear Room | Control building | Low Voltage Power System, Class 1E | Transformers |  | 480V | AC
50372 | 5/9/2003 | Not Challenging | No |  | Turbine Building |  | Electric Motor |  | 125VDC | DC
50373 | 10/7/2003 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Other |  | N/A | N/A
50374 | 4/22/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) | 110V | AC
50375 | 9/30/2004 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Closed/Component Cooling Water | Pumps | Electric motor driven pumps
50376 | 3/24/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50377 | 7/2/2005 | Not Challenging | No | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Transformers | Other (Capacitor Voltage, Poten
50378 | 7/27/2005 | Potentially Challenging | No | N/A | Control building | Instrument and Uninterruptible Power System | Transformers | Other (Capacitor Voltage, Poten | 110V | AC
50379 | 2/24/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50380 | 8/31/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50381 | 12/14/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50382 | 1/29/2007 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50383 | 3/1/2007 | Not Challenging | No | N/A | Control building |  | Other |  | 125VDC | DC
50384 | 3/22/2007 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50385 | 5/30/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50386
50387 | 3/29/2008 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Other |  | N/A | N/A
50388 | 6/8/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Transformers | Dry transformer | 110V | AC
50389 | 6/23/2008 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Pumps | Electric motor driven pumps | 4KV | AC
50390 | 10/1/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | 480V | AC
50391 | 7/2/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50392 | 8/13/2000 | Not Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans
50393 | 10/17/2000 | Undetermined (NC‐PC) | No |  |  |  | Other |  | N/A | N/A
50394 | 4/21/2001 | Not Challenging | No |  |  | High Pressure Core Spray System (BWR) | Electrical panel | Circuit breaker or other distribu
50395 | 4/16/2001 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50396 | 5/1/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring
50397 | 1/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50398 | 12/2/2003 | Not Challenging | No | N/A |  |  | Electrical panel
50399 | 2/26/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50400 | 8/7/2004 | Not Challenging | No |  |  | Reactor Core Isolation Cooling System (BWR) | Other
50401 | 10/4/2005 | Not Challenging | No |  |  |  | Other
50402 | 11/8/2005 | Not Challenging | No | N/A | Radwaste Building | General Ventillation Systems | Pumps | Electric motor driven pumps
50403 | 11/8/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50404 | 11/25/2005 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Electrical panel | Other (specify in comments)
50405 | 3/4/2006 | Undetermined (NC‐PC) | No |  |  |  | Air Compressors
50406 | 8/21/2007 | Not Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps
50407 | 3/11/2008 | Potentially Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50408
50409 | 10/5/2006 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR)
50410 | 9/29/2005 | Not Challenging | No |  |  |  | Other
50411 | 7/9/2005 | Undetermined (NC‐PC) | No | Main Control Room | Control building | General Ventillation Systems | Electric Motor | Fans
50412
50413
50414
50415
50416
50417
50418
50419
50420
50421
50422
50423 | 2/28/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50424 | 3/15/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50425 | 3/16/2000 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50426 | 5/2/2000 | Potentially Challenging | No | N/A | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
50427 | 8/19/2000 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
50428 | 9/20/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50429 | 3/19/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50430 | 2/18/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
50431
50432 | 3/19/2001 | Not Challenging | No |  |  | General Ventillation Systems | Electrical panel | Motor control center
50433 | 8/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50434 | 10/28/2001 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Motor control center
50435 | 7/22/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50436 | 8/12/2002 | Not Challenging | Yes | Cable vault/tunnel area | Other (Specify in comments) |  | Other |  | N/A | N/A
50437
50438 | 1/7/2003 | Not Challenging | No | N/A | Other (Specify in comments) | Switchyard System | Transformers
50439 | 3/3/2003 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
50440 | 10/13/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50441 | 10/23/2004 | Not Challenging | Yes |  |  |  | Air Compressors
50442 | 11/8/2004 | Potentially Challenging | No | N/A | Radwaste Building | Main Generator Hydrogen Cooling System | Other |  | N/A | N/A
50443 | 3/20/2005 | Not Challenging | No |  |  |  | Electric Motor | Crane motor
50444 | 4/27/2005 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments)
50445 | 4/28/2005 | Not Challenging | No | N/A |  | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC
50446 | 7/14/2005 | Not Challenging | No | Switchgear Room |  | DC Power System | Electrical panel | Relay rack | 125VDC | DC
50447 | 9/14/2005 | Potentially Challenging | No | N/A |  | General Ventillation Systems | Electrical panel | Circuit breaker or other distribu | 480V | AC
50448 | 10/11/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Other
50449 | 2/21/2006 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50450 | 2/28/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50451 | 7/15/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Cable/Wiring
50452 | 8/18/2006 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Other (Specify in comments) |  | Other |  | N/A | N/A
50453 | 8/22/2006 | Not+D20421:D20432Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50454 | 11/8/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50455 | 11/30/2006 | Not Challenging | No | Main Control Room | Control building | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 110V | AC
50456 | 2/15/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50457 | 7/28/2007 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
50458 | 8/15/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50459 | 2/8/2008 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps
50460 | 4/16/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50461 | 4/24/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50462 | 6/12/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50463 | 4/11/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50464 | 4/26/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Cable/Wiring |  | 480V | AC
50465
50466 | 2/4/2005 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps
50467 | 2/4/2006 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | 11/2/2007
50468 | 11/2/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu
50469 | 7/28/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries
50470 | 11/19/2008 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments)
50471 | 12/2/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Switchyard System | Cable/Wiring |  | 480V | AC
50472 | 8/30/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50473 | 6/26/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Wall Mounted or Sealed
50474 | 8/29/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50475 | 10/11/2000 | Undetermined (PC‐CH) | No |  |  |  | Electrical panel | Electric bus bar or bus duct
50476 | 12/19/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50477 | 3/18/2000 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50478 | 3/19/2000 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50479 | 3/22/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Dryers
50480 | 4/7/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50481 | 11/4/2006 | Not Challenging | No | N/A | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC
50482 | 3/8/2006 | Not Challenging | Yes | N/A |  | Feedwater System | Pumps | Electric motor driven pumps | 480V | AC
50483 | 3/11/2008 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Emergency Onsite Power Supply System | Electrical panel | Circuit breaker or other distribu | 480V | AC
50484 | 3/23/2008 | Not Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans
50485
50486 | 4/20/2008 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Cable/Wiring |  | 13 KV or greater | AC
50487 | 3/6/2009 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC
50488 | 5/27/2009 | Not Challenging | Yes | N/A |  | Turbine Lube Oil System | Lube Oil |  | N/A | N/A
50489 | 8/30/2009 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Low Voltage Power System (600V and less) | Cable/Wiring |  | 480V | AC
50490 | 9/16/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50491 | 10/16/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 220V | AC
50492 | 11/2/2009 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Transformers
50493
50494 | 2/5/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50495 | 11/11/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50496 | 1/21/2002 | Not Challenging | No | Switchgear Room |  | Non Essential Service Water System | Electrical panel | Other instrument/control cabin | Other (specify) | AC
50497 | 8/15/2006 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  | 220V | AC
50498
50499 | 4/1/2004 | Not Challenging | Yes | Switchgear Room | Other (Specify in comments) | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 125VDC | DC
50500 |  | Not Challenging
50501 | 11/6/2001 | Not Challenging | No | N/A | Control building |  | Other
50502 | 10/16/2002 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring
50503 | 6/14/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50504 | 5/20/2002 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel |  | 480V | AC
50505
50506 | 12/9/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | Other (specify) | AC
50507 | 11/15/2005 | Not Challenging | No | Containment/Drywell | Turbine Building |  | Other |  | N/A | N/A
50508 | 11/26/2005 | Not Challenging | No | Containment/Drywell | Other (Specify in comments) |  | Other |  | N/A | N/A
50509 | [8 empty] | N/A | N/A
50510 | 4/19/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50511 | 5/15/2004 | Not Challenging | No | N/A | Turbine Building |  | Lube Oil |  | N/A | N/A
50512 | 5/31/2000 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
50513 | 8/27/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
50514 | 4/29/2009 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50515 | 11/30/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50516 | 10/5/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50517 | 10/8/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50518 | 11/18/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring
50519 | 10/19/2009 | Not Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System, Class 1E | Cable/Wiring | Other (specify in comments) | 250VDC | DC
50520 | 12/7/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50521 | 2/1/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50522 | 9/8/2003 | Undetermined (NC‐PC) | No |  |  |  | Pumps | Electric motor driven pumps
50523 | 9/19/2003 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System, Class 1E | Cable/Wiring |  | 110V | AC
50524 | 1/23/2008 | Not Challenging | No |  |  |  | Other
50525 | 12/18/2009 | Not Evaluated | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers |  | 13 KV or greater | AC
50526 | 12/7/2006 | Not Evaluated | No
50527 | 6/23/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50528 | 6/19/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50529 | 3/31/2003 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50530 | 10/21/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Electric Motor | Fans | 4KV | AC
50531
50532
50533
50534 | 1/7/2002 | Not Evaluated | No | N/A | Turbine Building | Hydrogen Supply System | Other |  | N/A | N/A
50535 | 1/8/2002 | Not Challenging | Yes | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50536 | 3/21/2002 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other
50537 | 3/23/2002 | Not Challenging | No |  |  |  | Electric Motor | Fans
50538 | 3/27/2002 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50539 | 5/22/2002 | Not Challenging | Yes | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Other |  | N/A | N/A
50540 | 5/25/2002 | Not Challenging | No |  |  |  | Other
50541 | 4/6/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50542 | 7/30/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50543 | 3/27/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other |  | N/A | N/A
50544
50545 | 9/18/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50546 | 12/1/2004 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other
50547 | 4/4/2006 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50548 | 6/9/2006 | Not Challenging | Yes |  |  |  | Other |  | N/A | N/A
50549 | 1/21/2007 | Not Challenging | No |  |  |  | Other
50550 | 6/9/2007 | Not Challenging | Yes | N/A | Other (Specify in comments)
50551 | 10/6/2008 | Not Challenging | No | Battery Room | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 220V | AC
50552 | 3/23/2009 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Other |  | N/A | N/A
50553 | 5/2/2003 | Potentially Challenging | No | Main Control Room | Control building |  | Electrical panel | Other instrument/control cabin
50554 | 5/19/2003 | Not Challenging | No | Fuel handling area |  | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 110V | AC
50555 | 6/25/2003 | Not Challenging | Yes |  | Other (Specify in comments)
50556 | 2/25/2005 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electric Motor | MG set | 13 KV or greater | AC
50557 | 1/16/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electric Motor | MG set | 250VDC | DC
50558 | 1/2/2007 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electric Motor | MG set | 250VDC | DC
50559
50560
50561
50562 | 5/28/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Offgas System (BWR) | Other
50563 | 11/16/2005 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Hydrogen Supply System | Other
50564 | 1/15/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50565 | 8/26/2008 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps
50566 | 9/17/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 13 KV or greater | AC
50567
50568
50569 | 3/24/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Outlets
50570 | 6/21/2004 | Undetermined (NC‐PC) | No | N/A | Service Water Pump house | Low Voltage Power System (600V and less) | Pumps | Electric motor driven pumps | 480V | AC
50571 | 7/22/2004 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50572 | 10/8/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50573 | 8/24/2004 | Not Challenging | No |  | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps
50574 | 9/16/2004 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50575 | 9/14/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries |  | Other (specify) | AC
50576 | 9/17/2004 | Not Challenging | No | Battery Room | Reactor Building (BWR) | General Ventillation Systems | Other |  | 110V | AC
50577 | 10/23/2004 | Not Challenging | No | N/A | Control building |  | Electric Motor | Elevator motor | N/A | N/A
50578 | 11/23/2004 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR)
50579 | 5/4/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50580 | 10/9/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 480V | AC
50581 | 6/24/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50582 | 8/22/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  |  | N/A
50583 | 9/3/2005 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | Circuit breaker or other distribu | AC
50584 | 6/27/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Relay rack | 125VDC | DC
50585 | 10/8/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50586 | 9/28/2005 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Relay rack
50587 | 2/4/2006 | Not Challenging | Yes | N/A |  | Medium Voltage Power System (601V to 35kV) | Electrical panel | Electric bus bar or bus duct | 13 KV or greater | AC
50588 | 2/4/2006 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu
50589 | 4/15/2006 | Not Challenging | No | Cable vault/tunnel area | Reactor Building (BWR) |  | Lighting Ballasts |  | 110V | AC
50590 | 5/6/2006 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Switchgear | 13 KV or greater | AC
50591 | 5/29/2006 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other |  | N/A | N/A
50592 | 7/11/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 220V | AC
50593 | 10/4/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 480V | AC
50594 | 10/5/2006 | Not Challenging | No | N/A | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Outlets |  | 110V | AC
50595 | 10/28/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50596 | 1/5/2007 | Not Challenging | No | Cable vault/tunnel area | Other (Specify in comments) |  | Other |  | 110V | AC
50597 | 12/18/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50598 | 3/10/2008 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Electric Motor | Fans
50599 | 3/31/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC
50600 | 12/2/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC
50601 | 8/30/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Lighting Ballasts |  | 110V | AC
50602
50603 | 2/24/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Junction Boxes |  | 220V | AC
50604 | 11/27/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50605 | 10/4/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50606 | 10/8/2001 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts |  | 110V | AC
50607 | 3/1/1997 | Not Evaluated | No |  |  |  | Electrical panel | Other instrument/control cabin
50608 | 5/28/1997 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Cable/Wiring |  | 110V | AC
50609 | 11/23/2000 | Not Evaluated | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans
50610 | 5/30/2005 | Not Evaluated | No | Fuel handling area | Reactor Building (BWR) |  | Cable/Wiring |  | 480V | AC
50611 | 3/19/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other
50612 | 10/21/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring
50613 | 7/3/2003 | Not Evaluated | No | Fuel handling area | Turbine Building |  | Other
50614 | 3/9/2004 | Not Evaluated | No | N/A |  |  | Other |  | N/A | N/A
50615 | 3/11/2004 | Not Evaluated | No | N/A |  |  |  |  | N/A | N/A
50616 | 3/21/2004 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A
50617 | 3/29/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A
50618 | 9/14/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
50619 | 2/8/2006 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50620 | 3/27/2008 | Not Challenging | No | N/A | Control building |  | Lighting Ballasts
50621 | 9/11/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50622 | 11/8/2009 | Not Challenging | No | N/A |  |  | Lighting Ballasts
50623 | 12/15/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Outlets |  | 110V | AC
50624 | 5/14/2003 | Not Challenging | No |  | Turbine Building |  | Lighting Ballasts
50625 | 1/8/2001 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50626
50627 | 3/24/2001 | Not Challenging | No |  |  |  | Other
50628 | 3/9/2000 | Not Challenging | No | Main Control Room | Control building |  | Other |  | 110V | AC
50629 | 10/16/2000 | Not Challenging | No |  |  |  | Transformers | Dry transformer
50630 | 10/22/2000 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring
50631 | 10/27/2000 | Not Challenging | No |  |  |  | Electrical panel | Motor control center
50632 | 10/27/2000 | Not Challenging | No | N/A | Control building |  | Electrical panel | Relay rack
50633 | 11/12/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50634 | 3/6/2002 | Not Challenging | No |  |  |  | Electrical panel | Battery charger | 250VDC | DC
50635 | 12/12/2000 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Relay rack
50636 | 2/10/2001 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
50637 | 4/18/2001 | Not Challenging | No |  |  |  | Other
50638 | 5/14/2001 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 480V | AC
50639 | 11/10/2001 | Not Challenging | Yes | N/A |  | Heat Rejection System (Circulating Water) | Transformers | Other (Capacitor Voltage, Poten | 220V | AC
50640 | 12/23/2001 | Not Challenging | Yes | N/A |  | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 220V | AC
50641 | 3/4/2002 | Not Challenging | No |  |  |  | Electric Motor | Other (specify in comments)
50642 | 4/16/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50643 | 4/18/2002 | Not Challenging | No |  |  |  | Electrical panel
50644 | 6/24/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Main control board (i.e., the ma | 110V | AC
50645 | 12/23/2002 | Not Challenging | No | Main Control Room | Control building |  | Lighting Ballasts
50646 | 3/7/2003 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu
50647 | 8/12/2003 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Other (specify in comments) | N/A | N/A
50648 | 12/2/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Crane |  | N/A | N/A
50649 | 4/22/2003 | Not Challenging | No | N/A | Diesel Generator Building |  | Other |  | 110V | AC
50650 | 9/26/2003 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other | Electric motor driven pumps | 110V | AC
50651 | 10/17/2003 | Not Challenging | Yes | N/A | Turbine Building |  | Other |  | N/A | N/A
50652 | 3/18/2004 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
50653 | 10/4/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50654 | 9/24/2007 | Not Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps
50655 | 12/4/2007 | Undetermined (NC‐PC) | No |  |  |  | Other
50656 | 8/18/2008 | Not Challenging | No |  |  |  | Electrical panel | Electrical panel
50657 | 3/2/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC
50658 | 4/24/2004 | Not Challenging | Yes | N/A | Turbine Building |  | Other |  | N/A | N/A
50659 | 8/11/2004 | Not Challenging | No | N/A | Containment (PWR) |  | Electric Motor | Other (specify in comments)
50660 | 9/24/2000 | Not Challenging | No |  |  |  | Other
50661 | 4/25/2001 | Not Evaluated | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Other |  | 13 KV or greater | AC
50662 | 6/5/2001 | Not Evaluated | No |  |  |  | Pumps | Electric motor driven pumps
50663 | 8/12/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC
50664 | 6/29/2001 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
50665 | 9/17/2004 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Closed/Component Cooling Water | Pumps | Electric motor driven pumps
50666 | 3/22/2005 | Not Challenging | No | N/A | Service Water Pump house |  | Pumps | Electric motor driven pumps
50667 | 3/28/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 220V | AC
50668 | 4/16/2005 | Not Challenging | No |  |  |  | Electrical panel | Relay rack
50669 | 1/3/2002 | Not Evaluated | No |  |  |  | Pumps | Diesel driven pumps
50670 | 10/12/2005 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Circuit breaker or other distribu
50671 | 10/20/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
50672 | 4/5/2002 | Not Evaluated | No |  |  |  | Electrical panel | Other instrument/control cabin
50673 | 4/5/2002 | Not Evaluated | No | N/A | Turbine Building |  | Other
50674 | 9/23/2005 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 480V | AC
50675 | 8/12/2002 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50676 | 11/29/2005 | Not Challenging | No | N/A | Service Water Pump house |  | Other |  | N/A | N/A
50677 | 9/24/2002 | Not Challenging | No |  |  |  | Other
50678 | 3/28/2006 | Not Challenging | Yes | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 220V | AC
50679 | 10/4/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC
50680 | 8/24/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50681 | 11/22/2000 | Not Evaluated | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
50682 | 4/10/2007 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50683 | 5/18/2004 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50684 | 3/8/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50685 | 3/30/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50686 | 4/4/2007 | Undetermined (NC‐PC) | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A
50687 | 7/23/2007 | Not Challenging | No |  |  |  | Junction Boxes
50688 | 5/28/2004 | Not Challenging | No | N/A |  |  | Pumps | Diesel driven pumps
50689 | 10/17/2005 | Not Evaluated | No | Containment/Drywell | Containment (PWR) |  | Other
50690 | 10/24/2005 | Not Evaluated | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A
50691 | 2/15/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Batteries |  | N/A | N/A
50692 | 3/24/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other
50693 | 10/13/2008 | Not Evaluated | No | N/A |  |  | Pumps | Electric motor driven pumps
50694 | 10/24/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50695
50696 | 4/21/2008 | Not Challenging | No |  |  |  | Junction Boxes
50697 | 7/16/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50698 | 3/17/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
50699 | 4/7/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50700 | 5/13/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) | Heat Rejection System (Circulating Water) | Other |  | N/A | N/A
50701 | 5/24/2000 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC
50702 | 6/25/2000 | Not Challenging | No | Main Control Room | Control building
50703 | 8/22/2000 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other | Oil‐filled Transformer
50704 | 12/22/2000 | Not Challenging | Yes | N/A |  | Low Voltage Power System (600V and less) | Cable/Wiring |  | 480V | AC
50705 | 4/15/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50706 | 4/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
50707 | 4/25/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps | 480V | AC
50708 | 5/17/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other
50709 | 10/26/2001 | Not Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Other instrument/control cabin | 24‐48VDC | DC
50710 | 11/19/2001 | Not Challenging | Yes | N/A | Turbine Building
50711 | 11/20/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts
50712 | 12/14/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps | 4KV | AC
50713 | 1/1/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50714 | 1/9/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
50715 | 1/16/2002 | Not Challenging | No | Main Control Room | Control building |  | Other |  | 110V | AC
50716 | 1/24/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Lighting Ballasts |  | 220V | AC
50717 | 5/21/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50718 | 3/20/2003 | Not Challenging | Yes | N/A |  |  | Electric Motor | Other (specify in comments) | 480V | AC
50719 | 8/1/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50720 | 8/4/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50721 | 8/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50722 | 10/10/2003 | Not Challenging | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps
50723 | 1/8/2004 | Not Challenging | No | Battery Room | Reactor Building (BWR) | General Ventillation Systems | Other
50724 | 3/5/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments)
50725 | 3/10/2004 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps
50726 | 10/14/2003 | Not Challenging | No |  | Containment (PWR) |  | Other
50727
50728 | 1/20/2009 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans
50729 | 4/4/2008 | Not Challenging | No | N/A | Other (Specify in comments) | Condensate System | Cable/Wiring
50730 | 3/1/2006 | Not Challenging | No | N/A | Other (Specify in comments)
50731 | 2/11/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC
50732 | 11/7/2002 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Service Water Pump house |  | Other
50733 | 4/23/2004 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other
50734
50735 | 4/9/2007 | Not Challenging | No | N/A | Containment (PWR) | Cable/Wiring
50736 | 4/10/2007 | Not Challenging | No |  | Containment (PWR) |  | Transformers | Other (Capacitor Voltage, Poten
50737
50738 | 3/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other
50739 | 3/28/2001 | Not Challenging | No | N/A | Control building |  | Electric Motor | Elevator motor
50740 | 5/16/2000 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure |  | Other
50741 | 9/18/2000 | Not Evaluated | No |  |  | Feedwater System | Pumps | Electric motor driven pumps
50742 | 10/4/2006 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps
50743 | 7/17/2008 | Not Challenging | No |  |  |  | Pumps | Diesel driven pumps
50744 | 8/3/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other
50745 | 9/22/2009 | Not Challenging | No | N/A | Control building |  | Junction Boxes
50746 | 5/6/2001 | Not Challenging | No | N/A | Turbine Building |  | Other
50747 | 2/9/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50748 | 9/22/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring
50749 | 10/28/2008 | Challenging | No | N/A | Other (Specify in comments) |  | Other
50750 | 1/10/2001 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50751 | 11/17/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50752
50753 | 12/11/2009 | Not Challenging | No | Main Control Room | Control building |  | Other | Other instrument/control cabin
50754 | 1/23/2009 | Potentially Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans
50755
50756 | 9/21/2004 | Not Challenging | No | Main Control Room | Reactor Building (BWR) |  | Lighting Ballasts
50757 | 9/7/2002 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Other instrument/control cabin
50758 | 6/14/2004 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps
50759 | 7/29/2006 | Not Challenging | No | N/A | Radwaste Building |  | Lighting Ballasts |  | 110V | AC
50760 | 11/8/2006 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50761 | 1/25/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring
50762 | 10/1/2001 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other
50763 | 11/14/2008 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten
50764 | 1/14/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments)
50765 | 10/12/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 110V | AC
50766 | 8/18/2000 | Not Challenging | Yes | N/A | Control building |  | Other
50767 | 6/1/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50768 | 1/1/2002 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electric Motor | Fans
50769 | 12/6/2002 | Not Challenging | No | Main Control Room | Control building |  | Lighting Ballasts
50770 | 1/30/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50771 | 5/6/2003 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Dryers
50772 | 7/2/2003 | Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC
50773 | 9/11/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50774 | 1/7/2004 | Not Challenging | No |  | Turbine Building | Feedwater System | Pumps | Electric motor driven pumps
50775 | 2/13/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50776 | 5/6/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50777 | 8/5/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50778 | 10/11/2004 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50779 | 10/25/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC
50780 | 1/6/2005 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50781 | 3/10/2005 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 480V | AC
50782 | 3/11/2005 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A
50783 | 6/27/2005 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts
50784 | 11/20/2005 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electrical panel | Relay rack
50785 | 12/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
50786 | 3/10/2006 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50787 | 1/4/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50788 | 3/8/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50789 | 3/4/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries
50790 | 6/7/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50791 | 10/25/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts
50792 | 11/6/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts
50793 | 11/18/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50794 | 3/4/2009 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50795 | 7/12/2009 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts
50796 | 11/4/2009 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 24‐48VDC | DC
50797 | 11/8/2009 | Not Challenging | No |  |  |  | Other
50798 | 12/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50799 | 12/12/2009 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A
50800
50801
50802
50803 | 12/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50804 | 1/13/2004 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less | Electrical panel | Load center | 480V | AC
50805 | 2/12/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50806 | 8/30/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Generator | Other generator (specify in com
50807 | 8/24/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator
50808 | 3/21/2006 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments) | 480V | AC
50809 | 11/9/2000 | Potentially Challenging | No | Cable vault/tunnel area | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  | 110V | AC
50810 | 6/25/2000 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50811 | 1/9/2001 | Potentially Challenging | No | N/A | Radwaste Building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | 110V | AC
50812 | 6/11/2001 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | N/A | N/A
50813 | 9/3/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring
50814 | 5/31/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50815 | 5/19/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50816 | 11/16/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50817 | 2/13/2006 | Not Challenging | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  | N/A | N/A
50818 | 3/21/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50819 | 6/13/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50820 | 10/23/2008 | Potentially Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less | Junction Boxes |  | 480V | AC
50821 | 10/30/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50822 | 11/7/2008 | Not Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC
50823 | 4/9/2009 | Not Challenging | No | Main Control Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | 110V | AC
50824 | 9/13/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps
50825 | 10/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Lighting Ballasts
50826 | 12/9/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Outlets |  | 110V | AC
50827 | 4/27/2002 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC
50828 | 10/2/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50829 | 9/11/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC
50830
50831
50832
50833 | 9/23/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Lighting Ballasts
50834 | 9/24/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50835 | 10/1/2009 | Not Challenging | No | N/A | Turbine Building |  | Other
50836
50837 | 7/9/2001 | Not Evaluated | No | N/A | Radwaste Building |  | Electrical panel | Other (specify in comments) | 220V | AC
50838 | 11/19/2001 | Not Evaluated | No | N/A |  |  | Other |  | N/A | N/A
50839 | 11/26/2001 | Not Evaluated | No | Fuel handling area | Reactor Building (BWR) |  | Other |  | N/A | N/A
50840 | 11/28/2001 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50841 | 11/29/2001 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50842 | 8/23/2002 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A
50843 | 3/22/2003 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A | N/A
50844 | 7/24/2003 | Not Evaluated | No | N/A | Turbine Building | Offgas System (BWR) | Other |  | N/A | N/A
50845 | 12/13/2003 | Not Evaluated | No |  |  |  | Lighting Ballasts |  | 110V | AC
50846 | 1/24/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A
50847 | 1/27/2005 | Not Evaluated | No |  |  |  | Outlets
50848 | 1/30/2005 | Not Evaluated | No |  |  |  | Electric Motor | MG set
50849 | 3/8/2005 | Not Evaluated | No |  |  |  | Lighting Ballasts
50850 | 4/1/2005 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A | N/A
50851 | 4/27/2005 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps
50852 | 5/25/2005 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
50853 | 11/28/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A
50854 | 9/18/2006 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50855 | 4/26/2008 | Not Evaluated | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50856 | 1/31/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Cable/Wiring
50857 | 11/6/2009 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50858
50859
50860 | 12/14/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50861 | 12/20/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50862 | 2/9/2006 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring |  | N/A | N/A
50863 | 9/30/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50864 | 9/24/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50865 | 1/31/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50866 | 3/28/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts
50867 | 10/31/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50868 | 7/3/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50869 | 10/25/2001 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Transformers
50870 | 1/8/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50871 | 1/24/2002 | Potentially Challenging | No |  | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps
50872 | 3/31/2002 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
50873 | 5/9/2002 | Not Challenging | No |  |  |  | Other |  | N/A | N/A
50874 | 7/12/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electrical panel | Circuit breaker or other distribu
50875 | 11/10/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50876 | 11/13/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Feedwater System | Cable/Wiring
50877
50878 | 11/12/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Feedwater System | Other |  | N/A | N/A
50879 | 11/15/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50880 | 11/15/2002 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
50881 | 12/31/2002 | Not Challenging | No |  | Other (Specify in comments) | DC Power System | Electrical panel | Inverter | 110V | AC
50882 | 1/20/2003 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Other
50883 | 4/18/2003 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A
50884 | 2/23/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50885 | 6/17/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50886 | 2/27/2004 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50887 | 3/7/2004 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A
50888 | 7/16/2004 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A
50889 | 3/22/2005 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electrical panel | Circuit breaker or other distribu | 4KV | AC
50890 | 4/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50891 | 4/8/2005 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
50892 | 4/12/2005 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A
50893 | 12/2/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Transformers | Other instrument/control cabin | 480V | AC
50894 | 3/12/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50895 | 5/13/2007 | Potentially Challenging | No | N/A | Turbine Building
50896 | 5/13/2007 | Undetermined (NC‐PC) | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
50897 | 12/22/2007 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Generator | Other generator (specify in com | N/A | N/A
50898 | 2/29/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin
50899 | 10/27/2008 | Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A
50900 | 5/1/2009 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A
50901 | 8/28/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A

## Fire Event Attributes
FireID | Event Date_FEA | Disposition_FEA | Fire Cause | Combustible Group | Type | Form | Fire Type | Smoke | Temperature | Damage Extent | Collateral Damage
1 | 12/12/2006 | Undetermined | High Energy Arc Fault | Transient | Temporary | N/A | Arc/electric discharge | Unknow | Unknow | Confined to the objective of origin | Yes
2 | 1/5/1999 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | Yes
3 | 1/14/1999 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No
4
5 | 5/18/1999 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the objective of origin | No
6 | 7/13/1999 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No
7 | 10/9/1999 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | Insulation | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
8 | 5/7/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
9 | 1/3/1990 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Not available | Yes
10
11 | 3/15/1990 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
12 | 3/30/1990 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
13 | 4/10/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
14 | 5/24/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No
15 | 5/27/1990 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
16 | 6/10/1990 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
17 | 6/28/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Not available | No
18 | 7/13/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
19 | 8/4/1990 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Interior finish | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
20 | 8/25/1990 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No
21 | 9/22/1990 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
22 | 12/3/1990 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No
23 | 12/19/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
24 | 12/22/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
25 | 1/11/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
26 | 2/14/1991 | Challenging | Misuse of heating devices | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
27 | 1/16/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Outside area, smoke only in fire plume |  | Confined to the object of origin | No
28 | 1/23/1991 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
29 | 2/23/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of originn (broad/extensive damage) | No
30 | 4/29/1991 | Challenging | Electrical arcing or sparks (non‐HEAF) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | Yes
31 | 6/15/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
32 | 6/27/1991 | Potentially Challenging | Personnel error during test and maintenance activity | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
33 | 8/1/1991 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
34 | 8/11/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
35 | 11/2/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
36 | 11/9/1991 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | Yes
37 | 11/15/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
38 | 3/21/1992 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes
39 | 5/3/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
40 | 5/22/1992 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
41 | 6/17/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
42 | 7/3/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
43 | 7/4/1992 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
44 | 7/13/1992 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
45 | 7/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
46 | 8/4/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
47 | 8/10/1992 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
48 | 9/4/1992 | Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
49 | 9/15/1992 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50 | 11/24/1992 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Structural component | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
51 | 2/5/1993 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
52 | 6/19/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
53 | 7/27/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
54 | 8/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | laming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
55 | 10/13/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No
56 | 10/21/1993 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
57 | 11/2/1993 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
58 | 12/25/1993 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to part of room or area of origin | Yes
59 | 1/29/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
60 | 2/3/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Ambient pressure, within a component | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
61 | 4/3/1994 | Challenging | Electrical arcing or sparks (non‐HEAF) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
62 | 6/6/1994 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
63 | 6/15/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
64 | 6/1/1994 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
65 | 7/2/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
66 | 7/11/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
67 | 7/29/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
68 | 8/10/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
69 | 8/29/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
70 | 10/26/1994 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
71 | 3/1/1995 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
72 | 4/14/1995 | Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
73 | 6/1/1995 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
74 | 6/10/1995 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | Yes
75 | 8/22/1995 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Unknown | Unknown | No damage | No
76 | 10/21/1995 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
77 | 12/10/1995 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
78 | 1/24/1996 | Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish | N/A | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | No
79 | 2/5/1996 | Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
80 | 2/29/1996 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
81 | 3/25/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
82 | 3/27/1996 | Potentially Challenging | Unknown | Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
83 | 4/4/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
84 | 4/19/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
85 | 5/13/1996 | Not Challenging | Unknown | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
86 | 6/23/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | Yes
87 | 8/19/1996 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
88 | 10/5/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
89 | 10/15/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
90 | 10/17/1996 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
91 | 11/19/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Unknown | No
92 | 11/22/1996 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
93 | 3/4/1997 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
94 | 8/1/1997 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Mixed | Other (Specify) | Flaming combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to the object of origin | No
95 | 10/9/1997 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
96 | 10/28/1997 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
97 | 6/10/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
98 | 10/8/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
99 | 10/10/1998 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
100 | 5/15/2000 | Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | Yes
101 | 9/3/2000 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
102 | 9/4/2000 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
103 | 9/22/2000 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
104 | 10/14/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
105 | 11/10/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
106 | 2/3/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
107 | 3/21/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Cleaning solvents or paint | Contained within component | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
108 | 4/6/2001 | Not Challenging | Unknown |  | Unknown |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to part of room or area of origin | No
109 | 4/24/2001 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
110 | 6/25/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
111 | 8/2/2001 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
112 | 8/3/2001 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
113 | 6/12/2002 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
114 | 8/21/2002 | Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
115 | 8/22/2002 | Challenging | Mechanical malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
116 | 10/3/2002 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
117 | 10/9/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
118 | 1/15/2003 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
119 | 3/18/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No
120 | 4/7/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | No damage | No
121 | 4/26/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
122 | 4/29/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
123 | 10/16/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Not available | No
124 | 10/28/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
125 | 1/6/2004 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | Yes
126 | 5/21/2004 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
127 | 6/18/2004 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
128 | 8/31/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
129 | 11/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
130 | 12/14/2004 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | No damage | No
131 | 1/14/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
132 | 3/4/2005 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
133 | 5/4/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
134 | 6/27/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
135 | 8/25/2005 | otentially Challenging | Electrical Failure (overheating, spark, HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light – visibility reduced, but all areas of the space can be seen | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
136 | 10/25/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
137 | 10/29/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No
138 | 2/11/2006 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Interior finish | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
139 | 2/24/2006 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Other (Specify) | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
140 | 3/20/2006 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
141 | 5/1/2006 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent） | No
142 | 5/24/2006 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
143 | 8/15/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to room of origin | No
144 | 10/30/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
145 | 11/11/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
146 | 2/27/2007 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Not available | No
147 | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
148 | 4/6/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition） | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No
149 | 4/8/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
150 | 4/25/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No
151 | 8/1/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No
152 | 10/23/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No
153 | 8/16/2008 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | Yes
154 | 9/20/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin
155 | 11/17/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | No damage | No
157 | 2/1/2009 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
158 | 6/26/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
159 | 1/16/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | Yes
160 | 2/7/2009 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to fire rated compartment of origin | No
161 | 4/22/2009 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
162 | 8/5/2009 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Single Cable Tray | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to floor of origin | No
163 | 10/12/2009 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
164 | 3/28/1990 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent） | No
168 | 11/13/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Mixed | Unknown | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
169 | 11/13/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
170 | 11/21/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes
172 | 12/7/2003 | Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to room of origin | No
173 | 12/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Overheating – no smoldering or flaming combustion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
174 | 12/30/2003 | Not Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
175 | 11/22/2009 | Challenging | Electrical malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to part of room or area of origin | No
176 | 12/12/2009 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
181 | 2/13/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage） | No
184 | 6/27/1997 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No
185 | 3/23/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
186 | 5/14/1998 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
187 | 8/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No
188 | 8/24/1999 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
189 | 10/14/1996 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to part of room or area of origin | No
190 | 3/18/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
191 | 11/11/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
192 | 5/15/1999 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
193 | 7/31/1991 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
194 | 5/22/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Contained within reservoir | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
195 | 3/21/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
199 | 1/22/1990 | Potentially Challenging |  | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
200 | 2/6/1990 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
201 | 3/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
202 | 3/23/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
203 | 4/6/1990 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
204 | 4/9/1990 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
206 | 6/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
207 | 7/15/1990 | Undetermined (PC-CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
208 | 8/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
209 | 8/22/1990 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
210 | 10/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
211 | 11/2/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
212 | 12/5/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
214 | 3/8/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
215 | 3/11/1991 | Not Challenging |  | In‐Situ | Other (specify) |  | Flaming combustion – external to component |  |  | Confined to part of room or area of origin
216 | 7/12/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
217 | 7/19/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
218 | 9/12/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No
219 | 9/27/1991 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
220 | 10/20/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
221 | 10/23/1991 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
222 | 2/1/1992 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
223 | 3/3/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
224 | 3/8/1992 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
225 | 3/23/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
226 | 4/17/1992 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
227 | 6/9/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
228 | 8/14/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
229 | 8/21/1992 | Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable Tray | Other (specify) | Unknown | Unknown | Confined to the object of origin | Yes
230 | 8/31/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
231 | 10/22/1992 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
232 | 10/27/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
233 | 11/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
234 | 12/16/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
235 | 12/30/1992 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
236 | 1/6/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
237 | 3/19/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
238 | 4/1/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
239 | 7/14/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
240 | 7/19/1993 | Undetermined (PC‐CH） | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
241 | 11/3/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
242 | 11/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
243 | 12/1/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
244 | 12/7/1993 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
245 | 12/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
246 | 1/12/1994 | Challenging | Personnel error: Misuse of material ignited | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to room of origin | No
247 | 1/12/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
248 | 3/5/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
249 | 3/7/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
250 | 7/19/1994 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
251 | 10/11/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
252 | 3/18/1995 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
253 | 7/6/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
254 | 9/25/1995 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
255 | 11/19/1995 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | No
256 | 7/22/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
257 | 10/22/1997 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
258 | 11/3/1997 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | No
259 | 11/26/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
260 | 2/3/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
261 | 5/11/1998 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
262 | 2/19/1999 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
263 | 4/25/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
264 | 10/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Unknown | No
265 | 9/23/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
266 | 11/9/2006 | Potentially Challenging | Unknown | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
267 | 6/1/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
268 | 4/7/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
269 | 12/12/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
270 | 11/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
271 | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
272 | 4/17/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Contained within reservoir | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes
273 | 5/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
274 | 5/7/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
275 | 10/14/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
276 | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
277 | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
278 | 1/5/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
280 | 11/19/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
282 | 4/23/2001 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
283 | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
284 | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
285 | 11/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
286 | 4/20/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
287 | 8/10/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
288 | 10/10/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
289 | 5/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
290 | 8/22/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
292 | 10/8/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
293 | 10/14/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
294 | 10/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
295 | 10/22/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
296 | 10/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
297 | 11/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
298 | 12/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
299 | 3/4/2008 | Not Challenging | Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
300 | 3/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
302 | 12/21/1999 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
303 | 3/1/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
305 | 6/21/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
306 | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
307 | 10/17/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
308 | 10/14/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
309 | 10/23/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
310 | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
311 | 12/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
312 | 10/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
313 | 11/9/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
314 | 2/10/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
316 | 8/17/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
317 | 9/27/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
318 | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
319 | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
320 | 10/24/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
321 | 10/31/2000 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
322 | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
324 | 1/12/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
325 | 3/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
326 | 3/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
327 | 1/1/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
328 | 9/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
329 | 9/25/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
330 | 9/27/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
332 | 4/15/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
333 | 5/11/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
335 | 8/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
337 | 8/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
338 | 7/25/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
340 | 8/7/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
341 | 2/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
342 | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
343 | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
344 | 10/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
345 | 4/25/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
346 | 3/1/2002 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
349 | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
350 | 7/11/2002 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
351 | 9/26/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
352 | 2/28/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
353 | 1/21/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
354 | 10/1/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
355 | 3/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
356 | 4/19/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
357 | 1/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
358 | 5/2/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
359 | 3/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
360 | 7/25/2001 | Not Challenging | Mechanical equipment malfunction/failure |  |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
361 | 2/4/2002 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
362 | 4/16/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
363 | 5/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
364 | 10/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
365 | 8/7/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
366 | 1/25/2006 | Not Challenging | Personnel error: Misuse of heating devices | Liquid | Lube Oil or grease |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
367 | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
368 | 10/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
372 | 9/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
373 | 10/5/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
374 | 10/13/2009 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
375 | 10/15/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
376 | 6/5/2004 | Not Challenging |  | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
377 | 8/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
378 | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
379 | 10/2/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
380 | 10/29/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
381 | 3/6/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
384 | 3/23/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
385 | 4/14/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | Yes
386 | 6/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
387 | 7/24/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
388 | 7/25/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
389 | 10/17/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
390 | 10/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
392 | 10/30/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
393 | 10/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
394 | 2/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
397 | 5/2/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
398 | 7/7/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
399 | 12/24/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
400 | 3/28/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
401 | 6/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
404 | 6/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
405 | 8/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
406 | 6/12/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
407 | 12/1/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
408 | 6/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
409 | 9/21/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Other (specify) | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
410 | 7/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
411 | 3/8/2001 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
412 | 7/15/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
416 | 10/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
418 | 10/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
419 | 4/5/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
420 | 6/24/2001 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
421 | 7/1/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
422 | 3/7/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
423 | 6/23/2003 | Undetermined (PC‐CH) | Unknown | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
424 | 3/10/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
426 | 9/17/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
427 | 2/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
428 | 9/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A |  | Unknown | Unknown | Confined to the object of origin | No
429 | 3/12/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
430 | 10/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
431 | 4/3/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
436 | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
437 | 2/3/2001 | Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | High – protective clothing needed for room entry | Confined to room of origin | Yes
438 | 6/24/2001 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | Yes
439 | 10/2/2002 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a component | Explosion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
440 | 1/2/2003 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
441 | 11/23/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
442 | 2/4/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
443 | 3/3/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
444 | 6/28/2004 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes
445 | 8/30/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
446 | 10/5/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
447 | 10/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
448 | 11/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
449 | 12/8/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
450 | 12/13/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
451 | 12/13/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
452 | 12/18/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
453 | 6/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
454 | 6/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
455 | 6/6/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
456 | 7/7/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
457 | 2/17/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
458 | 5/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
459 | 5/10/2006 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
460 | 9/7/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
461 | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
462 | 10/18/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
463 | 11/1/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
464 | 12/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
465 | 1/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
466 | 2/2/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
467 | 2/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
468 | 2/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
469 | 3/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
470 | 6/29/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
471 | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
472 | 7/17/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
473 | 8/4/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
474 | 8/21/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin
475 | 9/27/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
476 | 12/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
477 | 2/23/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No
478 | 3/30/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
479 | 3/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
480 | 4/7/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
481 | 6/29/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
482 | 2/8/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
483 | 11/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
484 | 11/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
485 | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
486 | 8/27/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
487 | 1/13/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
488 | 10/16/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
491 | 4/12/2000 | Undetermined (NC‐PC) | Unknown | In‐Situ | Structural component | N/A |  | Unknown | Unknown | Unknown
492 | 10/19/2000 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
494 | 3/8/2000 | Undetermined(NC‐PC) | Unknown | In‐Situ | Structuralcomponen | N/A |  | Unknown | Unknown | Unknown | No
495 | 3/20/2003 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A |  | Unknown | Unknown | Unknown | No
496 | 5/19/2002 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specif | N/A | Flamingcombustion–internaltocomponent | Unknown | Unknown | Unknown | No
497 | 8/14/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipmen | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
498 | 12/19/2000 | Undetermined(PC‐CH) | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
499 | 12/17/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
500 | 3/12/2001 | Undetermined(PC‐CH) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Unknown | Unknown | Unknown | Unknown
501 | 1/24/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent |  | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
502 | 11/18/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Transient | Temporaryelectricalwiringorequipment | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
503 | 5/14/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
504 | 10/9/2002 | Undetermined(PC‐CH) | Unknown | Unknown | Unknown |  | Unknown | Unknown | Unknown | Unknown
505 | 9/13/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
506 | 9/12/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | No
508 | 3/14/2005 | NotChallenging |  |  |  |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
509 | 1/19/2005 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
511 | 7/16/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
512 | 7/20/2005 | NotChallenging |  | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
513 | 11/18/2005 | Undetermined(NC‐PC) |  | In‐Situ | Thermalinsulationmaterials | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
514 | 4/27/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion
515 | 10/5/2005 | Undetermined(PC‐CH) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
516 | 10/25/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
517 | 3/23/2006 | Undetermined(PC‐CH) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
518 | 3/30/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
519 | 5/4/2007 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A |  | Unknown | Unknown | Confinedtotheobjectoforigin | No
520 | 6/6/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
521 | 12/17/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
522 | 9/19/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
523 | 9/27/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
524 | 10/11/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
526 | 1/30/2009 | Undetermined(NC‐PC) | Unknown | In‐Situ | Other(specify) | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
527 | 11/10/2009 | Undetermined(NC‐PC) | Mechanicalequipmentmalfunction/failure | In‐Situ | Structuralcomponent | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
529 | 11/28/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | No
530 | 3/5/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
531 | 8/24/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
533 | 1/27/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
534 | 4/10/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
535 | 6/16/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A |  | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
536 | 8/24/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation
537 | 10/13/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
538 | 10/20/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
539 | 10/23/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
540 | 10/23/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
541 | 10/24/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
542 | 3/4/2000 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Thermalinsulationmaterials | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
543 | 8/27/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
544 | 12/13/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
545 | 6/5/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
546 | 10/9/2002 | NotChallenging |  | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
547 | 11/5/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
548 | 11/13/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Unkno |  |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Unknown | Unknown | Confinedtotheobjectoforigin
549 | 7/16/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
550 | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtotheobjectoforigin
551 | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
552 | 7/31/2003 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
553 | 6/24/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
554 | 6/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
555 | 7/27/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
556 | 10/14/2005 | NotChallenging |  | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | : Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
557 | 11/2/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
558 | 12/13/2005 | PotentiallyChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
559 | 9/12/2006 | Undetermined(NC‐PC | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
560 | 5/20/2006 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplumt | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
561 | 1/3/2005 | NotChallenging | Unknown | In‐Situ | Other(specify) | N/A | NoFire‐Falseactuationofdetectiondevice | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
562 | 10/9/2006 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A |  | Unknown | Unknown | Confinedtotheobjectoforigin
563 | 10/18/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
564 | 3/13/2007 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
565 | 4/25/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
566 | 7/2/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
567 | 7/31/2007 | Undetermined(NC‐PC) | Arc/electricdischarge | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
568 | 1/12/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
569 | 5/15/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
570 | 6/3/2008 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Structuralcomponent | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
571 | 9/29/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
572 | 12/23/2008 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
573 | 1/29/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
575 | 5/18/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
576 | 8/31/2009 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
577 | 9/16/2002 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
578 | 11/8/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
579 | 3/23/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
580 | 1/6/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
581 | 4/17/2002 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
582 | 9/3/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
584 | 10/8/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Nodamage
585 | 12/10/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
586 | 5/5/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
587 | 5/13/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Transient | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
588 | 11/30/2006 | Challenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Thermoset | SingleCable | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
590 | 2/20/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
591 | 7/19/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
592 | 6/11/2009 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
593 | 10/16/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
594 | 1/28/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
595 | 2/13/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
596 | 6/13/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
597 | 7/22/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
598 | 10/12/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
599 |  | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
600 | 1/17/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
601 | 10/28/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
602 | 9/29/2006 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
603 | 11/14/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
604 | 9/8/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
605 | 9/14/2001 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
606 | 10/31/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
607 | 11/13/2008 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
609 |  | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10273 | 10/18/2000 | NotChallenging | Personnelerrorduringtestandmaintenanceactivity | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10274 | 10/21/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ |  |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10276 | 12/15/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10277 | 12/22/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10278 | 4/4/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10279 | 4/14/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10280 | 4/17/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10282 | 8/12/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | NoFire‐Falseactuationofdetectiondevice | Unknown | Unknown | Confinedtotheobjectoforigin
10283 | 2/10/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10284 | 3/10/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10285 | 4/7/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10286 | 5/10/2004 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10287 | 5/19/2004 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10288 | 5/22/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10289 | 5/28/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10290 | 6/3/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10291 | 9/18/2004 | Undetermined(PC‐CH) | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
10292 | 1/13/2005 | NotChallenging | Mechanicalequipmentmalfunction/failure | Insulation | Otherelectricalorelectronicequipment | Other(Specify) | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10293 | 8/16/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10294 | 10/9/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10295 | 10/18/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10296 | 8/21/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10297 | 12/14/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10298 | 2/12/2009 | NotChallenging | Unknown | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10299 | 2/19/2009 | NotChallenging | Mechanicalequipmentmalfunction/failure | Gas | Hydrogen | Jetfromapressurizedsource | NoFire‐Falseactuationofdetectiondevice | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown
10300 | 6/25/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10302 | 3/10/2000 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10303 | 5/18/2001 | NotChallenging | Suspicious | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10304 | 4/8/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10305 | 10/25/2001 | NotChallenging | Electricalarcingorsparks(non‐HEAF) |  |  |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10307 | 10/3/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10308 | 9/19/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10309 | 4/18/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10310 | 1/29/2007 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10311 | 1/9/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10312 | 2/9/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10313 | 4/3/2009 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10315 | 10/18/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10316 | 11/22/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10317 | 9/23/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10318 | 10/16/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10319 | 1/7/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10320 | 5/25/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10321 | 6/1/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10322 | 12/10/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown
10323 | 12/11/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10324 | 12/30/200 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10326 | 1/24/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10327 | 6/21/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10328 | 7/17/2007 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Liquid | Other(specify) | Other(specify) | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10329 | 9/22/2008 | NotChallenging | Unknown | Unknown |  |  | Other(specify) | Unknown | Unknown | Unknown
10330 | 9/23/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10331 | 3/24/2009 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10334 | 3/30/2000 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
10336 | 10/2/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10337 | 10/11/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10338 | 9/13/2001 | Undetermined(PC‐CH) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10339 | 8/16/2004 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10341 | 5/21/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10343 | 8/25/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10344 | 10/1/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10345 | 1/25/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10349 | 9/24/2007 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10350 | 1/21/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10352 | 12/11/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10353 | 1/5/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10354 | 7/2/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Pressurizedinacontainer | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10355 | 4/26/2008 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10356 | 10/3/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10357 | 7/1/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10358 | 7/3/2002 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10359 | 11/16/2000 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10360 | 10/13/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10361 | 5/5/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10362 | 10/28/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10363 | 11/5/2009 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10364 | 6/30/2005 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10365 | 8/22/2008 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Unknown | Unknown | Confinedtotheobjectoforigin
10367 | 10/22/2000 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10368 | 6/28/2004 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10369 | 10/4/2002 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10370 | 4/11/2008 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10371 | 10/20/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10372 | 10/22/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10373 | 4/14/2005 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10374 | 7/11/2003 | PotentiallyChallenging | Flamingcombustion–externaltocomponent | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10376 | 3/23/2004 | Challenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10377 | 3/10/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Thermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10378 | 3/18/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10379 | 3/22/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10380 | 9/23/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10381 | 10/24/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10382 | 3/20/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10383 | 4/3/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10384 | 6/26/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10385 | 2/12/2002 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10386 | 3/1/2003 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10387 | 3/4/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10389 | 9/8/2003 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10392 | 4/5/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10393 | 11/7/2004 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10394 | 2/22/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage)
10395 | 7/13/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10396 | 7/14/2005 | NotChallenging | Unkno | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10397 | 10/12/2005 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Structuralcomponent | N/A | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10399 | 1/31/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10401 | 5/9/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient
10402 | 6/27/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Overheating–nosmolderingorflamingcombustion | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10403 | 10/31/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10404 | 12/5/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10405 | 1/20/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Unknown | Confinedtotheobjectoforigin
10406 | 5/5/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10407 | 6/3/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10409 | 12/12/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10410 | 2/13/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10411 | 3/8/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10412 | 2/17/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10413 | 5/17/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10414 | 8/31/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10416 | 4/1/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10417 | 4/17/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10418 | 2/15/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10419 | 4/12/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10420 | 4/17/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10421 | 6/20/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10422 | 8/25/2008 | NotChallenging | Unknown | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10423 | 9/3/2008 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10424 | 10/19/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10425 | 11/6/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10426 | 4/29/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10427 | 5/3/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10428 | 6/1/2000 | NotChallenging | Mechanicalequipmentmalfunction/failure | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10429 | 9/21/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10430 | 12/21/2000 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10432 | 10/22/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10433 | 12/10/2003 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10434 | 5/7/2004 | NotChallenging | :Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10435 | 7/8/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10436 | 8/11/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10437 | 5/9/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | NoFire‐Falseactuationofdetectiondevice | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10441 | 3/4/2009 | PotentiallyChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10442 | 3/9/2009 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtotheobjectoforigin
10443 | 7/25/2009 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10444 | 10/13/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10445 | 2/7/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10446 | 4/11/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10447 | 3/9/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10448 | 10/23/2001 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10449 | 5/17/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10450 | 6/19/2001 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | Cleaningsolventsorpaint | Unconfinedspill | Flamingcombustion–externaltocomponent | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10451 | 6/5/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown
10452 | 9/17/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10453 | 11/20/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10454 | 2/17/2003 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10455 | 3/22/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10456 | 7/19/2002 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10457 | 10/22/2002 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Unknown |  |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10458 | 1/7/2003 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Liquid | Other(specify) | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10459 | 2/7/2003 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10460 | 4/9/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10461 | 3/6/2003 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10462 | 2/5/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10463 | 3/1/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10464 | 3/30/2005 | Challenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Containedwithinreservoir | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Unknown | Confinedtotheobjectoforigin
10465 | 9/30/2004 | NotChallenging | Unknown | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10466 | 8/31/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | In‐Situ |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10467 | 4/7/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10468 | 10/27/2005 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Structuralcomponent |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10469 | 3/23/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10470 | 5/5/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | re: Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10471 | 12/26/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10472 | 9/25/2007 | Challenging | HighEnergyArcFault(HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Explosion | Unknown | Unknown | Confinedtotheobjectoforigin
10473 | 1/23/2007 | NotChallenging | Unknown | In‐Situ | Other(specify) | N/A | Other(specify) | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown
10474 | 2/23/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10476 | 4/10/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10477 | 6/7/2007 | PotentiallyChallenging | Unknown | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10478 | 7/10/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10479 | 7/23/2008 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10480 | 7/23/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10482 | 10/22/2006 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10483 | 4/10/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10484 | 4/16/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10485 | 4/21/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10486 | 7/28/2007 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) | N/A | Mechanicalequipmentmalfunction/failure | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10487 | 9/4/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtopartofroomorareaoforigin
10488 | 9/24/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10489 | 4/6/2008 | Challenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10490 | 4/9/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Insulation | Typenotspecified | Unknown | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10491 | 4/29/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10492 | 9/30/2008 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage)
10493 | 10/23/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) | N/A | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10496 | 5/14/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10497 | 7/31/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10498 | 9/26/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10499 | 10/16/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Overheating–nosmolderingorflamingcombustion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10504 | 3/15/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10505 | 3/16/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10507 | 3/14/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10508 | 3/28/2001 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10509 | 4/1/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10510 | 4/10/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10512 | 6/22/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10513 | 8/20/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10514 | 8/26/2001 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10515 | 9/30/2001 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10516 | 11/20/2001 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10517 | 8/5/2002 | NotChallenging | Unknown | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10518 | 8/26/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
10519 | 9/25/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10520 | 11/26/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent | N/A | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtopartofroomorareaoforigin
10521 | 9/10/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10522 | 11/2/2003 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10523 | 11/9/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10524 | 1/7/2004 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10525 | 5/10/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10526 | 5/30/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10528 | 9/8/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10529 | 1/25/2006 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10530 | 3/15/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10531 | 3/31/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10532 | 6/28/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10533 | 2/1/2001 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10534 | 3/21/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Unknown |  |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10535 | 3/31/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10536 | 12/12/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10537 | 2/17/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10538 | 4/1/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10539 | 1/19/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10540 | 2/4/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Extendedbeyondstructureoforigin
10541 | 3/24/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10542 | 7/9/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10543 | 9/3/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10544 | 1/17/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10545 | 5/9/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
10546 | 3/15/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10547 | 1/22/2004 | NotChallenging |  | Insulation | Typenotspecified | SingleCable | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10548 | 6/25/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10549 | 10/8/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10550 | 9/3/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10551 | 7/14/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10552 | 7/8/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10553 | 4/17/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10554 | 5/3/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10555 | 5/5/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10556 | 5/11/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10557 | 1/13/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10558 | 1/19/2005 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10559 | 3/7/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10560 | 3/29/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10561 | 4/4/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10562 | 5/23/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10563 | 7/11/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10564 | 8/10/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10565 | 8/15/2005 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10566 | 9/15/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10567 | 12/19/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10568 | 1/12/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10569 | 2/8/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Unknown | Other(specify) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10570 | 2/13/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10571 | 3/5/2006 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10572 | 4/13/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
10573 | 7/5/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10574 | 7/17/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10575 | 7/18/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10576 | 7/26/2006 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Gas | Hydrogen | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10577 | 10/28/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | MultipleCablesNotInTrayorBundle | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10579 | 4/4/2008 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients | N/A | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10580 | 4/26/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10581 | 11/19/2008 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10582 | 12/9/2005 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) | N/A | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
10583 | 9/1/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) | N/A | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
10584 | 7/27/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Explosion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10585 | 4/24/2003 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment | N/A | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
10586 | 1/19/2000 | : Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10587 | 8/10/2000 | Not Challenging | Not Challenging | Gas | Hydrogen | Pressurized in a container | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
10588 | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
10589 | 2/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient (Liquid) | Fuel Oil | Unconfined spill | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10590 | 10/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume |  | No
10591 | 10/8/2002 | Not Challenging | vElectrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10592 | 1/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10593 | 7/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10594 | 1/25/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10595 | 2/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10596 | 11/4/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10598 | 1/3/2006 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10599 | 3/25/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10600 | 2/18/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
10601 | 2/16/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10602 | 2/13/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (specify) | Other (specify) | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10604 | 5/14/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10605 | 1/31/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10606 | 5/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (specify) | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10607 | 12/27/2004 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to componen | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | High – protective clothing needed for room entry | Confined to part of room or area of origin | Yes
10609 | 9/7/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10611 | 8/20/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10614 | 2/25/2004 | Undetermined (NC‐PC) FireID: 10614 | [5 empty] | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still
10615 | 10/15/2005 | Undetermined (NC‐PC) | [5 empty] | possible with SCBA
10617 | 2/14/2003 | Undetermined (NC‐PC) | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a compartment | Explosion | Unknown | Unknown | Unknown
10618 | 2/15/2000 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
10619 | 5/24/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
10620 | 8/9/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10621 | 8/22/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | No damage | No
10622 | 6/25/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10623 | 8/8/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
10624 | 10/26/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No
10625 | 9/28/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
10626 | 12/11/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10627 | 12/12/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
10628 | 12/30/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10630 | 6/6/2007 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Flaming combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10631 | 11/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
10632 | 3/3/2000 | Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
10633 | 3/7/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10636 | 9/26/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable Tray | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10638 | 3/5/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10639 | 2/16/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
10641 | 3/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Flaming combustion – internal to component | Flaming combustion – internal to component | Confined to the object of origin | No
10642 | 3/14/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10643 | 5/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10644 | 11/3/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10645 | 4/11/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10646 | 7/17/2003 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10647 | 8/22/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
10648 | 3/12/2004 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10649 | 3/15/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10650 | 3/20/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10652 | 3/10/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10653 | 4/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10654 | 2/5/2007 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10656 | 2/22/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10657 | 6/29/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10658 | 12/29/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10660 | 11/6/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10664 | 10/2/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10665 | 11/3/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10666 | 4/18/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10667 | 4/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10668 | 4/22/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10669 | 5/20/2001 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10670 | 6/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10671 | 6/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10672 | 6/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10673 | 9/4/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10674 | 12/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10675 | 12/31/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10676 | 3/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10677 | 4/4/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10678 | 5/29/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
10679 | 1/9/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10680 | 7/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10681 | 11/12/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Other (specify) | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10682 | 4/2/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10683 | 4/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10684 | 4/6/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10685 | 4/11/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10686 | 4/13/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10687 | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10688 | 10/31/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10689 | 1/26/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10690 | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | n‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10691 | 2/25/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10693 | 3/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10694 | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10695 | 7/27/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10696 | 8/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
10697 | 2/25/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
10698 | 4/18/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10699 | 4/24/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | n‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10700 | 7/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient
10701 | 8/25/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10702 | 2/8/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10703 | 11/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10704 | 3/28/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10705 | 12/3/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10706 | 12/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10707 | 8/8/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10708 | 9/22/2004 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10709 | 2/1/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10710 | 11/21/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10711 | 1/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10712 | 10/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
10713 | 3/25/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10715 | 2/5/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10716 | 7/26/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10717 | 4/12/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10718 | 5/20/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10719 | 6/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10720 | 4/8/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10721 | 8/26/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10722 | 9/3/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10723 | 10/4/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10724 | 10/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10725 | 10/29/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
10726 | 11/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10727 | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10728 | 8/23/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10729 | 4/3/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Lube Oil or grease | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10730 | 3/16/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
10731 | 6/27/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10732 | 4/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
10733 | 4/7/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Unknown | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10734 | 4/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10735 | 4/28/2006 | Not Challenging | Unknown | In‐Situ | Other (specify) | N/A | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10736 | 12/6/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10737 | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
10738 | 8/22/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
10739 | 4/24/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10740 | 10/8/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10741 | 9/21/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10742 | 4/11/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10743 | 4/19/2001 | Unknown | In‐Situ | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | No smoke present | Unknown | Confined to the object of origin | No
10744 | 8/17/2001 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
10745 | 7/25/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10746 | 5/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
10747 | 1/15/1999 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
10748 | 5/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10749 | 9/10/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10750 | 2/28/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
10751 | 1/28/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20264 | 1/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20265 | 2/2/1990 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No
20266 | 2/19/1990 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Other (specify) | Unknown | Unknown | No damage | No
20267 | 3/12/1990 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20268 | 4/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20269 | 4/30/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
20270 | 6/7/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20271 | 7/9/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20272 | 9/10/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20273 | 9/18/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
20274 | 10/9/1990 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
20275 | 10/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20276 | 10/12/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20277 | 11/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (specify | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20278 | 11/24/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20279 | 11/28/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
20280 | 12/5/1990 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
20281 | 6/24/1991 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No
20282 | 9/17/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
20283 | 10/3/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20284 | 10/14/1991 | Undetermined (NC‐PC) | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20285 | 10/25/1991 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
20286 | 1/23/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20287 | 2/29/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20288 | 3/9/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No
20289 | 3/16/1992 | Undetermined (NC‐PC) | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20290 | 4/26/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Unknown | Unknown | No damage | No
20291 | 4/28/1992 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20292 | 6/25/1992 | Undetermined (NC‐PC) | Personnel error: Misuse of material ignited | Gas | Hydrogen | Jet from a pressurized source | Other (specify) | Unknown | Unknown | Unknown | No
20293 | 9/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20294 | 10/5/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20295 | 10/12/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20296 | 10/23/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20297 | 11/17/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20298 | 1/11/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20299 | 3/9/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20300 | 3/30/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Insulation | Type not specified | Unknown | Unknown | Unknown | Unknown | Confined to the object of origin | No
20301 | 4/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Plastic Sheets | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20302 | 7/25/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
20303 | 10/14/1993 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
20304 | 11/2/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20305 | 11/18/1993 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20306 | 12/30/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20307 | 1/25/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20308 | 3/9/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20309 | 3/11/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20310 | 3/26/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20311 | 4/4/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20312 | 7/27/1994 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify | Unknown | Unknown | Unknown | No
20313 | 9/29/1994 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Other (specify | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
20314 | 12/19/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20315 | 2/20/1995 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20316 | 2/24/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20317 | 4/10/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Unknown | No
20318 | 8/9/1995 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
20319 | 8/15/1995 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
20320 | 3/21/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20321 | 7/10/1996 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20322 | 9/13/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
20323 | 1/8/1997 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
20324 | 8/12/1997 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20325 | 1/16/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20326 | 10/12/1998 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
20327 | 11/2/1998 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20328 | 5/6/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
20329 | 9/1/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20330 | 10/3/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
20331 | 11/4/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
20332 | 12/14/1999 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
20333 | 1/12/1990 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20334 | 2/20/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Unknown | Unknown | Unknown | No
20335 | 4/13/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Other (specify) | Unknown | Unknown | No damage | No
20336 | 2/14/1991 | Undetermined (NC‐PC) | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
20337 | 4/21/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Other (specify) | Unknown | Unknown | No damage | No
20338 | 10/11/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20339 | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20340 | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Unknown | Unknown | Unknown | Confined to the object of origin | No
20341 | 3/31/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20342 | 4/30/1993 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20343 | 8/13/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Other (specify) | Unknown | Unknown | No damage | No
20344 | 2/20/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
20345 | 3/28/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Unknown | Unknown | No damage | No
20346 | 3/30/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to part of room or area of origin | No
20347 | 4/15/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20348 | 4/16/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Unknown | Unknown | Unknown | Unknown | No
20349 | 4/23/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20350 | 6/9/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to the object of origin | No
20351 | 6/21/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20352 | 6/23/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Confined to the object of origin (localized/single subcomponent) | No
20353 | 7/13/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20354 | 10/8/1994 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Bundle | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20355 | 10/31/1994 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20356 | 2/19/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Unknown | No
20357 | 5/24/1995 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No
20358 | 1/23/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
20359 | 3/3/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
20360 | 5/25/1996 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to fire rated compartment of origin | No
20361 | 1/7/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20362 | 3/2/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
20363 | 7/27/1997 | Not Evaluated | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Unknown | No
20364 | 12/4/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
20365 | 1/13/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Interior finish | N/A | Unknown | Unknown | Unknown | Unknown | No
20366 | 2/6/1998 | Undetermined (NC‐PC) | Unknown | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | Unknown | No
20367 | 2/24/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Leak ‐ Oil soaked Insulation | Unknown | Unknown | Unknown | Unknown | No
20368 | 6/7/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20369 | 6/14/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify | Unknown | Unknown | Unknown | No
20370 | 7/1/1998 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20371 | 9/9/1998 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Unknown | [6 empty] | No
20372 | 11/23/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20373 | 3/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Unknown | No
20374 | 3/19/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20375 | 3/29/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
20376 | 7/29/1999 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
20377 | 2/8/2000 | Challenging | Personnel error: Misuse of heating devices | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
20378 | 2/25/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
20379 | 6/20/2000 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20380 | 8/16/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
20381 | 10/17/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment | N/A | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20382 | 10/23/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20383 | 11/5/2000 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
20385 | 12/27/2000 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
30265 | 8/5/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30266 | 1/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30268 | 8/9/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30269 | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30270 | 3/16/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30271 | 9/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30272 | 7/9/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30275 | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30276 | 7/24/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30277 | 12/3/2007 | Potentially Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30278 | 10/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30279 | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30281 | 6/5/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30282 | 11/26/2001 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30283 | 3/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30284 | 3/12/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30285 | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30286 | 6/18/2009 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Unknown | No
30287 | 10/1/2009 | Potentially Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
30288 | 4/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30289 | 7/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
30290 | 1/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30291 | 3/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30292 | 6/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30293 | 8/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30294 | 11/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30295 | 3/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30296 | 11/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
30297 | 8/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30298 | 4/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30299 | 4/25/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30300 | 5/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30301 | 6/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30302 | 1/26/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30303 | 6/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30304 | 11/29/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30305 | 12/14/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ |  |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30306 | 1/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30307 | 3/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30308 | 4/3/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30309 | 7/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30310 | 9/7/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30311 | 9/24/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30312 | 3/29/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30313 | 11/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30314 | 12/19/2001 | Undetermined (PC‐CH | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
30316 | 3/16/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30317 | 4/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30318 | 5/16/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Fuel Oil |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30319 | 7/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30320 | 5/8/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30321 | 11/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30322 | 10/28/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30323 | 12/9/2006 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30324 | 1/11/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30325 | 11/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
30326 | 5/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30327 | 3/6/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | n‐Situ | Structural component | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30330 | 4/30/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30331 | 10/12/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30332 | 4/6/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
30333 | 7/31/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient (Liquid) | Cleaning solvents or paint | Contained within reservoir | : Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30334 | 9/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30335 | 1/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30338 | 3/30/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30339 | 6/21/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30340 | 11/10/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30341 | 1/2/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30342 | 2/11/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Other (other personnel error, natural effect, etc. specify in comments) | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30343 | 5/3/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30344 | 1/23/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30345 | 8/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30346 | 10/22/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30347 | 3/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30348 | 11/22/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30350 | 7/26/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30351 | 5/14/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30354 | 2/8/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic euiment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes
30355 | 2/17/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30356 | 11/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30357 | 6/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30358 | 8/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | Other electrical or electronic equipment | In‐Situ | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30359 | 1/10/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30360 | 4/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30361 | 4/11/2001 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30362 | 12/16/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30363 | 5/5/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30364 | 5/26/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30365 | 9/8/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30366 | 12/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30367 | 3/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30368 | 7/6/2004 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Structural component | N/A | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30369 | 10/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30370 | 10/31/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30371 | 11/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
30372 | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
30373 | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30374 | 11/30/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30375 | 5/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30376 | 10/14/2007 | Not Challenging | Not Challenging | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30377 | 11/3/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30378 | 11/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30379 | 11/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30380 | 12/17/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30381 | 4/7/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30382 | 5/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30383 | 2/11/2009 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30384 | 10/18/2000 | Not Challenging | Not Challenging | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30385 | 10/27/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30386 | 5/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30387 | 5/24/2001 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30388 | 4/6/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30389 | 10/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Contained within component | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30390 | 5/7/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30391 | 11/13/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30392 | 3/20/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30393 | 3/24/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30394 | 2/2/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30395 | 3/21/2004 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Hot work (cutting/welding/grinding/etc.) | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
30396 | 3/22/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30397 | 4/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30398 | 10/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30400 | 9/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30401 | 2/6/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30402 | 4/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30403 | 9/24/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30404 | 4/21/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30405 | 10/26/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown |  |  | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
30407 | 4/30/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30408 | 3/19/2001 | Potentially Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30409 | 8/21/2000 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30410 | 10/25/2000 | Potentially Challenging | Unknown | In‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30411 | 3/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30412 | 4/25/2002 | Potentially Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30413 | 4/25/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30414 | 3/28/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30415 | 4/29/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30416 | 4/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30417 | 3/20/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30418 | 3/18/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30419 | 10/4/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30420 | 3/18/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30421 | 3/5/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin | No
30422 | 11/27/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | No
30423 | 3/17/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30424 | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30425 | 10/7/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30426 | 10/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (broad/extensive damage) | No
30429 | 5/6/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
30430 | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
30431 | 6/18/2006 | Not Challenging | Unknown | Unknown |  |  | No Fire ‐ False actuation of detection device | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
30433 | 6/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30434 | 8/12/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30435 | 8/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30436 | 9/30/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30437 | 10/6/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
30438 | 5/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30439 | 3/21/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30440 | 10/26/2005 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30441 | 9/5/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30442 | 9/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30443 | 12/31/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30444 | 3/13/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30445 | 10/18/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30446 | 4/1/2003 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30447 | 7/11/2004 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30449 | 10/8/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30452 | 8/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30453 | 1/30/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Contained within component | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
30454 | 6/22/2009 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30455 | 3/14/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30456 | 3/7/2001 | Potentially Challenging | Potentially Challenging | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30457 | 10/24/2006 | Undetermined (NC‐PC) |  | Transient (Gas) | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30458 | 1/18/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30459 | 3/9/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30460 | 3/18/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
30461 | 3/23/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30462 | 5/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30463 | 10/28/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30464 | 9/23/2008 | Not Challenging | Unknown | In‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30465 | 9/24/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30469 | 11/11/2007 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30471 | 4/4/2008 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30472 | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
30473 | 9/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30474 | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
30475 | 4/26/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30476 | 10/12/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30478 | 9/9/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
30479 | 9/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30480 | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30481 | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30482 | 10/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
30483 | 10/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
30485 | 9/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30487 | 12/4/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30489 | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30493 | 7/24/2008 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
30498 | 6/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ |  | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
30500 | 5/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30502 | 10/8/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30503 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30504 | 3/17/2002 | Not Challenging | : Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30505 | 3/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30506 | 12/17/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30507 | 7/26/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30508 | 3/26/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30509 | 8/11/2009 | Not Challenging | False actuation of detector, no ignition or overheat condition |  |  |  | No Fire ‐ False actuation of detection device |  |  | : No damage | No
30510 | 1/17/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30511 | 1/23/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30512 | 2/15/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30513 | 5/27/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30514 | 3/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Other electrical or electronic equipment | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30516 | 6/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30517 | 7/29/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
30519 | 1/5/2009 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
30520 | 3/1/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30521 | 9/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30522 | 9/12/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30523 | 9/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30524 | 12/14/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No
30525 | 3/7/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30526 | 6/12/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30527 | 2/1/2002 | Not Challenging | Unknown | In‐Situ | Structural component |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30528 | 2/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30529 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30530 | 3/23/2002 | Not Challenging | Unknown | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30531 | 4/17/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30532 | 6/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
30533 | 2/10/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30534 | 3/4/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
30535 | 4/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30536 | 9/13/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) |  |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30537 | 6/15/2005 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30538 | 1/23/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30539 | 2/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component |  |  | Confined to the object of origin | No
30540 | 5/2/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30541 | 7/6/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30542 | 7/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30543 | 8/24/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30544 | 10/4/2005 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30545 | 1/16/2006 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
30546 | 4/26/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30547 | 4/19/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30548 | 7/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30549 | 9/5/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component |  |  | Confined to the object of origin | No
30550 | 10/5/2006 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30551 | 10/20/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30552 | 5/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30553 | 8/28/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30554 | 10/17/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30555 | 4/1/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30556 | 4/4/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30557 | 4/30/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30558 | 10/20/2008 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Unknown | No
30559 | 11/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30560 | 2/4/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30561 | 4/3/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30562 | 3/17/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30563 | 3/9/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30564 | 11/18/2003 | Not Challenging | Unknown | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
30565 | 2/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | No damage | No
30566 | 9/11/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30567 | 10/17/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30568 | 1/19/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30569 | 10/16/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30570 | 3/28/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
30571 | 1/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
30572 | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30573 | 6/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30574 | 11/2/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
30576 | 8/15/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
30577 | 3/3/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30578 | 2/27/2003 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
30579 | 6/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30580 | 6/21/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30581 | 6/19/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to componen | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30582 | 6/7/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to componen | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
30583 | 6/30/2003 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
30584 | 5/24/2001 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30585 | 5/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30586 | 1/11/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
30587 | 3/4/2009 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No
30588 | 5/14/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30589 | 10/11/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30590 | 12/22/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30591 | 10/17/2005 | Not Challenging | Personnel error: Misuse of heating devices | Unknown |  |  | Other (specify) | Unknown | Unknown | Unknown | No
30593 | 2/7/2008 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30594 | 6/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
30595 | 10/10/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30596 | 10/17/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30597 | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30598 | 11/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30599 | 3/23/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30600 | 11/9/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30601 | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30602 | 5/19/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30603 | 1/13/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30604 | 5/28/2005 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30605 | 9/19/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30606 | 12/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30607 | 3/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30608 | 1/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
30609 | 4/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30610 | 7/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Confined to the object of origin | No
30693 | 2/3/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30694 | 8/10/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No
30695 | 9/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No
30696 | 9/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30697 | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30698 | 2/22/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30699 | 3/7/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30700 | 4/19/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30701 | 8/13/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | No damage | No
30702 | 9/11/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30703 | 10/2/2007 | Not Challenging | Other (personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30704 | 10/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30705 | 9/20/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30706 | 9/20/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30707 | 10/1/2000 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30708 | 2/6/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30709 | 7/13/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30710 | 9/19/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
30711 | 11/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | No damage |  | Smoldering combustion – internal to component |  |  | Confined to the object of origin | No
30712 | 4/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30713 | 4/29/2002 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30716 | 9/2/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30717 | 12/10/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30718 | 4/15/2003 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30719 | 6/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30720 | 7/2/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient (Liquid) | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30721 | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Other (specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30722 | 10/19/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | Unknown | Confined to the object of origin | No
30723 | 11/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30724 | 11/3/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30725 | 4/12/2000 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
30726 | 5/19/2000 | Not Challenging | Transient | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30727 | 10/30/2000 | Potentially Challenging | Trash (i.e., solid refuse collected for disposal) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
30728 | 12/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30729 | 12/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30730 | 3/5/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
30731 | 3/19/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component |  |  | No damage | No
30732 | 12/3/2001 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30733 | 6/27/2002 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
30734 | 8/26/2002 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30735 | 3/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify |  | Flaming combustion – internal to component | Unknown | Unknown | No damage | No
30736 | 3/13/2003 | Undetermined (PC‐CH) | Unknown | Unknown |  | Unknown | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
30737 | 5/12/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30738 | 9/23/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | In‐Situ |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | No
30739 | 3/29/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component |  | None or insignificant – temperature at or close to ambient | No damage | No
30740 | 2/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No
30741 | 3/24/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30742 | 4/15/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30743 | 4/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30744 | Hot work (cutting/welding/grinding/etc.) | Not Challenging | Unknown | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30745 | 10/10/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30746 | 10/28/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30747 | 11/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30748 | 11/27/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30749 | 1/9/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30750 | 5/9/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30751 | 3/28/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30752 | 4/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within reservoir | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30753 | 5/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30754 | 2/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30755 | 4/7/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
30756 | 11/23/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Hot work (cutting/welding/grinding/etc.) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
30757 | 8/24/2009 | Undetermined (NC‐PC) | Unknown | Transient | Hot work (cutting/welding/grinding/etc.) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
30758 | 9/3/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
40730 | 10/27/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
40731 | 2/13/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
40732 | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
40733 | 3/14/2001 | Potentially Challenging | Unknown | Unknown | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
40734 | 3/19/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
40735 | 4/4/2001 | Potentially Challenging | Unknown | Gas | Hydrogen | Confined liquid spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
40736 | 4/15/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
40737 | 4/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | Liquid | Liquid | Other (specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
40738 | 6/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
40739 | 7/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40740 | 3/3/2003 | Not Challenging | Unknown | Unknown |  |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
40741 | Confined to the object of origin | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
40742 | 7/7/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Hot work (cutting/welding/grinding/etc.) | N/A | Smoldering combustion – internal to componen | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40743 | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Hot work (cutting/welding/grinding/etc.) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
40744 | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Hot work (cutting/welding/grinding/etc.) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40745 | 10/20/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
40746 | 8/15/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40747 | 4/17/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40748 | 11/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40749 | 6/13/2008 | Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to room of origin | No
40750 | 11/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
50356 | 1/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50357 | 3/21/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50358 | 6/1/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50359 | 8/24/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50360 | 12/20/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50361 | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50362 | 7/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50364 | 10/4/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50365 | 3/4/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50366 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Unknown | No Fire ‐ False actuation of detection device | Unknown | Unknown | Confined to the object of origin | No
50367 | 3/14/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50368 | 6/6/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50369 | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50370 | 10/23/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50371 | 11/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50372 | 5/9/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50373 | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50374 | 4/22/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50375 | 9/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50376 | 9/30/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50377 | 7/2/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50378 | 7/27/2005 | Other electrical or electronic equipment | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50379 | 2/24/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50380 | 8/31/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50381 | 12/14/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50382 | 1/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Confined to the object of origin (localized/single subcomponent) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50383 | 3/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50384 | 3/22/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50385 | 5/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50387 | 3/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50388 | 6/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50389 | 6/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50390 | 10/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50391 | 7/2/2009 | Not Challenging | Unknown | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
50392 | 8/13/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50393 | 10/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50394 | 4/21/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50395 | 4/16/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50396 | 5/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50397 | 1/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50398 | 12/2/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50399 | 2/26/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50400 | 8/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50401 | 10/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50402 | 11/8/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50403 | 11/8/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized spray | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50404 | 11/25/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50405 | 3/4/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50406 | 8/21/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50407 | 3/11/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50409 | 10/5/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
50410 | 9/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50411 | 7/9/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Mechanical equipment malfunction/failure | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50423 | 2/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50424 | 3/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50425 | 3/16/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50426 | 5/2/2000 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50427 | 8/19/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50428 | 9/20/2000 | Not Challenging | Unknown | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50429 | 3/19/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50430 | 2/18/2000 | Not Challenging | Mechanical equipment malfunction/failure | 3/19/2001 | Structural component | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50432 | 3/19/2001 | Not Challenging | Electrical failure resulting in overheating materials | 3/19/2002 | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50433 | 8/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50434 | 10/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50435 | 7/22/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50436 | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50438 | 1/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50439 | 3/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50440 | 10/13/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
50441 | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50442 | 11/8/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50443 | 3/20/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50444 | 4/27/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50445 | 4/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50446 | 7/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50447 | 9/14/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50448 | 10/11/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50449 | 2/21/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50450 | 2/28/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50451 | 7/15/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50452 | 8/18/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50453 | 8/22/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50454 | 11/8/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50455 | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50456 | 2/15/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50457 | 7/28/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
50458 | 8/15/2007 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50459 | 2/8/2008 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50460 | 4/16/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50461 | 4/24/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50462 | 6/12/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50463 | 4/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50464 | 4/26/2000 | Not Challenging | Personnel error: Misuse of heating devices | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50466 | 2/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | Liquid | Lube Oil or grease | Contained within reservoir | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50467 | 2/4/2006 | Undetermined (NC‐PC) | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50468 | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50469 | 7/28/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50470 | 11/19/2008 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50471 | 12/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50472 | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50473 | 6/26/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50474 | 8/29/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50475 | 10/11/2000 | Undetermined (PC‐CH) |  | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Unknown
50476 | 12/19/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50477 | 3/18/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Other (specify) | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50478 | 3/19/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50479 | 3/22/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50480 | 4/7/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50481 | 11/4/2006 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | Unknown | No damage | No
50482 | 3/8/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin | No
50483 | 3/11/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50484 | 3/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Other (specify | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50486 | 4/20/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
50487 | 3/6/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50488 | 5/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50489 | 8/30/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50490 | 9/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50491 | 10/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50492 | 11/2/2009 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50494 | 2/5/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Flaming combustion – external to component | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
50495 | 11/11/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50496 | 1/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Thermal insulation materials | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50497 | 8/15/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50499 | 4/1/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50501 | : 11/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50502 | 10/16/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50503 | : 6/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : No damage | No
50504 | : 5/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component | N/A | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | Unknown | : Confined to the object of origin (localized/single subcomponent) | No
50506 | 12/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | : Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50507 | 11/15/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50508 | 11/26/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : Confined to the object of origin (localized/single subcomponent) | No
50510 | 4/19/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50511 | : 5/15/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) |  | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50512 | 5/31/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50513 | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Other electrical or electronic equipment | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50514 | 4/29/2009 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50515 | 11/30/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | Flaming combustion – external to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50516 | 10/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50517 | 10/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50518 | 11/18/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Smoldering combustion – external to component | Smoldering combustion – external to component | Confined to the object of origin (localized/single subcomponent) | No
50519 | 10/19/2009 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50520 | 12/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50521 | 2/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50522 | 9/8/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | : Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50523 | 9/19/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50524 | 1/23/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50525 | 12/18/2009 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50526 | 12/7/2006 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | In‐Situ | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50527 | 6/23/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50528 | 6/19/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50529 | 3/31/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50530 | 10/21/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50534 | 1/7/2002 | Not Evaluated | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50535 | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50536 | 3/21/2002 | Not Evaluated | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
50537 | 3/23/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Interior finish | N/A | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50538 | 3/27/2002 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50539 | 5/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50540 | 5/25/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50541 | 4/6/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50542 | 7/30/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50543 | 3/27/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
50545 | 9/18/2003 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50546 | 12/1/2004 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50547 | 4/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50548 | 6/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50549 | 1/21/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50550 | 6/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50551 | 10/6/2008 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50552 | 3/23/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50553 | 5/2/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50554 | 5/19/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50555 | : 6/25/2003 | Not Challenging | Unknown | Unknown |  |  | Unknown | Unknown | Unknown | Unknown | No
50556 | 2/25/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Flaming combustion – external to component | No smoke present | Unknown | Confined to the object of origin (broad/extensive damage) | No
50557 | 1/16/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50558 | 1/2/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50562 | 5/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
50563 | 11/16/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50564 | 1/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50565 | 8/26/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50566 | 9/17/2008 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50569 | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50570 | 6/21/2004 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50571 | 7/22/2004 | Not Challengin | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50572 | 10/8/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50573 | 8/24/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Other (specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50574 | 9/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50575 | 9/14/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50576 | 9/17/2004 | Not Challenging | Personnel error during test and maintenance activity | Transient (Liquid) | Other (specify) | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50577 | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50578 | 11/23/2004 | Not Challenging |  | Liquid | Lube Oil or grease | Other (specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | onfined to the object of origin (localized/single subcomponent) | No
50579 | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50580 | 10/9/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
50581 | 6/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No
50582 | 8/22/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within component | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No
50583 | 9/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50584 | 6/27/2005 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment | N/A | verheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50585 | 10/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50586 | 9/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage) | No
50587 | 2/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50588 | 2/4/2006 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion |  | Overheating – no smoldering or flaming combustion | Confined to the object of origin (localized/single subcomponent | No
50589 | 4/15/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No
50590 | 5/6/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50591 | 5/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50592 | 7/11/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50593 | 10/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50594 | 10/5/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50595 | 10/28/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50596 | 1/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50597 | 12/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50598 | 3/10/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion |  |  |  | No
50599 | 3/31/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Single Cable | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50600 | 12/2/2008 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50601 | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50603 | 2/24/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50604 | 11/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50605 | 10/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
50606 | 10/8/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50607 | 3/1/1997 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50608 | 5/28/1997 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | Electrical arcing or sparks (non‐HEAF) | Transient | N/A | Temporary electrical wiring or equipment | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No
50609 | 11/23/2000 | Not Evaluated | Mechanical equipment malfunction/failure | In‐Situ | Structural component | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50610 | 5/30/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50611 | 3/19/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Transient | Other (specify | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50612 | 10/21/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50613 | 7/3/2003 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50614 | 3/9/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | NA | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50615 | 3/11/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50616 | 3/21/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No
50617 | 3/29/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50618 | 9/14/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50619 | 2/8/2006 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
506203 | 3/27/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50621 | 9/11/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50622 | 11/8/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50623 | 12/15/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50624 | 5/14/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50625 | 1/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | Other (Specify) | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50627 | 3/24/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
50628 | 3/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50629 | 10/16/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50630 | 10/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50631 | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50632 | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50633 | 11/12/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients Form N | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50634 | 3/6/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50635 | 12/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50636 | 2/10/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50637 | 4/18/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50638 | 5/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50639 | 11/10/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50640 | 12/23/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50641 | 3/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Pressurized in a container | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50642 | 4/16/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50643 | 4/18/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50644 | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50645 | 12/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50646 | 3/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50647 | 8/12/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipmentOther electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50648 | 12/2/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
50649 | 4/22/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Single Cable | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50650 | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50650 | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50651 | 10/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Cleaning solvents or paint | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50652 | 3/18/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50653 | 10/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50654 | 9/24/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50655 | 12/4/2007 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In‐Situ | Other (specify | N/A | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50656 | 8/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50657 | 3/2/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50658 | 4/24/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50659 | 8/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50660 | 9/24/2000 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50661 | 4/25/2001 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Other (specify | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50662 | 6/5/2001 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50663 | 8/12/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50664 | 6/29/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50665 | 9/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | In‐Situ | N/A | Other (specify | Overheating – no smoldering or flaming combustion | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50666 | 3/22/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50667 | 3/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50668 | 4/16/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50669 | 1/3/2002 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50670 | 10/12/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50671 | 10/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50672 | 4/5/2002 | Not Evaluated | In‐Situ | Other electrical or electronic equipment | Fire not observed and fire type indeterminate from post‐inspecti | N/A | Unknown | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50673 | 4/5/2002 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
50674 | 9/23/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50675 | 8/12/2002 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50676 | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50677 | 9/24/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50678 | 3/28/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50679 | 10/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50680 | 8/24/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50681 | 11/22/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50682 | 4/10/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50683 | 5/18/2004 | Not Evaluated | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50684 | 3/8/2007 | Not Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other (specify | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50685 | 3/30/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
50686 | 4/4/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50687 | 7/23/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50688 | 5/28/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50689 | 10/17/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | NA | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50690 | 10/24/2005 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | Contained within reservoir | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
50691 | 2/15/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50692 | 3/24/2008 | Not Evaluated | Personnel error: Misuse of heating devices | Liquid | Other (specify | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50693 | 10/13/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50694 | 10/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Lube Oil or grease | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50696 | 4/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50697 | 7/16/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50698 | 3/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50699 | 4/7/2000 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No
50700 | 5/13/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50701 | 5/24/2000 | Not Challenging | High Energy Arc Fault (HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50702 | 6/25/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  | N/A | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
50703 | 8/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
50704 | 12/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50705 | 4/15/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50706 | 4/17/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
50707 | 4/25/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50708 | 5/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50709 | 10/26/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50710 | 11/19/2001 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  | Leak ‐ Oil soaked Insulation | Unknown | Unknown | Unknown | No Fire ‐ False actuation of detection device | No
50711 | 11/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50712 | 12/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50713 | 1/1/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50714 | 1/9/2002 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50715 | 1/16/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50716 | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50717 | 5/21/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
50718 | 3/20/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50719 | 8/1/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50720 | 8/4/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
50721 | 8/13/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify | N/A | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent | No
50722 | 10/10/2003 | Not Challenging | Unknown | Overheating – no smoldering or flaming combustion |  | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No
50723 | 1/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Other (specify) | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
50724 | 3/5/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50725 | 3/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc | Liquid | Lube Oil or grease | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50726 | 10/14/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50728 | 1/20/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
50729 | 4/4/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF |  |  | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50730 | 3/1/2006 | Not Challenging | Unknown |  |  | Other (Specify) | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Unknown | No
50731 | 2/11/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | Transient | Other (specify | N/A | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50732 | 11/7/2002 | Undetermined (NC‐PC | Mechanical equipment malfunction/failure | Insulation | Type not specified | N/A | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50733 | 4/23/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50735 | 4/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50736 | 4/10/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No
50738 | 3/13/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other (specify) | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50739 | 3/28/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50740 | 5/16/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50741 | 9/18/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
50742 | 10/4/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Insulation | Type not specified | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50743 | 7/17/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other (specify | N/A | Other (specify | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50744 | 8/3/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | N/A | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50745 | 9/22/2009 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50747 | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50748 | 9/22/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50749 | 10/28/2008 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
50750 | 1/10/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50751 | 11/17/2008 | Not Challenging | Unknown | Overheating – no smoldering or flaming combustion |  | N/A | Overheating – no or flaming combustion | Unknown | Unknown | Unknown | No
50753 | 12/11/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50754 | 1/23/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
50756 | 9/21/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50757 | 9/7/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50758 | 6/14/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
50759 | 7/29/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50760 | 11/8/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50761 | 1/25/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50762 | 10/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50763 | 11/14/2008 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50764 | 1/14/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50765 | 10/12/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
50766 | 8/18/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | Spill confined by curbs or other physical feat | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50767 | 6/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50768 | 1/1/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50769 | 12/6/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50770 | 1/30/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50771 | 5/6/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50772 | 7/2/2003 | Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | Severe – room entry not possible without venting or mitigation | Confined to room of origin
50773 | 9/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50774 | 1/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50775 | 2/13/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50777 | 8/5/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50778 | 10/11/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50779 | 10/25/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
50780 | 1/6/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50781 | 3/10/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
50782 | 3/11/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50783 | 6/27/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50784 | 11/20/2005 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50785 | 12/3/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50786 | 3/10/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50787 | 1/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid |  | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50788 | 3/8/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50789 | 3/4/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50790 | 6/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50791 | 10/25/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50792 | 11/6/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50793 | 11/18/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50794 | 3/4/2009 | Not Challenging | Mechanical equipment malfunction/failure | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50795 | 7/12/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50796 | 11/4/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50797 | 11/8/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50798 | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50799 | 12/12/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50803 | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50804 | 1/13/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
50805 | 2/12/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50806 | 8/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify | N/A | Unknown | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50807 | 8/24/2007 | Not Challenging | Personnel error during test and maintenance activity | Transient (Gas | Other (specify | N/A | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50808 | 3/21/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Other (specify | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50809 | 11/9/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50810 | 6/25/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50811 | 1/9/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50812 | 6/11/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50813 | 9/3/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50814 | 5/31/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50815 | 5/19/2005 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50816 | 11/16/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50817 | 2/13/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | Gas | Hydrogen | Pressurized in a container | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
50818 | 3/21/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50819 | 6/13/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | No damageNone or insignificant – temperature at or close to ambient | No damage | No
50820 | 10/23/2008 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
50821 | 10/30/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50822 | 11/7/2008 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
50823 | 4/9/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50824 | 9/13/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50825 | 10/1/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
50826 | 12/9/2009 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other electrical or electronic equipment | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
50827 | 4/27/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50828 | 10/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50829 | 9/11/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No
50833 | 9/23/2008 | Potentially Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50834 | 9/24/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50835 | 10/1/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc. | In‐Situ | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50837 | 7/9/2001 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Unknown | Unknown | Unknown | No
50838 | 11/19/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50839 | 11/26/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50840 | 11/28/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50841 | 11/29/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50842 | 8/23/2002 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50843 | 3/22/2003 | Not Evaluated | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50844 | 7/24/2003 | Not Evaluated | Personnel error during test and maintenance activity | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50845 | 12/13/2003 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
50846 | 1/24/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50847 | 1/27/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50848 | 1/30/2005 | Not Evaluated | Unknown | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50849 | 3/8/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50850 | 4/1/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50851 | 4/27/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify | N/A | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
50852 | 5/25/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
50853 | 11/28/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50854 | 9/18/2006 | Not Evaluated | Personnel error: Misuse of heating devices | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50855 | 4/26/2008 | Not Evaluated | Hot work (cutting/welding/grinding/etc. | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50856 | 1/31/2008 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50857 | 11/6/2009 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50860 | 12/14/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Unknown | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
50861 | 12/20/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50862 | 2/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment | N/A | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage | No
50863 | 9/30/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50864 | 9/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50865 | 1/31/2000 | Not Challenging | Personnel error: Misuse of material ignited | Transient (Gas | NA | N/A | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
50866 | 3/28/2001 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50867 | 10/31/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50868 | 7/3/2001 | Not Challenging | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | No damage | No
50869 | 10/25/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
50870 | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50872 | 3/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50873 | 5/9/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50874 | 7/12/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50875 | 11/10/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50876 | 11/13/2002 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50878 | 11/12/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50879 | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50880 | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50881 | 12/31/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Unknown | Unknown | Unknown | No
50882 | 1/20/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50883 | 4/18/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50884 | 2/23/2004 | Undetermined (NC‐PC | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50885 | 6/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) | N/A | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50886 | 2/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50887 | 3/7/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50888 | 7/16/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50889 | 3/22/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | N/A | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50890 | 4/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas | NA | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50891 | 4/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin (localized/single subcomponent | No
50892 | 4/12/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc. | Transient | Other (specify | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50893 | 12/2/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50894 | 3/12/2006 | Not Challenging | Unknown | Gas | Hydrogen | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50895 | 5/13/2007 | Potentially Challenging | Unknown |  |  | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
50896 | 5/13/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc | Transient | Other (specify | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50897 | 12/22/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | N/A | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
50899 | 10/27/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Other (specify | Other (specify | Explosion | Unknown | Unknown | Unknown | No
50900 | 5/1/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal | N/A | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50901 | 8/28/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials | N/A | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No

## Fire Severity Evaluation
FireID | Event Date_FSE | Disposition_FSE | Review Status: | Automatic Determination
1 | 12/12/2006 | Undetermined | Preliminary | Challenging
2 | 1/5/1999 | Not Challenging | Preliminary | Challenging
3 | 1/14/1999 | Challenging | Preliminary | Challenging
4
5 | 5/18/1999 | Not Evaluated | Preliminary | Potentially Challenging
6 | 7/13/1999 | Potentially Challenging | Final | Challenging
7 | 10/9/1999 | Undetermined (NC‐PC) | Final | Potentially Challenging
8 | 5/7/2000 | Potentially Challenging | Final | Potentially Challenging
9 | 1/3/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging
10
11 | 3/15/1990 | Not Challenging | Final | Potentially Challenging
12 | 3/30/1990 | Not Challenging | Final | Not Challenging
13 | 4/10/1990 | Potentially Challenging | Preliminary | Potentially Challenging
14 | 5/24/1990 | Potentially Challenging | Final | Potentially Challenging
15 | 5/27/1990 | Not Challenging | Final | Potentially Challenging
16 | 6/10/1990 | Not Challenging | Final | Potentially Challenging
17 | 6/28/1990 | Potentially Challenging | Final | Potentially Challenging
18 | 7/13/1990 | Potentially Challenging | Final | Potentially Challenging
19 | 8/4/1990 | Challenging | Preliminary | Challenging
20 | 8/25/1990 | Challenging | Preliminary | Potentially Challenging
21 | 9/22/1990 | Challenging | Preliminary | Challenging
22 | 12/3/1990 | Challenging | Preliminary | Challenging
23 | 12/19/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging
24 | 12/22/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging
25 | 1/11/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
26 | 2/14/1991 | Challenging | Preliminary | Challenging
27 | 1/16/1991 | Not Challenging | Final | Not Challenging
28 | 1/23/1991 | Not Challenging | Final | Undetermined (NC‐PC)
29 | 2/23/1991 | Potentially Challenging | Final | Potentially Challenging
30 | 4/29/1991 | Challenging | Preliminary | Challenging
31 | 6/15/1991 | Undetermined (PC‐CH) | Preliminary | Undetermined (PC‐CH)
32 | 6/27/1991 | Potentially Challenging | Preliminary | Potentially Challenging
33 | 8/1/1991 | Potentially Challenging | Final | Potentially Challenging
34 | 8/11/1991 | Potentially Challenging | Final | Challenging
35 | 11/2/1991 | Not Challenging | Final | Challenging
36 | 11/9/1991 | Not Challenging | Preliminary | Challenging
37 | 11/15/1991 | Not Challenging | Final | Potentially Challenging
38 | 3/21/1992 | Challenging | Final | Challenging
39 | 5/3/1992 | Not Challenging | Final | Potentially Challenging
40 | 5/22/1992 | Not Challenging | Final | Not Challenging
41 | 6/17/1992 | Potentially Challenging | Final | Potentially Challenging
42 | 7/3/1992 | Potentially Challenging | Final | Potentially Challenging
43 | 7/4/1992 | Challenging | Final | Challenging
44 | 7/13/1992 | Challenging | Final | Challenging
45 | 7/29/1992 | Potentially Challenging | Final | Potentially Challenging
46 | 8/4/1992 | Potentially Challenging | Final | Potentially Challenging
47 | 8/10/1992 | Not Challenging | Final | Not Challenging
48 | 9/4/1992 | Challenging | Final | Challenging
49 | 9/15/1992 | Challenging | Preliminary | Challenging
50 | 11/24/1992 | Potentially Challenging | Final | Potentially Challenging
51 | 2/5/1993 | Not Challenging | Final | Not Challenging
52 | 6/19/1993 | Potentially Challenging | Final | Potentially Challenging
53 | 7/27/1993 | Not Challenging | Final | Not Challenging
54 | 8/16/1993 | Not Challenging | Final | Potentially Challenging
55 | 10/13/1993 | Potentially Challenging | Final | Challenging
56 | 10/21/1993 | Potentially Challenging | Final | Potentially Challenging
57 | 11/2/1993 | Not Challenging | Final | Not Challenging
58 | 12/25/1993 | Challenging | Preliminary | Challenging
59 | 1/29/1994 | Challenging | Preliminary | Challenging
60 | 2/3/1994 | Not Challenging | Final | Not Challenging
61 | 4/3/1994 | Challenging | Preliminary | Challenging
62 | 6/6/1994 | Not Challenging | Final | Potentially Challenging
63 | 6/15/1994 | Potentially Challenging | Final | Potentially Challenging
64 | 6/1/1994 | Challenging | Preliminary | Challenging
65 | 7/2/1994 | Challenging | Preliminary | Challenging
66 | 7/11/1994 | Potentially Challenging | Preliminary | Potentially Challenging
67 | 7/29/1994 | Potentially Challenging | Preliminary | Potentially Challenging
68 | 8/10/1994 | Undetermined (PC‐CH) | Final | Challenging
69 | 8/29/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
70 | 10/26/1994 | Not Challenging | Final | Potentially Challenging
71 | 3/1/1995 | Undetermined (PC‐CH) | Final | Potentially Challenging
72 | 4/14/1995 | Challenging | Preliminary | Challenging
73 | 6/1/1995 | Not Challenging | Final | Not Challenging
74 | 6/10/1995 | Challenging | Preliminary | Challenging
75 | 8/22/1995 | Potentially Challenging | Final | Potentially Challenging
76 | 10/21/1995 | Challenging | Preliminary | Challenging
77 | 12/10/1995 | Not Challenging | Final | Undetermined (NC‐PC)
78 | 1/24/1996 | Challenging | Preliminary | Challenging
79 | 2/5/1996 | Challenging | Preliminary | Potentially Challenging
80 | 2/29/1996 | Potentially Challenging | Preliminary | Potentially Challenging
81 | 3/25/1996 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
82 | 3/27/1996 | Potentially Challenging | Final | Potentially Challenging
83 | 4/4/1996 | Potentially Challenging | Final | Potentially Challenging
84 | 4/19/1996 | Potentially Challenging | Preliminary | Potentially Challenging
85 | 5/13/1996 | Not Challenging | Final | Challenging
86 | 6/23/1996 | Challenging | Preliminary | Challenging
87 | 8/19/1996 | Potentially Challenging | Final | Potentially Challenging
88 | 10/5/1996 | Challenging | Preliminary | Challenging
89 | 10/15/1996 | Potentially Challenging | Final | Potentially Challenging
90 | 10/17/1996 | Challenging | Preliminary | Challenging
91 | 11/19/1996 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
92 | 11/22/1996 | Potentially Challenging | Preliminary | Potentially Challenging
93 | 3/4/1997 | Potentially Challenging | Final | Potentially Challenging
94 | 8/1/1997 | Potentially Challenging | Final | Challenging
95 | 10/9/1997 | Potentially Challenging | Final | Potentially Challenging
96 | 10/28/1997 | Not Challenging | Final | Potentially Challenging
97 | 6/10/1998 | Potentially Challenging | Final | Potentially Challenging
98 | 10/8/1998 | Potentially Challenging | Preliminary | Potentially Challenging
99 | 10/10/1998 | Not Challenging | Preliminary | Potentially Challenging
100 | 5/15/2000 | Challenging | Preliminary | Challenging
101 | 9/3/2000 | Undetermined (PC‐CH) | Final | Challenging
102 | 9/4/2000 | Challenging | Preliminary | Challenging
103 | 9/22/2000 | Challenging | Preliminary | Challenging
104 | 10/14/2000 | Potentially Challenging | Preliminary | Potentially Challenging
105 | 11/10/2000 | Potentially Challenging | Preliminary | Potentially Challenging
106 | 2/3/2001 | Challenging | Preliminary | Challenging
107 | 3/21/2001 | Potentially Challenging | Preliminary | Potentially Challenging
108 | 4/6/2001 | Not Challenging | Final | Challenging
109 | 4/24/2001 | Undetermined (PC‐CH) | Final | Challenging
110 | 6/25/2001 | Potentially Challenging | Preliminary | Potentially Challenging
111 | 8/2/2001 | Challenging | Final | Challenging
112 | 8/3/2001 | Undetermined (PC‐CH) | Final | Potentially Challenging
113 | 6/12/2002 | Challenging | Final | Challenging
114 | 8/21/2002 | Challenging | Final | Challenging
115 | 8/22/2002 | Challenging | Final | Challenging
116 | 10/3/2002 | Challenging | Final | Challenging
117 | 10/9/2002 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
118 | 1/15/2003 | Challenging | Final | Challenging
119 | 3/18/2003 | Not Challenging | Final | Potentially Challenging
120 | 4/7/2003 | Potentially Challenging | Final | Potentially Challenging
121 | 4/26/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging
122 | 4/29/2003 | Challenging | Final | Challenging
123 | 10/16/2003 | Challenging | Preliminary | Challenging
124 | 10/28/2003 | Potentially Challenging | Preliminary | Potentially Challenging
125 | 1/6/2004 | Challenging | Final | Challenging
126 | 5/21/2004 | Undetermined (PC‐CH) | Final | Potentially Challenging
127 | 6/18/2004 | Challenging | Preliminary | Challenging
128 | 8/31/2004 | Potentially Challenging | Final | Potentially Challenging
129 | 11/6/2004 | Potentially Challenging | Final | Potentially Challenging
130 | 12/14/2004 | Potentially Challenging | Final | Potentially Challenging
131 | 1/14/2005 | Undetermined (PC‐CH) | Final | Challenging
132 | 3/4/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
133 | 5/4/2005 | Potentially Challenging | Final | Potentially Challenging
134 | 6/27/2005 | Challenging | Final | Challenging
135 | 8/25/2005 | Potentially Challenging | Final | Challenging
136 | 10/25/2005 | Potentially Challenging | Final | Potentially Challenging
137 | 10/29/2005 | Challenging | Final | Challenging
138 | 2/11/2006 | Potentially Challenging | Preliminary | Potentially Challenging
139 | 2/24/2006 | Potentially Challenging | Final | Potentially Challenging
140 | 3/20/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
141 | 5/1/2006 | Undetermined (PC‐CH) | Final | Challenging
142 | 5/24/2006 | Challenging | Preliminary | Challenging
143 | 8/15/2006 | Potentially Challenging | Final | Challenging
144 | 10/30/2006 | Potentially Challenging | Final | Potentially Challenging
145 | 11/11/2006 | Not Challenging | Preliminary | Potentially Challenging
146 | 2/27/2007 | Undetermined (PC‐CH) | Final | Potentially Challenging
147 | 4/5/2007 | Not Challenging | Final | Not Challenging
148 | 4/6/2007 | Challenging | Final | Challenging
149 | 4/8/2007 | Potentially Challenging | Preliminary | Potentially Challenging
150 | 4/25/2007 | Challenging | Final | Challenging
151 | 8/1/2007 | Not Challenging | Final | Challenging
152 | 10/23/2007 | Potentially Challenging | Final | Potentially Challenging
153 | 8/16/2008 | Challenging | Preliminary | Challenging
154 | 9/20/2008 | Challenging | Final | Challenging
155 | 11/17/2008 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
156
157 | 2/1/2009 | Challenging | Final | Challenging
158 | 6/26/2009 | Potentially Challenging | Preliminary | Potentially Challenging
159 | 1/16/1990 | Potentially Challenging | Final | Potentially Challenging
160 | 2/7/2009 | Challenging | Final | Challenging
161 | 4/22/2009 | Potentially Challenging | Final | Potentially Challenging
162 | 8/5/2009 | Challenging | Preliminary | Challenging
163 | 10/12/2009 | Potentially Challenging | Preliminary | Potentially Challenging
164 | 3/28/1990 | Not Challenging | Final | Challenging
165
166
167
168 | 11/13/2003 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
169 | 11/13/2003 | Potentially Challenging | Final | Potentially Challenging
170 | 11/21/2003 | Not Challenging | Final | Challenging
171
172 | 12/7/2003 | Challenging | Final | Challenging
173 | 12/13/2003 | Not Challenging | Final | Not Challenging
174 | 12/30/2003 | Not Challenging | Final | Not Challenging
175 | 11/22/2009 | Challenging | Final | Challenging
176 | 12/12/2009 | Potentially Challenging | Final | Potentially Challenging
177
178
179
180
181 | 2/13/1997 | Potentially Challenging | Final | Potentially Challenging
182
183
184 | 6/27/1997 | Challenging | Final | Challenging
185 | 3/23/1998 | Not Challenging | Final | Potentially Challenging
186 | 5/14/1998 | Not Challenging | Final | Not Challenging
187 | 8/16/1999 | Potentially Challenging | Final | Potentially Challenging
188 | 8/24/1999 | Potentially Challenging | Final | Potentially Challenging
189 | 10/14/1996 | Not Challenging | Final | Challenging
190 | 3/18/1998 | Not Challenging | Final | Not Challenging
191 | 11/11/1998 | Not Challenging | Final | Not Challenging
192 | 5/15/1999 | Not Challenging | Final | Potentially Challenging
193 | 7/31/1991 | Not Challenging | Final | Not Challenging
194 | 5/22/1990 | Potentially Challenging | Final | Challenging
195 | 3/21/1992 | Not Challenging | Final | Not Challenging
196
197
198
199 | 1/22/1990 | Potentially Challenging | Preliminary | Potentially Challenging
200 | 2/6/1990 | Not Challenging | Final | Potentially Challenging
201 | 3/8/1990 | Potentially Challenging | Final | Potentially Challenging
202 | 3/23/1990 | Potentially Challenging | Final | Potentially Challenging
203 | 4/6/1990 | Challenging | Preliminary | Challenging
204 | 4/9/1990 | Not Challenging | Final | Not Challenging
205
206 | 6/11/1990 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
207 | 7/15/1990 | Undetermined (PC‐CH) | Preliminary | Challenging
208 | 8/8/1990 | Potentially Challenging | Final | Potentially Challenging
209 | 8/22/1990 | Not Challenging | Final | Potentially Challenging
210 | 10/16/1990 | Undetermined (NC‐PC) | Final | Potentially Challenging
211 | 11/2/1990 | Potentially Challenging | Final | Undetermined (NC‐PC)
212 | 12/5/1990 | Not Challenging | Final | Not Challenging
213
214 | 3/8/1991 | Potentially Challenging | Final | Potentially Challenging
215 | 3/11/1991 | Not Challenging | Final | Challenging
216 | 7/12/1991 | Potentially Challenging | Preliminary | Potentially Challenging
217 | 7/19/1991 | Potentially Challenging | Preliminary | Potentially Challenging
218 | 9/12/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
219 | 9/27/1991 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
220 | 10/20/1991 | Potentially Challenging | Final | Potentially Challenging
221 | 10/23/1991 | Not Challenging | Final | Not Challenging
222 | 2/1/1992 | Not Challenging | Final | Not Challenging
223 | 3/3/1992 | Not Challenging | Final | Not Challenging
224 | 3/8/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
225 | 3/23/1992 | Not Challenging | Final | Not Challenging
226 | 4/17/1992 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
227 | 6/9/1992 | Not Challenging | Final | Not Challenging
228 | 8/14/1992 | Potentially Challenging | Final | Challenging
229 | 8/21/1992 | Challenging | Preliminary | Challenging
230 | 8/31/1992 | Potentially Challenging | Final | Potentially Challenging
231 | 10/22/1992 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
232 | 10/27/1992 | Not Challenging | Final | Potentially Challenging
233 | 11/29/1992 | Potentially Challenging | Final | Undetermined (NC‐PC)
234 | 12/16/1992 | Not Challenging | Final | Not Challenging
235 | 12/30/1992 | Potentially Challenging | Final | Potentially Challenging
236 | 1/6/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
237 | 3/19/1993 | Potentially Challenging | Final | Potentially Challenging
238 | 4/1/1993 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
239 | 7/14/1993 | Potentially Challenging | Final | Potentially Challenging
240 | 7/19/1993 | Undetermined (PC‐CH) | Final | Challenging
241 | 11/3/1993 | Potentially Challenging | Final | Challenging
242 | 11/13/1993 | Undetermined (NC‐PC) | Final | Challenging
243 | 12/1/1993 | Potentially Challenging | Final | Challenging
244 | 12/7/1993 | Undetermined (PC‐CH) | Final | Challenging
245 | 12/16/1993 | Not Challenging | Final | Not Challenging
246 | 1/12/1994 | Challenging | Preliminary | Challenging
247 | 1/12/1994 | Undetermined (PC‐CH) | Final | Challenging
248 | 3/5/1994 | Undetermined (PC‐CH) | Final | Challenging
249 | 3/7/1994 | Undetermined (PC‐CH) | Final | Challenging
250 | 7/19/1994 | Potentially Challenging | Final | Challenging
251 | 10/11/1994 | Potentially Challenging | Preliminary | Potentially Challenging
252 | 3/18/1995 | Undetermined (NC‐PC) | Final | Challenging
253 | 7/6/1995 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
254 | 9/25/1995 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC)
255 | 11/19/1995 | Challenging | Preliminary | Challenging
256 | 7/22/1996 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
257 | 10/22/1997 | Not Challenging | Final | Not Challenging
258 | 11/3/1997 | Undetermined (PC‐CH) | Final | Challenging
259 | 12/26/1997 | Potentially Challenging | Final | Undetermined (NC‐PC)
260 | 2/3/1998 | Potentially Challenging | Preliminary | Potentially Challenging
261 | 5/11/1998 | Not Challenging | Final | Potentially Challenging
262 | 2/19/1999 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC)
263 | 4/25/1999 | Not Challenging | Final | Not Challenging
264 | 10/20/2001 | Not Challenging | Final | Undetermined (NC‐PC)
265 | 9/23/2006 | Not Challenging | Final | Not Challenging
266 | 11/9/2006 | Potentially Challenging | Final | Potentially Challenging
267 | 6/1/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
268 | 4/7/2000 | Not Challenging | Final | Not Challenging
269 | 12/12/2000 | Potentially Challenging | Final | Potentially Challenging
270 | 11/18/2005 | Potentially Challenging | Final | Potentially Challenging
271 | 10/5/2007 | Not Challenging | Final | Not Challenging
272 | 4/17/2004 | Not Challenging | Final | Challenging
273 | 5/10/2002 | Not Challenging | Final | Potentially Challenging
274 | 5/7/2003 | Not Challenging | Final | Challenging
275 | 10/14/2003 | Potentially Challenging | Final | Undetermined (NC‐PC)
276 | 11/2/2003 | Not Challenging | Final | Undetermined (NC‐PC)
277 | 11/2/2003 | Not Challenging | Final | Undetermined (NC‐PC)
278 | 1/5/2004 | Not Challenging | Final | Potentially Challenging
279
280 | 11/19/2005 | Not Challenging | Final | Not Challenging
281
282 | 4/23/2001 | Not Challenging | Final | Challenging
283 | 11/20/2005 | Not Challenging | Final | Not Challenging
284 | 11/29/2005 | Not Challenging | Final | Undetermined (NC‐PC)
285 | 12/9/2005 | Not Challenging | Final | Not Challenging
286 | 4/20/2006 | Not Challenging | Final | Not Challenging
287 | 8/10/2006 | Not Challenging | Final | Potentially Challenging
288 | 10/10/2006 | Potentially Challenging | Final | Potentially Challenging
289 | 5/28/2007 | Not Challenging | Final | Potentially Challenging
290 | 8/22/2007 | Not Challenging | Final | Potentially Challenging
291
292 | 10/8/2007 | Not Challenging | Final | Not Challenging
293 | 10/14/2007 | Not Challenging | Final | Not Challenging
294 | 10/13/2007 | Not Challenging | Final | Not Challenging
295 | 10/22/2007 | Not Challenging | Final | Potentially Challenging
296 | 10/30/2007 | Not Challenging | Final | Not Challenging
297 | 11/30/2007 | Not Challenging | Final | Not Challenging
298 | 12/16/2007 | Not Challenging | Final | Not Challenging
299 | 3/4/2008 | Not Challenging | Final | Potentially Challenging
300 | 3/16/2009 | Not Challenging | Final | Not Challenging
301
302 | 12/21/1999 | Not Challenging | Final | Potentially Challenging
303 | 3/1/2000 | Potentially Challenging | Final | Potentially Challenging
304
305 | 6/21/2001 | Not Challenging | Final | Potentially Challenging
306 | 1/24/2002 | Not Challenging | Final | Potentially Challenging
307 | 10/17/2002 | Not Challenging | Final | Not Challenging
308 | 10/14/2005 | Potentially Challenging | Final with disagreement | Potentially Challenging
309 | 10/23/2005 | Not Challenging | Final | Not Challenging
310 | 11/18/2005 | Not Challenging | Final | Not Challenging
311 | 12/1/2005 | Not Challenging | Final | Undetermined (NC‐PC)
312 | 10/29/2008 | Not Challenging | Final | Undetermined (NC‐PC)
313 | 11/9/2008 | Not Challenging | Final | Potentially Challenging
314 | 2/10/2000 | Not Challenging | Final | Potentially Challenging
315
316 | 8/17/2000 | Not Challenging | Final | Potentially Challenging
317 | 9/27/2003 | Not Challenging | Final | Not Challenging
318 | 10/5/2000 | Not Challenging | Final | Undetermined (NC‐PC)
319 | 10/5/2000 | Not Challenging | Final | Not Challenging
320 | 10/24/2000 | Potentially Challenging | Final | Potentially Challenging
321 | 10/31/2000 | Not Challenging | Final | Challenging
322 | 3/8/2001 | Not Challenging | Final | Not Challenging
323
324 | 1/12/2005 | Not Challenging | Final | Not Challenging
325 | 3/20/2005 | Not Challenging | Final | Not Challenging
326 | 3/25/2005 | Not Challenging | Final | Undetermined (NC‐PC)
327 | 1/1/2006 | Not Challenging | Final | Not Challenging
328 | 9/24/2006 | Not Challenging | Final | Not Challenging
329 | 9/25/2006 | Not Challenging | Final | Potentially Challenging
330 | 9/27/2006 | Not Challenging | Final | Not Challenging
331
332 | 4/15/2007 | Not Challenging | Final | Potentially Challenging
333 | 5/11/2007 | Potentially Challenging | Final | Potentially Challenging
334
335 | 8/3/2007 | Potentially Challenging | Final | Challenging
336
337 | 8/18/2005 | Not Challenging | Final | Not Challenging
338 | 7/25/2007 | Not Challenging | Final | Not Challenging
339
340 | 8/7/2009 | Not Challenging | Final | Potentially Challenging
341 | 2/18/2008 | Not Challenging | Final | Potentially Challenging
342 | 11/4/2006 | Not Challenging | Final | Not Challenging
343 | 11/4/2006 | Not Challenging | Final | Not Challenging
344 | 10/26/2006 | Not Challenging | Final | Not Challenging
345 | 4/25/2005 | Not Challenging | Final | Potentially Challenging
346 | 3/1/2002 | Potentially Challenging | Final | Potentially Challenging
347
348
349 | 4/5/2007 | Not Challenging | Final | Not Challenging
350 | 7/11/2002 | Potentially Challenging | Final | Potentially Challenging
351 | 9/26/2002 | Not Challenging | Final | Not Challenging
352 | 2/28/2003 | Not Challenging | Final | Not Challenging
353 | 1/21/2005 | Not Challenging | Final | Not Challenging
354 | 10/1/2005 | Not Challenging | Final | Not Challenging
355 | 3/7/2006 | Not Challenging | Final | Not Challenging
356 | 4/19/2006 | Potentially Challenging | Final | Potentially Challenging
357 | 1/10/2007 | Not Challenging | Final | Not Challenging
358 | 5/2/2007 | Not Challenging | Final | Not Challenging
359 | 3/6/2001 | Not Challenging | Final | Not Challenging
360 | 7/25/2001 | Not Challenging | Final | Not Challenging
361 | 2/4/2002 | Not Challenging | Final | Not Challenging
362 | 4/16/2002 | Not Challenging | Final | Undetermined (NC‐PC)
363 | 5/27/2003 | Not Challenging | Final | Not Challenging
364 | 10/3/2003 | Not Challenging | Final | Not Challenging
365 | 8/7/2004 | Not Challenging | Final | Potentially Challenging
366 | 1/25/2006 | Not Challenging | Final | Not Challenging
367 | 10/12/2006 | Not Challenging | Final | Not Challenging
368 | 10/24/2006 | Not Challenging | Final | Undetermined (NC‐PC)
369
370
371
372 | 9/8/2009 | Not Challenging | Final | Not Challenging
373 | 10/5/2009 | Not Challenging | Final | Not Challenging
374 | 10/13/2009 | Not Challenging | Final | Undetermined (NC‐PC)
375 | 10/16/2009 | Potentially Challenging | Final | Potentially Challenging
376 | 6/5/2004 | Not Challenging | Final | Not Challenging
377 | 8/27/2004 | Not Challenging | Final | Not Challenging
378 | 6/24/2002 | Not Challenging | Final | Not Challenging
379 | 10/2/2009 | Not Challenging | Final | Not Challenging
380 | 10/29/2004 | Not Challenging | Final | Not Challenging
381 | 3/6/2005 | Potentially Challenging | Final | Potentially Challenging
382
383
384 | 3/23/2007 | Not Challenging | Final | Not Challenging
385 | 4/14/2006 | Not Challenging | Final | Potentially Challenging
386 | 6/3/2008 | Not Challenging | Final | Not Challenging
387 | 7/24/2008 | Not Challenging | Final | Potentially Challenging
388 | 7/25/2005 | Not Challenging | Final | Challenging
389 | 10/17/2004 | Not Challenging | Final | Potentially Challenging
390 | 10/29/2007 | Not Challenging | Preliminary | Potentially Challenging
391
392 | 10/30/2002 | Not Challenging | Final | Challenging
393 | 10/30/2004 | Not Challenging | Final | Potentially Challenging
394 | 2/11/2000 | Not Challenging | Final | Potentially Challenging
395
396
397 | 5/2/2000 | Not Challenging | Final | Not Challenging
398 | 7/7/2000 | Not Challenging | Final | Not Challenging
399 | 12/24/2000 | Not Challenging | Final | Not Challenging
400 | 3/28/2001 | Not Challenging | Preliminary | Potentially Challenging
401 | 6/13/2001 | Not Challenging | Final | Not Challenging
402
403
404 | 6/12/2001 | Not Challenging | Final | Potentially Challenging
405 | 8/13/2001 | Not Challenging | Final | Potentially Challenging
406 | 6/12/2001 | Not Challenging | Final | Potentially Challenging
407 | 12/1/2001 | Not Challenging | Final | Not Challenging
408 | 6/1/2002 | Not Challenging | Final | Potentially Challenging
409 | 9/21/2004 | Not Challenging | Final | Not Challenging
410 | 7/25/2005 | Not Challenging | Final | Not Challenging
411 | 3/8/2001 | Potentially Challenging | Final | Not Challenging
412 | 7/15/2009 | Not Challenging | Final | Not Challenging
413
414
415
416 | 10/11/2000 | Not Challenging | Final | Undetermined (NC‐PC)
417
418 | 10/8/2000 | Not Challenging | Final | Not Challenging
419 | 4/5/2005 | Not Challenging | Final | Not Challenging
420 | 6/24/2001 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
421 | 7/1/2002 | Not Challenging | Final | Undetermined (NC‐PC)
422 | 3/7/2003 | Potentially Challenging | Final | Potentially Challenging
423 | 6/23/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging
424 | 3/10/2005 | Undetermined (NC‐PC) | Final | Challenging
425
426 | 9/17/2007 | Not Challenging | Final | Potentially Challenging
427 | 2/3/2003 | Not Challenging | Final | Potentially Challenging
428 | 9/14/2005 | Not Challenging | Final | Undetermined (NC‐PC)
429 | 3/12/2007 | Not Challenging | Final | Not Challenging
430 | 10/10/2007 | Not Challenging | Final | Not Challenging
431 | 4/3/2000 | Not Challenging | Final | Not Challenging
432
433
434
435
436 | 11/21/2000 | Not Challenging | Preliminary | Potentially Challenging
437 | 2/3/2001 | Challenging | Preliminary | Challenging
438 | 6/24/2001 | Challenging | Preliminary | Challenging
439 | 10/2/2002 | Not Challenging | Preliminary | Challenging
440 | 1/2/2003 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
441 | 11/23/2003 | Not Challenging | Final | Not Challenging
442 | 2/4/2004 | Potentially Challenging | Preliminary | Potentially Challenging
443 | 3/3/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
444 | 6/28/2004 | Challenging | Preliminary | Challenging
445 | 8/30/2004 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
446 | 10/5/2004 | Potentially Challenging | Preliminary | Potentially Challenging
447 | 10/8/2004 | Not Challenging | Final | Not Challenging
448 | 11/17/2004 | Not Challenging | Final | Not Challenging
449 | 12/8/2004 | Not Challenging | Final | Potentially Challenging
450 | 12/13/2004 | Not Challenging | Final | Not Challenging
451 | 12/13/2004 | Not Challenging | Final | Undetermined (NC‐PC)
452 | 12/18/2004 | Not Challenging | Final | Not Challenging
453 | 6/3/2005 | Not Challenging | Final | Not Challenging
454 | 6/4/2005 | Not Challenging | Final | Not Challenging
455 | 6/6/2005 | Not Challenging | Final | Potentially Challenging
456 | 7/7/2005 | Not Challenging | Final | Not Challenging
457 | 2/17/2006 | Not Challenging | Final | Undetermined (NC‐PC)
458 | 5/4/2006 | Not Challenging | Final | Not Challenging
459 | 5/10/2006 | Potentially Challenging | Preliminary | Potentially Challenging
460 | 9/7/2006 | Not Challenging | Final | Not Challenging
461 | 10/12/2006 | Not Challenging | Final | Not Challenging
462 | 10/18/2006 | Not Challenging | Final | Potentially Challenging
463 | 11/1/2006 | Not Challenging | Final | Undetermined (NC‐PC)
464 | 12/8/2006 | Not Challenging | Final | Potentially Challenging
465 | 1/31/2007 | Not Challenging | Final | Potentially Challenging
466 | 2/2/2007 | Not Challenging | Preliminary | Challenging
467 | 2/13/2007 | Not Challenging | Final | Potentially Challenging
468 | 2/20/2007 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
469 | 3/19/2007 | Not Challenging | Final | Not Challenging
470 | 6/29/2007 | Not Challenging | Preliminary | Undetermined (NC‐PC)
471 | 7/10/2007 | Not Challenging | Final | Not Challenging
472 | 7/17/2007 | Not Challenging | Final | Not Challenging
473 | 8/4/2007 | Potentially Challenging | Preliminary | Potentially Challenging
474 | 8/21/2007 | Potentially Challenging | Preliminary | Potentially Challenging
475 | 9/27/2007 | Potentially Challenging | Preliminary | Potentially Challenging
476 | 12/6/2007 | Not Challenging | Final | Potentially Challenging
477 | 2/23/2008 | Not Challenging | Final | Not Challenging
478 | 3/30/2008 | Not Challenging | Final | Not Challenging
479 | 3/17/2000 | Not Challenging | Final | Not Challenging
480 | 4/7/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
481 | 6/29/2000 | Not Challenging | Final | Not Challenging
482 | 2/8/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
483 | 11/9/2000 | Not Challenging | Final | Not Challenging
484 | 11/8/2001 | Not Challenging | Preliminary | Potentially Challenging
485 | 9/14/2001 | Not Challenging | Final | Not Challenging
486 | 8/27/2001 | Not Challenging | Final | Undetermined (NC‐PC)
487 | 1/13/2001 | Not Challenging | Final | Not Challenging
488 | 10/16/2000 | Not Challenging | Preliminary | Potentially Challenging
489
490
491 | 4/12/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
492 | 10/19/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
493
494 | 3/8/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
495 | 3/20/2003 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
496 | 5/19/2002 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
497 | 8/14/2003 | Not Challenging | Final | Not Challenging
498 | 12/19/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
499 | 12/17/2000 | Not Challenging | Final | Undetermined (NC‐PC)
500 | 3/12/2001 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC)
501 | 1/24/2001 | Not Challenging | Final | Potentially Challenging
502 | 11/18/2003 | Not Challenging | Final | Not Challenging
503 | 5/14/2002 | Not Challenging | Final | Potentially Challenging
504 | 10/9/2002 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC)
505 | 9/13/2003 | Not Challenging | Final | Potentially Challenging
506 | 9/12/2003 | Not Challenging | Final | Not Challenging
507
508 | 3/14/2005 | Not Challenging | Final | Potentially Challenging
509 | 1/19/2005 | Potentially Challenging | Preliminary | Potentially Challenging
510
511 | 7/16/2005 | Not Challenging | Final | Not Challenging
512 | 7/20/2005 | Not Challenging | Final | Not Challenging
513 | 11/18/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
514 | 4/27/2007 | Not Challenging | Final | Not Challenging
515 | 10/5/2005 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC)
516 | 10/25/2005 | Potentially Challenging | Final | Potentially Challenging
517 | 3/23/2006 | Undetermined (PC‐CH) | Final | Challenging
518 | 3/30/2006 | Not Challenging | Final | Not Challenging
519 | 5/4/2007 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
520 | 6/6/2006 | Potentially Challenging | Final | Potentially Challenging
521 | 12/17/2007 | Not Challenging | Final | Not Challenging
522 | 9/19/2006 | Not Challenging | Final | Potentially Challenging
523 | 9/27/2006 | Not Challenging | Final | Potentially Challenging
524 | 10/11/2006 | Not Challenging | Final | Undetermined (NC‐PC)
525
526 | 1/30/2009 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
527 | 11/10/2009 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
528
529 | 11/28/2008 | Not Challenging | Final | Potentially Challenging
530 | 3/5/2008 | Not Challenging | Final | Not Challenging
531 | 8/24/2009 | Not Challenging | Final | Not Challenging
532
533 | 1/27/2000 | Not Challenging | Final | Not Challenging
534 | 4/10/2000 | Not Challenging | Final | Not Challenging
535 | 6/16/2000 | Not Challenging | Final | Not Challenging
536 | 8/24/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
537 | 10/13/2000 | Not Challenging | Final | Potentially Challenging
538 | 10/20/2000 | Not Challenging | Final | Potentially Challenging
539 | 10/23/2000 | Not Challenging | Final | Potentially Challenging
540 | 10/23/2000 | Not Challenging | Final | Not Challenging
541 | 10/24/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
542 | 3/4/2000 | Not Challenging | Final | Not Challenging
543 | 8/27/2001 | Not Challenging | Final | Not Challenging
544 | 12/13/2001 | Not Challenging | Final | Potentially Challenging
545 | 6/5/2002 | Not Challenging | Final | Not Challenging
546 | 10/9/2002 | Not Challenging | Final | Potentially Challenging
547 | 11/5/2002 | Not Challenging | Final | Not Challenging
548 | 11/13/2002 | Not Challenging | Final | Not Challenging
549 | 7/16/2004 | Not Challenging | Final | Potentially Challenging
550 | 2/2/2005 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
551 | 2/2/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
552 | 7/31/2003 | Not Challenging | Final | Not Challenging
553 | 6/24/2004 | Not Challenging | Final | Potentially Challenging
554 | 6/2/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
555 | 7/27/2005 | Not Challenging | Preliminary | Undetermined (NC‐PC)
556 | 10/14/2005 | Not Challenging | Final | Not Challenging
557 | 11/2/2005 | Not Challenging | Final | Not Challenging
558 | 12/13/2005 | Potentially Challenging | Preliminary | Potentially Challenging
559 | 9/12/2006 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
560 | 5/20/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
561 | 1/3/2005 | Not Challenging | Final | Not Challenging
562 | 10/9/2006 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
563 | 10/18/2006 | Not Challenging | Preliminary | Potentially Challenging
564 | 3/13/2007 | Not Challenging | Final | Not Challenging
565 | 4/25/2007 | Not Challenging | Final | Potentially Challenging
566 | 7/2/2007 | Not Challenging | Final | Not Challenging
567 | 7/31/2007 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
568 | 1/12/2008 | Not Challenging | Final | Potentially Challenging
569 | 5/15/2008 | Not Challenging | Final | Potentially Challenging
570 | 6/3/2008 | Potentially Challenging | Preliminary | Potentially Challenging
571 | 9/29/2008 | Not Challenging | Final | Potentially Challenging
572 | 12/23/2008 | Undetermined (NC‐PC) | Preliminary | Not Challenging
573 | 1/29/2009 | Not Challenging | Final | Not Challenging
574
575 | 5/18/2009 | Not Challenging | Final | Not Challenging
576 | 8/31/2009 | Not Challenging | Final | Not Challenging
577 | 9/16/2002 | Not Challenging | Final | Potentially Challenging
578 | 11/8/2003 | Not Challenging | Final | Not Challenging
579 | 3/23/2004 | Not Challenging | Final | Not Challenging
580 | 1/6/2003 | Not Challenging | Final | Not Challenging
581 | 4/17/2002 | Not Challenging | Final | Not Challenging
582 | 9/3/2004 | Not Challenging | Final | Potentially Challenging
583
584 | 10/8/2001 | Not Challenging | Final | Potentially Challenging
585 | 12/10/2002 | Not Challenging | Final | Not Challenging
586 | 5/5/2003 | Not Challenging | Final | Not Challenging
587 | 5/13/2003 | Not Challenging | Final | Not Challenging
588 | 11/30/2006 | Challenging | Final | Challenging
589
590 | 2/20/2005 | Not Challenging | Final | Not Challenging
591 | 7/19/2006 | Potentially Challenging | Final | Not Challenging
592 | 6/11/2009 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
593 | 10/16/2008 | Not Challenging | Final | Not Challenging
594 | 1/28/2000 | Not Challenging | Final | Undetermined (NC‐PC)
595 | 2/13/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
596 | 6/13/2000 | Not Challenging | Final | Undetermined (NC‐PC)
597 | 7/22/2000 | Not Challenging | Final | Undetermined (NC‐PC)
598 | 10/12/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
599 |  | Not Challenging | Final | Potentially Challenging
600 | 1/17/2004 | Not Challenging | Final | Not Challenging
601 | 10/28/2004 | Not Challenging | Final | Undetermined (NC‐PC)
602 | 9/29/2006 | Potentially Challenging | Final | Potentially Challenging
603 | 11/14/2007 | Potentially Challenging | Final | Potentially Challenging
604 | 9/8/2000 | Not Challenging | Final | Potentially Challenging
605 | 9/14/2001 | Not Challenging | Final | Not Challenging
606 | 10/31/2006 | Potentially Challenging | Final | Potentially Challenging
607 | 11/13/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging
608
609 |  | Not Challenging | Final | Not Challenging
10273 | 10/18/2000 | Not Challenging | Final | Not Challenging
10274 | 10/21/2000 | Not Challenging | Final | Not Challenging
10275
10276 | 12/15/2000 | Not Challenging | Final | Not Challenging
10277 | 12/22/2000 | Not Challenging | Final | Potentially Challenging
10278 | 4/4/2001 | Not Challenging | Final | Not Challenging
10279 | 4/14/2001 | Not Challenging | Final | Not Challenging
10280 | 4/17/2001 | Not Challenging | Final | Not Challenging
10281
10282 | 8/12/2001 | Not Challenging | Final | Not Challenging
10283 | 2/10/2004 | Not Challenging | Final | Not Challenging
10284 | 3/10/2004 | Not Challenging | Final | Not Challenging
10285 | 4/7/2004 | Not Challenging | Final | Potentially Challenging
10286 | 5/10/2004 | Potentially Challenging | Final | Potentially Challenging
10287 | 5/19/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
10288 | 5/22/2004 | Not Challenging | Final | Not Challenging
10289 | 5/28/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10290 | 6/3/2004 | Not Challenging | Final | Potentially Challenging
10291 | 9/18/2004 | Undetermined (PC‐CH) | Final | Challenging
10292 | 1/13/2005 | Not Challenging | Final | Not Challenging
10293 | 8/16/2005 | Not Challenging | Final | Not Challenging
10294 | 10/9/2005 | Not Challenging | Final | Undetermined (NC‐PC)
10295 | 10/18/2005 | Not Challenging | Final | Not Challenging
10296 | 8/21/2008 | Not Challenging | Final | Not Challenging
10297 | 12/14/2008 | Not Challenging | Final | Not Challenging
10298 | 2/12/2009 | Not Challenging | Final | Not Challenging
10299 | 2/19/2009 | Not Challenging | Final | Not Challenging
10300 | 6/25/2009 | Not Challenging | Final | Potentially Challenging
10301
10302 | 3/10/2000 | Not Challenging | Final | Undetermined (NC‐PC)
10303 | 5/18/2001 | Not Challenging | Final | Potentially Challenging
10304 | 4/8/2001 | Not Challenging | Final | Potentially Challenging
10305 | 10/25/2001 | Not Challenging | Final | Not Challenging
10306
10307 | 10/3/2003 | Not Challenging | Final | Not Challenging
10308 | 9/19/2004 | Not Challenging | Final | Potentially Challenging
10309 | 4/18/2006 | Not Challenging | Final | Undetermined (NC‐PC)
10310 | 1/29/2007 | Not Challenging | Final | Potentially Challenging
10311 | 1/9/2008 | Not Challenging | Final | Not Challenging
10312 | 2/9/2009 | Not Challenging | Final | Not Challenging
10313 | 4/3/2009 | Undetermined (NC‐PC) | Final | Not Challenging
10314
10315 | 10/18/2002 | Not Challenging | Final | Potentially Challenging
10316 | 11/22/2002 | Not Challenging | Final | Potentially Challenging
10317 | 9/23/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10318 | 10/16/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10319 | 1/7/2005 | Not Challenging | Final | Not Challenging
10320 | 5/25/2005 | Not Challenging | Final | Potentially Challenging
10321 | 6/1/2005 | Not Challenging | Final | Undetermined (NC‐PC)
10322 | 12/10/2005 | Not Challenging | Final | Not Challenging
10323 | 12/11/2005 | Not Challenging | Final | Not Challenging
10324 | 12/30/2005 | Not Challenging | Final | Not Challenging
10325
10326 | 1/24/2007 | Not Challenging | Final | Not Challenging
10327 | 6/21/2007 | Not Challenging | Final | Not Challenging
10328 | 7/17/2007 | Not Challenging | Final | Potentially Challenging
10329 | 9/22/2008 | Not Challenging | Final | Undetermined (NC‐PC)
10330 | 9/23/2008 | Not Challenging | Final | Undetermined (NC‐PC)
10331 | 3/24/2009 | Potentially Challenging | Final | Potentially Challenging
10332
10333
10334 | 3/30/2000 | Undetermined (NC‐PC) | Final | Challenging
10335
10336 | 10/2/2000 | Not Challenging | Final | Potentially Challenging
10337 | 10/11/2000 | Not Challenging | Final | Potentially Challenging
10338 | 9/13/2001 | Undetermined (PC‐CH) | Final | Potentially Challenging
10339 | 8/16/2004 | Not Challenging | Final | Not Challenging
10340
10341 | 5/21/2005 | Not Challenging | Final | Not Challenging
10342
10343 | 8/25/2005 | Not Challenging | Final | Not Challenging
10344 | 10/1/2005 | Not Challenging | Final | Potentially Challenging
10345 | 1/25/2006 | Not Challenging | Final | Potentially Challenging
10346
10347
10348
10349 | 9/24/2007 | Not Challenging | Final | Not Challenging
10350 | 1/21/2008 | Not Challenging | Final | Potentially Challenging
10351
10352 | 12/11/2008 | Not Challenging | Final | Not Challenging
10353 | 1/5/2009 | Not Challenging | Final | Potentially Challenging
10354 | 7/2/2009 | Not Challenging | Final | Not Challenging
10355 | 4/26/2008 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10356 | 10/3/2007 | Potentially Challenging | Preliminary | Potentially Challenging
10357 | 7/1/2005 | Potentially Challenging | Preliminary | Potentially Challenging
10358 | 7/3/2002 | Potentially Challenging | Preliminary | Potentially Challenging
10359 | 11/16/2000 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10360 | 10/13/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
10361 | 5/5/2005 | Potentially Challenging | Preliminary | Potentially Challenging
10362 | 10/28/2006 | Potentially Challenging | Preliminary | Potentially Challenging
10363 | 11/5/2009 | Potentially Challenging | Final | Potentially Challenging
10364 | 6/30/2005 | Potentially Challenging | Preliminary | Potentially Challenging
10365 | 8/22/2008 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
10366
10367 | 10/22/2000 | Potentially Challenging | Preliminary | Potentially Challenging
10368 | 6/28/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
10369 | 10/4/2002 | Potentially Challenging | Preliminary | Potentially Challenging
10370 | 4/11/2008 | Potentially Challenging | Preliminary | Potentially Challenging
10371 | 10/20/2009 | Not Challenging | Final | Potentially Challenging
10372 | 10/22/2009 | Not Challenging | Final | Potentially Challenging
10373 | 4/14/2005 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10374 | 7/11/2003 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10375
10376 | 3/23/2004 | Challenging | Preliminary | Challenging
10377 | 3/10/2000 | Not Challenging | Final | Not Challenging
10378 | 3/18/2000 | Not Challenging | Final | Not Challenging
10379 | 3/22/2000 | Not Challenging | Final | Not Challenging
10380 | 9/23/2000 | Not Challenging | Final | Potentially Challenging
10381 | 10/24/2000 | Not Challenging | Final | Not Challenging
10382 | 3/20/2001 | Not Challenging | Final | Potentially Challenging
10383 | 4/3/2001 | Not Challenging | Final | Potentially Challenging
10384 | 6/26/2001 | Not Challenging | Final | Not Challenging
10385 | 2/12/2002 | Not Challenging | Final | Not Challenging
10386 | 3/1/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging
10387 | 3/4/2003 | Not Challenging | Final | Potentially Challenging
10388
10389 | 9/8/2003 | Potentially Challenging | Final with disagreement | Potentially Challenging
10390
10391
10392 | 4/5/2004 | Not Challenging | Final | Potentially Challenging
10393 | 11/7/2004 | Not Challenging | Final | Not Challenging
10394 | 2/22/2005 | Potentially Challenging | Final | Potentially Challenging
10395 | 7/13/2005 | Not Challenging | Final | Not Challenging
10396 | 7/14/2005 | Not Challenging | Final | Potentially Challenging
10397 | 10/12/2005 | Potentially Challenging | Final | Challenging
10398
10399 | 1/31/2006 | Not Challenging | Final | Not Challenging
10400
10401 | 5/9/2006 | Not Challenging | Final | Not Challenging
10402 | 6/27/2006 | Not Challenging | Final | Potentially Challenging
10403 | 10/31/2006 | Not Challenging | Final | Not Challenging
10404 | 12/5/2006 | Not Challenging | Final | Not Challenging
10405 | 1/20/2007 | Not Challenging | Final | Not Challenging
10406 | 5/5/2007 | Not Challenging | Final | Challenging
10407 | 6/3/2007 | Potentially Challenging | Final | Potentially Challenging
10408
10409 | 12/12/2007 | Not Challenging | Final | Not Challenging
10410 | 2/13/2008 | Not Challenging | Final | Not Challenging
10411 | 3/8/2008 | Not Challenging | Final | Challenging
10412 | 2/17/2009 | Not Challenging | Final | Potentially Challenging
10413 | 5/17/2009 | Not Challenging | Final | Not Challenging
10414 | 8/31/2009 | Not Challenging | Final | Potentially Challenging
10415
10416 | 4/1/2007 | Not Challenging | Final | Not Challenging
10417 | 4/17/2007 | Not Challenging | Final | Not Challenging
10418 | 2/15/2008 | Not Challenging | Final | Potentially Challenging
10419 | 4/12/2008 | Not Challenging | Final | Not Challenging
10420 | 4/17/2008 | Not Challenging | Final | Not Challenging
10421 | 6/20/2008 | Not Challenging | Final | Potentially Challenging
10422 | 8/25/2008 | Not Challenging | Final | Not Challenging
10423 | 9/3/2008 | Not Challenging | Final | Not Challenging
10424 | 10/19/2009 | Not Challenging | Final | Potentially Challenging
10425 | 11/6/2009 | Not Challenging | Final | Not Challenging
10426 | 4/29/2002 | Not Challenging | Final | Potentially Challenging
10427 | 5/3/2001 | Not Challenging | Final | Potentially Challenging
10428 | 6/1/2000 | Not Challenging | Final | Potentially Challenging
10429 | 9/21/2002 | Not Challenging | Final | Not Challenging
10430 | 12/21/2000 | Potentially Challenging | Final | Potentially Challenging
10431
10432 | 10/22/2003 | Not Challenging | Final | Not Challenging
10433 | 12/10/2003 | Not Challenging | Final | Not Challenging
10434 | 5/7/2004 | Not Challenging | Final | Not Challenging
10435 | 7/8/2004 | Not Challenging | Final | Not Challenging
10436 | 8/11/2004 | Not Challenging | Final | Potentially Challenging
10437 | 5/9/2005 | Not Challenging | Final | Not Challenging
10438
10439
10440
10441 | 3/4/2009 | Potentially Challenging | Preliminary | Potentially Challenging
10442 | 3/9/2009 | Potentially Challenging | Preliminary | Potentially Challenging
10443 | 7/25/2009 | Potentially Challenging | Preliminary | Potentially Challenging
10444 | 10/13/2009 | Not Challenging | Final | Not Challenging
10445 | 2/7/2000 | Not Challenging | Final | Not Challenging
10446 | 4/11/2000 | Not Challenging | Final | Not Challenging
10447 | 3/9/2000 | Undetermined (NC‐PC) | Final | Not Challenging
10448 | 10/23/2001 | Not Challenging | Final | Not Challenging
10449 | 5/17/2001 | Not Challenging | Final | Not Challenging
10450 | 6/19/2001 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10451 | 6/5/2001 | Not Challenging | Final | Not Challenging
10452 | 9/17/2001 | Not Challenging | Final | Not Challenging
10453 | 11/20/2001 | Not Challenging | Final | Not Challenging
10454 | 2/17/2003 | Not Challenging | Final | Not Challenging
10455 | 3/22/2002 | Not Challenging | Final | Not Challenging
10456 | 7/19/2002 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10457 | 10/22/2002 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
10458 | 1/7/2003 | Not Challenging | Final | Not Challenging
10459 | Potentially Challenging | Preliminary | Potentially Challenging | Not Challenging
10460 | 4/9/2003 | Not Challenging | Final | Potentially Challenging
10461 | 3/6/2003 | Not Challenging | Final | Undetermined (NC‐PC)
10462 | 2/5/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
10463 | 3/1/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
10464 | 3/30/2005 | Challenging | Preliminary | Challenging
10465 | 9/30/2004 | Not Challenging | Final | Not Challenging
10466 | 8/31/2005 | Potentially Challenging | Preliminary | Potentially Challenging
10467 | 4/7/2005 | Not Challenging | Final | Not Challenging
10468 | 10/27/2005 | Not Challenging | Final | Not Challenging
10469 | 3/23/2006 | Not Challenging | Final | Not Challenging
10470 | 5/5/2006 | Not Challenging | Final | Potentially Challenging
10471 | 12/26/2007 | Not Challenging | Final | Potentially Challenging
10472 | 9/25/2007 | Challenging | Preliminary | Challenging
10473 | 1/23/2007 | Not Challenging | Final | Undetermined (NC‐PC)
10474 | 2/23/2007 | Not Challenging | Final | Not Challenging
10475
10476 | 4/10/2007 | Potentially Challenging | Preliminary | Potentially Challenging
10477 | 6/7/2007 | Potentially Challenging | Preliminary | Potentially Challenging
10478 | 7/10/2008 | Not Challenging | Final | Potentially Challenging
10479 | 7/23/2008 | Not Challenging | Final | Not Challenging
10480 | 7/23/2008 | Not Challenging | Final | Not Challenging
10481
10482 | 10/22/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging
10483 | 4/10/2007 | Not Challenging | Final | Not Challenging
10484 | 4/16/2007 | Not Challenging | Final | Not Challenging
10485 | 4/21/2007 | Not Challenging | Final | Not Challenging
10486 | 7/28/2007 | Not Challenging | Final | Not Challenging
10487 | 9/4/2007 | Not Challenging | Final | Challenging
10488 | 9/24/2007 | Not Challenging | Final | Not Challenging
10489 | 4/6/2008 | Challenging | Final | Challenging
10490 | 4/9/2008 | Not Challenging | Final | Potentially Challenging
10491 | 4/29/2008 | Not Challenging | Final | Potentially Challenging
10492 | 9/30/2008 | Not Challenging | Final | Undetermined (NC‐PC)
10493 | 10/23/2008 | Not Challenging | Final | Undetermined (NC‐PC)
10494
10495
10496 | 5/14/2009 | Not Challenging | Final | Not Challenging
10497 | 7/31/2009 | Not Challenging | Final | Potentially Challenging
10498 | 9/26/2009 | Not Challenging | Final | Not Challenging
10499 | 10/16/2009 | Not Challenging | Final | Not Challenging
10500
10501
10502
10503
10504 | 3/15/2000 | Not Challenging | Final | Potentially Challenging
10505 | 3/16/2000 | Not Challenging | Final | Not Challenging
10506
10507 | 3/14/2001 | Not Challenging | Final | Potentially Challenging
10508 | 3/28/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging
10509 | 4/1/2001 | Not Challenging | Final | Potentially Challenging
10510 | 4/10/2001 | Not Challenging | Final | Potentially Challenging
10511
10512 | 6/22/2001 | Not Challenging | Final | Potentially Challenging
10513 | 8/20/2001 | Not Challenging | Final | Potentially Challenging
10514 | 8/26/2001 | Potentially Challenging | Final | Potentially Challenging
10515 | 9/30/2001 | Potentially Challenging | Final | Potentially Challenging
10516 | 11/20/2001 | Potentially Challenging | Final | Potentially Challenging
10517 | 8/5/2002 | Not Challenging | Final | Potentially Challenging
10518 | 8/26/2002 | Not Challenging | Final | Potentially Challenging
10519 | 9/25/2002 | Not Challenging | Final | Undetermined (NC‐PC)
10520 | 11/26/2002 | Not Challenging | Final | Challenging
10521 | 9/10/2003 | Not Challenging | Final | Potentially Challenging
10522 | 11/2/2003 | Potentially Challenging | Final | Potentially Challenging
10523 | 11/9/2003 | Not Challenging | Final | Potentially Challenging
10524 | 1/7/2004 | Potentially Challenging | Final | Potentially Challenging
10525 | 5/10/2004 | Not Challenging | Final | Potentially Challenging
10526 | 5/30/2004 | Not Challenging | Final | Potentially Challenging
10527
10528 | 9/8/2004 | Not Challenging | Final | Potentially Challenging
10529 | 1/25/2006 | Not Challenging | Final | Potentially Challenging
10530 | 3/15/2006 | Not Challenging | Final | Undetermined (NC‐PC)
10531 | 3/31/2006 | Not Challenging | Final | Not Challenging
10532 | 6/28/2006 | Not Challenging | Final | Potentially Challenging
10533 | 2/1/2001 | Not Challenging | Final | Potentially Challenging
10534 | 3/21/2001 | Not Challenging | Final | Not Challenging
10535 | 3/31/2002 | Not Challenging | Final | Undetermined (NC‐PC)
10536 | 12/12/2002 | Not Challenging | Final | Undetermined (NC‐PC)
10537 | 2/17/2003 | Not Challenging | Final | Undetermined (NC‐PC)
10538 | 4/1/2003 | Not Challenging | Final | Potentially Challenging
10539 | 1/19/2004 | Not Challenging | Final | Potentially Challenging
10540 | 2/4/2004 | Not Challenging | Final | Challenging
10541 | 3/24/2001 | Not Challenging | Final | Not Challenging
10542 | 7/9/2003 | Not Challenging | Final | Not Challenging
10543 | 9/3/2003 | Not Challenging | Final | Not Challenging
10544 | 1/17/2003 | Not Challenging | Final | Potentially Challenging
10545 | 5/9/2002 | Not Challenging | Final | Challenging
10546 | 3/15/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10547 | 1/22/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10548 | 6/25/2003 | Not Challenging | Final | Undetermined (NC‐PC)
10549 | 10/8/2003 | Not Challenging | Final | Not Challenging
10550 | 9/3/2003 | Not Challenging | Final | Not Challenging
10551 | 7/14/2003 | Not Challenging | Final | Undetermined (NC‐PC)
10552 | 7/8/2003 | Not Challenging | Final | Not Challenging
10553 | 4/17/2000 | Not Challenging | Final | Not Challenging
10554 | 5/3/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10555 | 5/5/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
10556 | 5/11/2004 | Not Challenging | Final | Potentially Challenging
10557 | 1/13/2005 | Not Challenging | Final | Not Challenging
10558 | 1/19/2005 | Potentially Challenging | Final | Potentially Challenging
10559 | 3/7/2005 | Not Challenging | Final | Not Challenging
10560 | 3/29/2005 | Not Challenging | Final | Not Challenging
10561 | 4/4/2005 | Not Challenging | Final | Not Challenging
10562 | 5/23/2005 | Not Challenging | Final | Potentially Challenging
10563 | 7/11/2005 | Not Challenging | Final | Not Challenging
10564 | 8/10/2005 | Not Challenging | Final | Undetermined (NC‐PC)
10565 | 8/15/2005 | Not Challenging | Final | Potentially Challenging
10566 | 9/15/2005 | Not Challenging | Final | Not Challenging
10567 | 12/19/2005 | Not Challenging | Final | Not Challenging
10568 | 1/12/2006 | Not Challenging | Final | Not Challenging
10569 | 2/8/2006 | Not Challenging | Final | Not Challenging
10570 | 2/13/2006 | Not Challenging | Final | Not Challenging
10571 | 3/5/2006 | Not Challenging | Final | Potentially Challenging
10572 | 4/13/2006 | Not Challenging | Final | Challenging
10573 | 7/5/2006 | Not Challenging | Final | Not Challenging
10574 | 7/17/2006 | Not Challenging | Final | Not Challenging
10575 | 7/18/2006 | Not Challenging | Final | Potentially Challenging
10576 | 7/26/2006 | Potentially Challenging | Final | Potentially Challenging
10577 | 10/28/2006 | Not Challenging | Final | Not Challenging
10578
10579 | 4/4/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging
10580 | 4/26/2008 | Not Challenging | Final | Undetermined (NC‐PC)
10581 | 11/19/2008 | Not Challenging | Final | Potentially Challenging
10582 | 12/9/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
10583 | 9/1/2006 | Not Challenging | Final | Not Challenging
10584 | 7/27/2008 | Not Challenging | Final | Challenging
10585 | 4/24/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging
10586 | 1/19/2000 | Not Challenging | Final | Not Challenging
10587 | 8/10/2000 | Not Challenging | Final | Potentially Challenging
10588 | 11/21/2000 | Not Challenging | Final | Potentially Challenging
10589 | 2/3/2001 | Not Challenging | Final | Potentially Challenging
10590 | 10/3/2001 | Not Challenging | Final | Not Challenging
10591 | 10/8/2002 | Not Challenging | Final | Not Challenging
10592 | 1/7/2003 | Not Challenging | Final | Not Challenging
10593 | 7/7/2003 | Not Challenging | Final | Potentially Challenging
10594 | 1/25/2004 | Not Challenging | Final | Potentially Challenging
10595 | 2/11/2004 | Not Challenging | Final | Not Challenging
10596 | 11/4/2004 | Not Challenging | Final | Potentially Challenging
10597
10598 | 1/3/2006 | Not Challenging | Final | Not Challenging
10599 | 3/25/2006 | Potentially Challenging | Final | Potentially Challenging
10600 | 2/18/2008 | Not Challenging | Final | Potentially Challenging
10601 | 2/16/2005 | Not Challenging | Final | Not Challenging
10602 | 2/13/2008 | Not Challenging | Final | Not Challenging
10603
10604 | 5/14/2001 | Potentially Challenging | Final | Potentially Challenging
10605 | 1/31/2006 | Potentially Challenging | Final | Potentially Challenging
10606 | 5/6/2004 | Not Challenging | Final | Not Challenging
10607 | 12/27/2004 | Not Challenging | Final | Challenging
10608
10609 | 9/7/2008 | Not Challenging | Final | Not Challenging
10610 | 8/20/2009 | Potentially Challenging | Final | Potentially Challenging
10611
10612
10613
10614 | 2/25/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
10615 | 10/15/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
10616
10617 | 2/14/2003 | Undetermined (NC‐PC) | Final | Challenging
10618 | 2/15/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
10619 | 5/24/2000 | Not Challenging | Final | Not Challenging
10620 | 8/9/2000 | Not Challenging | Final | Potentially Challenging
10621 | 8/22/2000 | Not Challenging | Final | Undetermined (NC‐PC)
10622 | 6/25/2001 | Not Challenging | Final | Not Challenging
10623 | 8/8/2001 | Not Challenging | Final | Not Challenging
10624 | 10/26/2001 | Not Challenging | Final | Challenging
10625 | 9/28/2002 | Not Challenging | Final | Potentially Challenging
10626 | 12/11/2002 | Potentially Challenging | Final | Potentially Challenging
10627 | 12/12/2002 | Not Challenging | Final | Undetermined (NC‐PC)
10628 | 12/30/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
10629
10630 | 6/6/2007 | Potentially Challenging | Final | Potentially Challenging
10631 | 11/28/2001 | Not Challenging | Final | Potentially Challenging
10632 | 3/3/2000 | Challenging | Final | Challenging
10633 | 3/7/2000 | Potentially Challenging | Final | Undetermined (NC‐PC)
10634
10635
10636 | 9/26/2000 | Not Challenging | Final | Not Challenging
10637
10638 | 3/5/2001 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
10639 | 2/16/2001 | Not Challenging | Final | Potentially Challenging
10640
10641 | 3/11/2001 | Potentially Challenging | Preliminary | Potentially Challenging
10642 | 3/14/2002 | Potentially Challenging | Preliminary | Potentially Challenging
10643 | 5/22/2002 | Potentially Challenging | Preliminary | Potentially Challenging
10644 | 1/3/2002 | Potentially Challenging | Preliminary | Potentially Challenging
10645 | 4/11/2003 | Not Challenging | Final | Not Challenging
10646 | 7/17/2003 | Potentially Challenging | Preliminary | Potentially Challenging
10647 | 8/22/2003 | Potentially Challenging | Preliminary | Potentially Challenging
10648 | 3/12/2004 | Potentially Challenging | Preliminary | Potentially Challenging
10649 | 3/15/2004 | Potentially Challenging | Preliminary | Potentially Challenging
10650 | 3/20/2004 | Not Challenging | Final | Not Challenging
10651
10652 | 3/10/2005 | Not Challenging | Final | Potentially Challenging
10653 | 4/3/2005 | Not Challenging | Final | Not Challenging
10654 | 2/5/2007 | Not Challenging | Final | Not Challenging
10655
10656 | 2/22/2008 | Not Challenging | Final | Potentially Challenging
10657 | 6/29/2009 | Not Challenging | Final | Not Challenging
10658 | 12/29/2009 | Potentially Challenging | Preliminary | Potentially Challenging
10659
10660 | 11/6/2009 | Not Challenging | Final | Undetermined (NC‐PC)
10661
10662
10663
10664 | 10/2/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
10665 | 11/3/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
10666 | 4/18/2001 | Not Challenging | Final | Undetermined (NC‐PC)
10667 | 4/26/2001 | Not Challenging | Final | Undetermined (NC‐PC)
10668 | 4/22/2001 | Not Challenging | Final | Undetermined (NC‐PC)
10669 | 5/20/2001 | Not Challenging | Final | Not Challenging
10670 | 6/1/2001 | Not Challenging | Final | Not Challenging
10671 | 6/21/2001 | Not Challenging | Final | Not Challenging
10672 | 6/26/2001 | Not Challenging | Final | Undetermined (NC‐PC)
10673 | 9/4/2001 | Not Challenging | Final | Not Challenging
10674 | 12/5/2002 | Not Challenging | Final | Not Challenging
10675 | 12/31/2002 | Not Challenging | Final | Not Challenging
10676 | 3/29/2003 | Not Challenging | Final | Not Challenging
10677 | 4/4/2003 | Not Challenging | Final | Not Challenging
10678 | 5/29/2003 | Not Challenging | Final | Potentially Challenging
10679 | 1/9/2004 | Not Challenging | Final | Potentially Challenging
10680 | 7/10/2004 | Not Challenging | Final | Potentially Challenging
10681 | 11/12/2004 | Not Challenging | Final | Undetermined (NC‐PC)
10682 | 4/2/2005 | Not Challenging | Final | Undetermined (NC‐PC)
10683 | 4/5/2005 | Not Challenging | Final | Undetermined (NC‐PC)
10684 | 4/6/2005 | Potentially Challenging | Final | Not Challenging
10685 | 4/11/2005 | Not Challenging | Final | Not Challenging
10686 | 4/13/2005 | Not Challenging | Final | Potentially Challenging
10687 | 5/4/2005 | Not Challenging | Final | Potentially Challenging
10688 | 10/31/2006 | Not Challenging | Final | Not Challenging
10689 | 1/26/2007 | Not Challenging | Final | Potentially Challenging
10690 | 2/9/2007 | Not Challenging | Final | Potentially Challenging
10691 | 2/25/2007 | Not Challenging | Final | Potentially Challenging
10692
10693 | 3/4/2007 | Not Challenging | Final | Not Challenging
10694 | 7/10/2007 | Not Challenging | Final | Not Challenging
10695 | 7/27/2007 | Not Challenging | Final | Potentially Challenging
10696 | 8/30/2007 | Not Challenging | Final | Not Challenging
10697 | 2/25/2008 | Not Challenging | Final | Not Challenging
10698 | 4/18/2008 | Not Challenging | Final | Not Challenging
10699 | 4/24/2008 | Potentially Challenging | Final | Potentially Challenging
10700 | 7/18/2008 | Not Challenging | Final | Not Challenging
10701 | 8/25/2008 | Not Challenging | Final | Not Challenging
10702 | 2/8/2009 | Not Challenging | Final | Not Challenging
10703 | 11/21/2009 | Not Challenging | Final | Potentially Challenging
10704 | 3/28/2002 | Not Challenging | Final | Not Challenging
10705 | 12/3/2003 | Not Challenging | Final | Potentially Challenging
10706 | 12/4/2003 | Not Challenging | Final | Potentially Challenging
10707 | 8/8/2004 | Not Challenging | Final | Potentially Challenging
10708 | 9/22/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
10709 | 2/1/2005 | Not Challenging | Final | Potentially Challenging
10710 | 11/21/2005 | Not Challenging | Final | Potentially Challenging
10711 | 1/8/2006 | Not Challenging | Final | Potentially Challenging
10712 | 10/8/2006 | Not Challenging | Final | Potentially Challenging
10713 | 3/25/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging
10714
10715 | 2/5/2009 | Potentially Challenging | Final | Potentially Challenging
10716 | 7/26/2009 | Not Challenging | Final | Potentially Challenging
10717 | 4/12/2003 | Not Challenging | Final | Not Challenging
10718 | 5/20/2004 | Not Challenging | Final | Potentially Challenging
10719 | 6/1/2005 | Not Challenging | Final | Not Challenging
10720 | 4/8/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging
10721 | 8/26/2007 | Not Challenging | Final | Potentially Challenging
10722 | 9/3/2007 | Not Challenging | Final | Potentially Challenging
10723 | 10/4/2007 | Potentially Challenging | Final | Potentially Challenging
10724 | 10/7/2007 | Not Challenging | Final | Potentially Challenging
10725 | 10/29/2007 | Not Challenging | Final | Potentially Challenging
10726 | 11/4/2007 | Not Challenging | Final | Potentially Challenging
10727 | 2/5/2009 | Not Challenging | Final | Undetermined (NC‐PC)
10728 | 8/23/2009 | Not Challenging | Final | Potentially Challenging
10729 | 4/3/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging
10730 | 3/16/2006 | Not Challenging | Final | Potentially Challenging
10731 | 6/27/2008 | Not Challenging | Final | Not Challenging
10732 | 4/22/2002 | Not Challenging | Final | Undetermined (NC‐PC)
10733 | 4/7/2003 | Not Challenging | Final | Not Challenging
10734 | 4/27/2004 | Not Challenging | Final | Potentially Challenging
10735 | 4/28/2006 | Not Challenging | Final | Not Challenging
10736 | 12/6/2004 | Not Challenging | Final | Not Challenging
10737 | 11/30/2006 | Not Challenging | Final | Potentially Challenging
10738 | 8/22/2001 | Not Challenging | Final | Not Challenging
10739 | 4/24/2008 | Not Challenging | Final | Potentially Challenging
10740 | 10/8/2009 | Not Challenging | Final | Potentially Challenging
10741 | 9/21/2007 | Not Challenging | Final | Potentially Challenging
10742 | 4/11/2004 | Not Challenging | Final | Potentially Challenging
10743 | 4/19/2001 | Not Challenging | Final | Potentially Challenging
10744 | 8/17/2001 | Not Challenging | Final | Not Challenging
10745 | 7/25/2006 | Not Challenging | Final | Potentially Challenging
10746 | 5/12/2000 | Not Challenging | Final | Potentially Challenging
10747 | 1/15/1999 | Not Challenging | Final | Potentially Challenging
10748 | 5/29/2003 | Not Challenging | Final | Not Challenging
10749 | 9/10/2009 | Not Challenging | Final | Potentially Challenging
10750 | 2/28/2009 | Not Challenging | Final | Not Challenging
10751 | 1/28/2000 | Not Challenging | Final | Potentially Challenging
20264 | 1/19/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20265 | 2/2/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20266 | 2/19/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20267 | 3/12/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20268 | 4/19/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20269 | 4/30/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20270 | 6/7/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20271 | 7/9/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20272 | 9/10/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20273 | 9/18/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20274 | 10/9/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20275 | 10/11/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20276 | 10/12/1990 | Undetermined (NC‐PC) | Final | Not Challenging
20277 | 11/16/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20278 | 11/24/1990 | Not Challenging | Final | Not Challenging
20279 | 11/28/1990 | Not Challenging | Preliminary | Potentially Challenging
20280 | 12/5/1990 | Not Challenging | Final | Challenging
20281 | 6/24/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20282 | 9/17/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20283 | 10/3/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20284 | 10/14/1991 | Undetermined (NC‐PC) | Final | Challenging
20285 | 10/25/1991 | Not Challenging | Final | Not Challenging
20286 | 1/23/1992 | Not Challenging | Final | Undetermined (NC‐PC)
20287 | 2/29/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20288 | 3/9/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20289 | 3/16/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20290 | 4/26/1992 | Not Challenging | Final | Potentially Challenging
20291 | 4/28/1992 | Potentially Challenging | Final | Potentially Challenging
20292 | 6/25/1992 | Undetermined (NC‐PC) | Final | Not Challenging
20293 | 9/1/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20294 | 10/5/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20295 | 10/12/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20296 | 10/23/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20297 | 11/17/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20298 | 1/11/1993 | Undetermined (NC‐PC) | Preliminary | Challenging
20299 | 3/9/1993 | Not Challenging | Final | Not Challenging
20300 | 3/30/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20301 | 4/13/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20302 | 7/25/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20303 | 10/14/1993 | Potentially Challenging | Final | Potentially Challenging
20304 | 11/2/1993 | Potentially Challenging | Final | Undetermined (NC‐PC)
20305 | 11/18/1993 | Not Challenging | Final | Not Challenging
20306 | 12/30/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20307 | 1/25/1994 | Not Challenging | Final | Not Challenging
20308 | 3/9/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20309 | 3/11/1994 | Not Challenging | Preliminary | Not Challenging
20310 | 3/26/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20311 | 4/4/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20312 | 7/27/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20313 | 9/29/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20314 | 12/19/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20315 | 2/20/1995 | Not Challenging | Final | Not Challenging
20316 | 2/24/1995 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20317 | 4/10/1995 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20318 | 8/9/1995 | Not Challenging | Final | Potentially Challenging
20319 | 8/15/1995 | Undetermined (NC‐PC) | Final | Challenging
20320 | 3/21/1996 | Undetermined (NC‐PC) | Final | Challenging
20321 | 7/10/1996 | Not Challenging | Preliminary | Undetermined (NC‐PC)
20322 | 9/13/1996 | Undetermined (NC‐PC) | Final | Challenging
20323 | 1/8/1997 | Challenging | Preliminary | Challenging
20324 | 8/12/1997 | Undetermined (NC‐PC) | Final | Not Challenging
20325 | 1/16/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20326 | 10/12/1998 | Undetermined (NC‐PC) | Final | Not Challenging
20327 | 11/2/1998 | Not Challenging | Final | Not Challenging
20328 | 5/6/1999 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20329 | 9/1/1999 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20330 | 10/3/1999 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
20331 | 11/4/1999 | Not Challenging | Final | Not Challenging
20332 | 12/14/1999 | Not Challenging | Final | Potentially Challenging
20333 | 1/12/1990 | Not Challenging | Final | Not Challenging
20334 | 2/20/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20335 | 4/13/1990 | Not Challenging | Final | Undetermined (NC‐PC)
20336 | 2/14/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20337 | 4/21/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20338 | 10/11/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20339
20340 | 12/1/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20341 | 3/31/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20342 | 4/30/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20343 | 8/13/1993 | Not Challenging | Preliminary | Undetermined (NC‐PC)
20344 | 2/20/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20345 | 3/28/1994 | Not Challenging | Final | Undetermined (NC‐PC)
20346 | 3/30/1994 | Undetermined (NC‐PC) | Preliminary | Challenging
20347 | 4/15/1994 | Not Challenging | Preliminary | Challenging
20348 | 4/16/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20349 | 4/23/1994 | Undetermined (NC‐PC) | Preliminary | Challenging
20350 | 6/9/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20351 | 6/21/1994 | Undetermined (NC‐PC) | Preliminary | Challenging
20352 | 6/23/1994 | Potentially Challenging | Final | Potentially Challenging
20353 | 7/13/1994 | Potentially Challenging | Final | Potentially Challenging
20354 | 10/8/1994 | Not Challenging | Final | Challenging
20355 | 10/31/1994 | Not Challenging | Preliminary | Not Challenging
20356 | 2/19/1995 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
20357 | 5/24/1995 | Potentially Challenging | Final | Not Challenging
20358 | 1/23/1996 | Undetermined (NC‐PC) | Final | Not Challenging
20359 | 3/3/1996 | Potentially Challenging | Final | Challenging
20360 | 5/25/1996 | Undetermined (NC‐PC) | Final | Challenging
20361 | 1/7/1997 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20362 | 3/2/1997 | Potentially Challenging | Final | Undetermined (NC‐PC)
20363 | 7/27/1997 | Not Challenging | Preliminary | Undetermined (NC‐PC)
20364 | 12/4/1997 | Undetermined (NC‐PC) | Preliminary | Challenging
20365 | 1/13/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20366 | 2/6/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
20367 | 2/24/1998 | Potentially Challenging | Final | Undetermined (NC‐PC)
20368 | 6/7/1998 | Undetermined (NC‐PC) | Final | Not Challenging
20369 | 6/14/1998 | Potentially Challenging | Final | Not Challenging
20370 | 7/1/1998 | Undetermined (NC‐PC) | Final | Not Challenging
20371 | 9/9/1998 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
20372 | 11/23/1998 | Potentially Challenging | Preliminary | Potentially Challenging
20373 | 3/16/1999 | Potentially Challenging | Final | Not Challenging
20374 | 3/19/1999 | Potentially Challenging | Final | Potentially Challenging
20375 | 3/29/1999 | Not Challenging | Final | Potentially Challenging
20376 | 7/29/1999 | Not Challenging | Preliminary | Potentially Challenging
20377 | 2/8/2000 | Challenging | Preliminary | Challenging
20378 | 2/25/2000 | Potentially Challenging | Final | Potentially Challenging
20379 | 6/20/2000 | Challenging | Preliminary | Challenging
20380 | 8/16/2000 | Potentially Challenging | Final | Potentially Challenging
20381 | 10/17/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
20382 | 10/23/2000 | Potentially Challenging | Final | Undetermined (NC‐PC)
20383 | 11/5/2000 | Undetermined (NC‐PC) | Final | Not Challenging
20384
20385 | 12/27/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
30265 | 8/5/2008 | Not Challenging | Final | Not Challenging
30266 | 1/20/2009 | Potentially Challenging | Final | Potentially Challenging
30267
30268 | 8/9/2000 | Not Challenging | Final | Not Challenging
30269 | 8/14/2002 | Not Challenging | Final | Potentially Challenging
30270 | 3/16/2003 | Potentially Challenging | Final | Potentially Challenging
30271 | 9/11/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging
30272 | 7/9/2004 | Not Challenging | Final | Potentially Challenging
30273
30274
30275 | 1/13/2006 | Not Challenging | Final | Undetermined (NC‐PC)
30276 | 7/24/2006 | Potentially Challenging | Final | Potentially Challenging
30277 | 12/3/2007 | Potentially Challenging | Final | Potentially Challenging
30278 | 10/15/2000 | Not Challenging | Final | Not Challenging
30279 | 5/12/2002 | Not Challenging | Final | Not Challenging
30280
30281 | 6/5/2008 | Potentially Challenging | Final | Challenging
30282 | 11/26/2001 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
30283 | 3/20/2002 | Potentially Challenging | Preliminary | Potentially Challenging
30284 | 3/12/2004 | Not Challenging | Final | Not Challenging
30285 | 11/2/2007 | Not Challenging | Final | Not Challenging
30286 | 6/18/2009 | Potentially Challenging | Preliminary | Potentially Challenging
30287 | 10/1/2009 | Potentially Challenging | Preliminary | Potentially Challenging
30288 | 4/14/2000 | Not Challenging | Final | Potentially Challenging
30289 | 7/8/2000 | Not Challenging | Final | Challenging
30290 | 1/20/2001 | Not Challenging | Final | Not Challenging
30291 | 3/14/2001 | Not Challenging | Final | Potentially Challenging
30292 | 6/17/2001 | Not Challenging | Final | Potentially Challenging
30293 | 8/20/2001 | Not Challenging | Final | Not Challenging
30294 | 11/7/2001 | Not Challenging | Final | Not Challenging
30295 | 3/15/2002 | Not Challenging | Final | Not Challenging
30296 | 11/22/2002 | Potentially Challenging | Final | Challenging
30297 | 8/7/2003 | Not Challenging | Final | Potentially Challenging
30298 | 4/13/2006 | Not Challenging | Final | Potentially Challenging
30299 | 4/25/2006 | Not Challenging | Final | Potentially Challenging
30300 | 5/13/2006 | Not Challenging | Final | Not Challenging
30301 | 6/7/2006 | Not Challenging | Final | Potentially Challenging
30302 | 1/26/2007 | Potentially Challenging | Final | Potentially Challenging
30303 | 6/8/2007 | Not Challenging | Final | Not Challenging
30304 | 11/29/2007 | Not Challenging | Final | Undetermined (NC‐PC)
30305 | 12/14/2007 | Not Challenging | Final | Not Challenging
30306 | 1/17/2009 | Not Challenging | Final | Not Challenging
30307 | 3/27/2000 | Not Challenging | Final | Not Challenging
30308 | 4/3/2001 | Not Challenging | Final | Not Challenging
30309 | 7/21/2001 | Not Challenging | Final | Potentially Challenging
30310 | 9/7/2001 | Not Challenging | Final | Potentially Challenging
30311 | 9/24/2001 | Not Challenging | Final | Not Challenging
30312 | 3/29/2003 | Potentially Challenging | Final | Potentially Challenging
30313 | 11/5/2007 | Not Challenging | Final | Not Challenging
30314 | 12/19/2001 | Undetermined (PC‐CH) | Final | Challenging
30315
30316 | 3/16/2003 | Not Challenging | Final | Not Challenging
30317 | 4/18/2005 | Potentially Challenging | Final | Potentially Challenging
30318 | 5/16/2005 | Not Challenging | Final | Potentially Challenging
30319 | 7/18/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30320 | 5/8/2008 | Not Challenging | Final | Not Challenging
30321 | 11/21/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30322 | 10/28/2006 | Potentially Challenging | Final | Potentially Challenging
30323 | 12/9/2006 | Not Challenging | Final | Potentially Challenging
30324 | 1/11/2007 | Potentially Challenging | Final | Potentially Challenging
30325 | 11/6/2007 | Not Challenging | Final | Not Challenging
30326 | 5/1/2008 | Not Challenging | Final | Not Challenging
30327 | 3/6/2009 | Potentially Challenging | Final | Potentially Challenging
30328
30329
30330 | 4/30/2000 | Potentially Challenging | Final | Potentially Challenging
30331 | 10/12/2000 | Not Challenging | Final | Potentially Challenging
30332 | 4/6/2003 | Not Challenging | Final | Challenging
30333 | 7/31/2003 | Undetermined (PC‐CH) | Final | Challenging
30334 | 9/27/2003 | Not Challenging | Final | Potentially Challenging
30335 | 1/24/2004 | Not Challenging | Final | Potentially Challenging
30336 |  | Not Challenging | Final | Not Challenging
30337 |  | Not Challenging | Final | Not Challenging
30338 | 3/30/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging
30339 | 6/21/2000 | Not Challenging | Final | Not Challenging
30340 | 11/10/2000 | Potentially Challenging | Final | Potentially Challenging
30341 | 1/2/2001 | Potentially Challenging | Final | Potentially Challenging
30342 | 2/11/2002 | Undetermined (NC‐PC) | Final | Not Challenging
30343 | 5/3/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30344 | 1/23/2003 | Potentially Challenging | Final | Potentially Challenging
30345 | 8/29/2003 | Not Challenging | Final | Not Challenging
30346 | 10/22/2003 | Not Challenging | Final | Undetermined (NC‐PC)
30347 | 3/27/2009 | Not Challenging | Final | Not Challenging
30348 | 11/22/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30349
30350 | 7/26/2004 | Potentially Challenging | Final | Potentially Challenging
30351 | 5/14/2005 | Not Challenging | Final | Not Challenging
30352
30353
30354 | 2/8/2005 | Not Challenging | Final | Challenging
30355 | 2/17/2005 | Not Challenging | Final | Potentially Challenging
30356 | 11/21/2006 | Not Challenging | Final | Undetermined (NC‐PC)
30357 | 6/20/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging
30358 | 8/2/2007 | Not Challenging | Final | Potentially Challenging
30359 | 1/10/2008 | Not Challenging | Final | Not Challenging
30360 | 4/21/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30361 | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging
30362 | 12/16/2001 | Potentially Challenging | Final | Challenging
30363 | 5/5/2003 | Potentially Challenging | Final | Potentially Challenging
30364 | 5/26/2003 | Not Challenging | Final | Undetermined (NC‐PC)
30365 | 9/8/2003 | Not Challenging | Final | Not Challenging
30366 | 12/2/2003 | Not Challenging | Final | Not Challenging
30367 | 3/30/2004 | Not Challenging | Final | Not Challenging
30368 | 7/6/2004 | Not Challenging | Final | Not Challenging
30369 | 10/29/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30370 | 10/31/2005 | Potentially Challenging | Final | Potentially Challenging
30371 | 11/8/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30372 | 11/18/2005 | Not Challenging | Final | Not Challenging
30373 | 11/20/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30374 | 11/30/2005 | Potentially Challenging | Final | Potentially Challenging
30375 | 5/9/2007 | Not Challenging | Final | Not Challenging
30376 | 10/14/2007 | Not Challenging | Final | Not Challenging
30377 | 11/3/2007 | Not Challenging | Final | Not Challenging
30378 | 11/6/2007 | Not Challenging | Final | Not Challenging
30379 | 11/16/2007 | Not Challenging | Final | Undetermined (NC‐PC)
30380 | 12/17/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging
30381 | 4/7/2008 | Not Challenging | Final | Potentially Challenging
30382 | 5/21/2009 | Not Challenging | Final | Not Challenging
30383 | 2/11/2009 | Not Challenging | Final | Undetermined (NC‐PC)
30384 | 10/18/2000 | Not Challenging | Final | Not Challenging
30385 | 10/27/2000 | Potentially Challenging | Preliminary | Undetermined (NC‐PC)
30386 | 5/11/2001 | Potentially Challenging | Preliminary | Potentially Challenging
30387 | 5/24/2001 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30388 | 4/6/2002 | Potentially Challenging | Preliminary | Potentially Challenging
30389 | 10/18/2005 | Not Challenging | Final | Potentially Challenging
30390 | 5/7/2008 | Potentially Challenging | Preliminary | Potentially Challenging
30391 | 11/13/2009 | Not Challenging | Final | Not Challenging
30392 | 3/20/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
30393 | 3/24/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
30394 | 2/2/2003 | Potentially Challenging | Final | Potentially Challenging
30395 | 3/21/2004 | Undetermined (PC‐CH) | Final | Potentially Challenging
30396 | 3/22/2009 | Not Challenging | Final | Not Challenging
30397 | 4/4/2009 | Not Challenging | Final | Potentially Challenging
30398 | 10/17/2006 | Not Challenging | Final | Not Challenging
30399
30400 | 9/18/2007 | Not Challenging | Final | Potentially Challenging
30401 | 2/6/2008 | Not Challenging | Final | Potentially Challenging
30402 | 4/29/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30403 | 9/24/2009 | Not Challenging | Final | Not Challenging
30404 | 4/21/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging
30405 | 10/26/2009 | Not Challenging | Final | Not Challenging
30406
30407 | 4/30/2002 | Potentially Challenging | Final | Potentially Challenging
30408 | 3/19/2001 | Potentially Challenging | Final | Potentially Challenging
30409 | 8/21/2000 | Potentially Challenging | Final | Potentially Challenging
30410 | 10/25/2000 | Potentially Challenging | Final | Potentially Challenging
30411 | 3/28/2000 | Not Challenging | Final | Potentially Challenging
30412 | 4/25/2002 | Potentially Challenging | Final | Potentially Challenging
30413 | 4/25/2002 | Not Challenging | Final | Not Challenging
30414 | 3/28/2002 | Not Challenging | Final | Potentially Challenging
30415 | 4/29/2002 | Not Challenging | Final | Potentially Challenging
30416 | 4/29/2002 | Not Challenging | Final | Not Challenging
30417 | 3/20/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30418 | 2/19/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging
30419 | 10/4/2001 | Not Challenging | Final | Potentially Challenging
30420 | 3/18/2002 | Not Challenging | Final | Potentially Challenging
30421 | 3/5/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging
30422 | 11/27/2001 | Potentially Challenging | Final | Potentially Challenging
30423 | 3/17/2001 | Not Challenging | Final | Not Challenging
30424 | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging
30425 | 10/7/2002 | Potentially Challenging | Final | Potentially Challenging
30426 | 10/31/2002 | Not Challenging | Final | Potentially Challenging
30427
30428
30429 | 5/6/2004 | Potentially Challenging | Final | Potentially Challenging
30430 | 1/13/2006 | Not Challenging | Final | Challenging
30431 | 6/18/2006 | Not Challenging | Final | Not Challenging
30432
30433 | 6/2/2007 | Not Challenging | Final | Potentially Challenging
30434 | 8/12/2007 | Potentially Challenging | Final | Potentially Challenging
30435 | 8/16/2007 | Not Challenging | Final | Potentially Challenging
30436 | 9/30/2000 | Not Challenging | Final | Not Challenging
30437 | 10/6/2000 | Potentially Challenging | Final | Potentially Challenging
30438 | 5/15/2007 | Not Challenging | Final | Not Challenging
30439 | 3/21/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging
30440 | 10/26/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
30441 | 9/5/2001 | Not Challenging | Final | Potentially Challenging
30442 | 9/5/2001 | Not Challenging | Final | Potentially Challenging
30443 | 12/31/2001 | Not Challenging | Final | Not Challenging
30444 | 3/13/2002 | Not Challenging | Final | Not Challenging
30445 | 10/18/2002 | Not Challenging | Final | Not Challenging
30446 | 4/1/2003 | Potentially Challenging | Final | Potentially Challenging
30447 | 7/11/2004 | Potentially Challenging | Final | Potentially Challenging
30448
30449 | 10/8/2005 | Not Challenging | Final | Not Challenging
30450
30451
30452 | 8/8/2008 | Not Challenging | Final | Not Challenging
30453 | 1/30/2009 | Potentially Challenging | Final | Undetermined (NC‐PC)
30454 | 6/22/2009 | Not Challenging | Final | Potentially Challenging
30455 | 3/14/2000 | Not Challenging | Final | Potentially Challenging
30456 | 3/7/2001 | Potentially Challenging | Final | Potentially Challenging
30457 | 10/24/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30458 | 1/18/2003 | Not Challenging | Final | Potentially Challenging
30459 | 3/9/2003 | Potentially Challenging | Final | Potentially Challenging
30460 | 3/18/2003 | Potentially Challenging | Final | Potentially Challenging
30461 | 3/23/2004 | Not Challenging | Final | Potentially Challenging
30462 | 5/24/2004 | Not Challenging | Final | Potentially Challenging
30463 | 10/28/2009 | Not Challenging | Final | Not Challenging
30464 | 9/23/2008 | Not Challenging | Final | Potentially Challenging
30465 | 9/24/2008 | Potentially Challenging | Final | Potentially Challenging
30466
30467
30468
30469 | 11/11/2007 | Potentially Challenging | Final | Potentially Challenging
30470
30471 | 4/4/2008 | Potentially Challenging | Final | Potentially Challenging
30472 | 9/29/2006 | Potentially Challenging | Final | Potentially Challenging
30473 | 9/20/2001 | Not Challenging | Final | Potentially Challenging
30474 | 8/12/2002 | Not Challenging | Final | Challenging
30475 | 4/26/2003 | Not Challenging | Final | Potentially Challenging
30476 | 10/12/2003 | Not Challenging | Final | Challenging
30477
30478 | 9/9/2005 | Not Challenging | Final | Potentially Challenging
30479 | 9/24/2005 | Not Challenging | Final | Not Challenging
30480 | 9/25/2005 | Not Challenging | Final | Not Challenging
30481 | 9/25/2005 | Not Challenging | Final | Potentially Challenging
30482 | 10/5/2005 | Not Challenging | Final | Not Challenging
30483 | 10/9/2005 | Not Challenging | Final | Potentially Challenging
30484
30485 | 9/17/2006 | Not Challenging | Final | Undetermined (NC‐PC)
30486
30487 | 12/4/2006 | Not Challenging | Final | Potentially Challenging
30488
30489 | 10/5/2007 | Not Challenging | Final | Not Challenging
30490
30491
30492
30493 | 7/24/2008 | Challenging | Final | Challenging
30494
30495
30496
30497
30498 | 6/21/2009 | Not Challenging | Final | Potentially Challenging
30499
30500 | 5/29/2002 | Not Challenging | Preliminary | Potentially Challenging
30501
30502 | 10/8/2003 | Not Challenging | Final | Potentially Challenging
30503 | 3/8/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30504 | 3/17/2002 | Not Challenging | Final | Potentially Challenging
30505 | 3/11/2003 | Not Challenging | Final | Challenging
30506 | 12/17/2003 | Not Challenging | Final | Potentially Challenging
30507 | 7/26/2005 | Potentially Challenging | Final | Potentially Challenging
30508 | 3/26/2009 | Potentially Challenging | Final | Potentially Challenging
30509 | 8/11/2009 | Not Challenging | Final | Undetermined (NC‐PC)
30510 | 1/17/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30511 | 1/23/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30512 | 2/15/2006 | Potentially Challenging | Final with disagreement | Potentially Challenging
30513 | 5/27/2008 | Potentially Challenging | Final | Potentially Challenging
30514 | 3/7/2003 | Not Challenging | Final | Not Challenging
30515
30516 | 6/25/2005 | Not Challenging | Final | Potentially Challenging
30517 | 7/29/2005 | Not Challenging | Preliminary | Potentially Challenging
30518
30519 | 1/5/2009 | Not Challenging | Final | Potentially Challenging
30520 | 3/1/2000 | Not Challenging | Final | Potentially Challenging
30521 | 9/11/2000 | Not Challenging | Final | Undetermined (NC‐PC)
30522 | 9/12/2000 | Potentially Challenging | Final | Potentially Challenging
30523 | 9/14/2000 | Not Challenging | Final | Undetermined (NC‐PC)
30524 | 12/14/2000 | Undetermined (NC‐PC) | Final | Not Challenging
30525 | 3/7/2001 | Not Challenging | Final | Challenging
30526 | 6/12/2001 | Not Challenging | Final | Undetermined (NC‐PC)
30527 | 2/1/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30528 | 2/24/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30529 | 3/8/2002 | Not Challenging | Final | Not Challenging
30530 | 3/23/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30531 | 4/17/2002 | Not Challenging | Final | Not Challenging
30532 | 6/14/2002 | Not Challenging | Final | Potentially Challenging
30533 | 2/10/2003 | Not Challenging | Final | Potentially Challenging
30534 | 3/4/2004 | Not Challenging | Final | Not Challenging
30535 | 4/16/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30536 | 9/13/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30537 | 6/15/2005 | Not Challenging | Final | Potentially Challenging
30538 | 1/23/2005 | Not Challenging | Final | Potentially Challenging
30539 | 2/3/2005 | Not Challenging | Final | Potentially Challenging
30540 | 5/2/2005 | Not Challenging | Final | Potentially Challenging
30541 | 7/6/2005 | Potentially Challenging | Final | Potentially Challenging
30542 | 7/28/2005 | Not Challenging | Final | Not Challenging
30543 | 8/24/2005 | Not Challenging | Final | Potentially Challenging
30544 | 10/4/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30545 | 1/16/2006 | Not Challenging | Final | Potentially Challenging
30546 | 4/26/2006 | Not Challenging | Final | Potentially Challenging
30547 | 4/19/2006 | Not Challenging | Final | Potentially Challenging
30548 | 7/24/2006 | Not Challenging | Final | Potentially Challenging
30549 | 9/5/2006 | Not Challenging | Final | Potentially Challenging
30550 | 10/5/2006 | Not Challenging | Final | Potentially Challenging
30551 | 10/20/2006 | Not Challenging | Final | Undetermined (NC‐PC)
30552 | 5/8/2007 | Not Challenging | Final | Not Challenging
30553 | 8/28/2007 | Not Challenging | Final | Not Challenging
30554 | 10/17/2007 | Not Challenging | Final | Not Challenging
30555 | 4/1/2008 | Not Challenging | Final | Potentially Challenging
30556 | 4/4/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging
30557 | 4/30/2008 | Not Challenging | Final | Not Challenging
30558 | 10/20/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30559 | 11/21/2008 | Not Challenging | Final | Not Challenging
30560 | 2/4/2009 | Not Challenging | Final | Not Challenging
30561 | 4/3/2008 | Not Challenging | Final | Potentially Challenging
30562 | 3/17/2008 | Not Challenging | Final | Not Challenging
30563 | 3/9/2008 | Not Challenging | Final | Not Challenging
30564 | 11/18/2003 | Not Challenging | Final | Not Challenging
30565 | 2/11/2000 | Not Challenging | Final | Not Challenging
30566 | 9/11/2000 | Not Challenging | Final | Not Challenging
30567 | 10/17/2000 | Not Challenging | Final | Not Challenging
30568 | 1/19/2002 | Not Challenging | Final | Potentially Challenging
30569 | 10/16/2006 | Not Challenging | Final | Undetermined (NC‐PC)
30570 | 3/28/2001 | Not Challenging | Final | Not Challenging
30571 | 1/12/2001 | Not Challenging | Final | Not Challenging
30572 | 5/12/2002 | Not Challenging | Final | Undetermined (NC‐PC)
30573 | 6/6/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30574 | 11/2/2000 | Not Challenging | Final | Potentially Challenging
30575
30576 | 8/15/2006 | Not Challenging | Final | Potentially Challenging
30577 | 3/3/2000 | Not Challenging | Final | Potentially Challenging
30578 | 2/27/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging
30579 | 6/6/2007 | Not Challenging | Final | Undetermined (NC‐PC)
30580 | 6/21/2000 | Not Challenging | Final | Potentially Challenging
30581 | 6/19/2007 | Not Challenging | Final | Not Challenging
30582 | 6/7/2000 | Not Challenging | Final | Undetermined (NC‐PC)
30583 | 6/30/2003 | Not Challenging | Final | Potentially Challenging
30584 | 5/24/2001 | Not Challenging | Final | Undetermined (NC‐PC)
30585 | 5/3/2001 | Not Challenging | Final | Not Challenging
30586 | 1/11/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30587 | 3/4/2009 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30588 | 5/14/2009 | Not Challenging | Final | Not Challenging
30589 | 10/11/2009 | Not Challenging | Final | Potentially Challenging
30590 | 12/22/2009 | Not Challenging | Final | Not Challenging
30591 | 10/17/2005 | Not Challenging | Final | Undetermined (NC‐PC)
30592
30593 | 2/7/2008 | Undetermined (PC‐CH) | Final | Potentially Challenging
30594 | 6/17/2007 | Not Challenging | Final | Not Challenging
30595 | 10/10/2008 | Not Challenging | Final | Undetermined (NC‐PC)
30596 | 10/17/2008 | Not Challenging | Final | Not Challenging
30597 | 2/5/2009 | Potentially Challenging | Final | Potentially Challenging
30598 | 11/20/2009 | Potentially Challenging | Final | Potentially Challenging
30599 | 3/23/2001 | Not Challenging | Final | Not Challenging
30600 | 11/9/2001 | Not Challenging | Final | Not Challenging
30601 | 9/14/2001 | Not Challenging | Final | Not Challenging
30602 | 5/19/2004 | Not Challenging | Final | Not Challenging
30603 | 1/13/2005 | Not Challenging | Final | Not Challenging
30604 | 5/28/2005 | Potentially Challenging | Final | Potentially Challenging
30605 | 9/19/2005 | Not Challenging | Final | Not Challenging
30606 | 12/19/2007 | Not Challenging | Final | Not Challenging
30607 | 3/20/2001 | Not Challenging | Final | Not Challenging
30608 | 1/10/2002 | Not Challenging | Final | Not Challenging
30609 | 4/17/2001 | Not Challenging | Final | Not Challenging
30610 | 7/21/2002 | Not Challenging | Final | Potentially Challenging
30693 | 2/3/2004 | Potentially Challenging | Final | Potentially Challenging
30694 | 8/10/2004 | Not Challenging | Final | Potentially Challenging
30695 | 9/21/2006 | Not Challenging | Final | Potentially Challenging
30696 | 9/26/2006 | Not Challenging | Final | Not Challenging
30697 | 9/29/2006 | Not Challenging | Final | Potentially Challenging
30698 | 2/22/2007 | Not Challenging | Final | Potentially Challenging
30699 | 3/7/2007 | Not Challenging | Final | Not Challenging
30700 | 4/19/2007 | Not Challenging | Final | Not Challenging
30701 | 8/13/2007 | Not Challenging | Final | Not Challenging
30702 | 9/11/2007 | Not Challenging | Final | Not Challenging
30703 | 10/2/2007 | Not Challenging | Final | Potentially Challenging
30704 | 10/17/2007 | Not Challenging | Final | Not Challenging
30705 | 9/20/2007 | Not Challenging | Final | Not Challenging
30706 | 6/28/2000 | Not Challenging | Final | Undetermined (NC‐PC)
30707 | 10/1/2000 | Not Challenging | Final | Potentially Challenging
30708 | 2/6/2001 | Not Challenging | Final | Not Challenging
30709 | 7/13/2001 | Not Challenging | Final | Not Challenging
30710 | 9/19/2001 | Not Challenging | Final | Potentially Challenging
30711 | 11/16/2001 | Not Challenging | Final | Not Challenging
30712 | 4/24/2002 | Not Challenging | Final | Potentially Challenging
30713 | 4/29/2002 | Not Challenging | Final | Potentially Challenging
30714
30715
30716 | 9/2/2002 | Not Challenging | Final | Not Challenging
30717 | 12/10/2002 Undetermined (NC‐PC) | Undetermined (NC‐PC) | Final | Potentially Challenging
30718 | 4/15/2003 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30719 | 6/11/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging
30720 | 7/2/2003 | Not Challenging | Final | Potentially Challenging
30721 | 8/27/2003 | Not Challenging | Final | Potentially Challenging
30722 | 10/19/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging
30723 | 11/3/2008 | Not Challenging | Final | Not Challenging
30724 | 11/16/2008 | Not Challenging | Final | Not Challenging
30725 | 4/12/2000 | Potentially Challenging | Final | Potentially Challenging
30726 | 5/19/2000 | Not Challenging | Final | Not Challenging
30727 | 10/30/2000 | Potentially Challenging | Final | Potentially Challenging
30728 | 12/21/2000 | Not Challenging | Final | Potentially Challenging
30729 | 12/22/2000 | Not Challenging | Final | Undetermined (NC‐PC)
30730 | 3/5/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging
30731 | 3/19/2001 | Potentially Challenging | Final | Potentially Challenging
30732 | 12/3/2001 | Potentially Challenging | Final | Potentially Challenging
30733 | 6/27/2002 | Potentially Challenging | Final | Potentially Challenging
30734 | 8/26/2002 | Potentially Challenging | Final | Potentially Challenging
30735 | 3/4/2003 | Not Challenging | Final | Potentially Challenging
30736 | 3/13/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging
30737 | 5/12/2003 | Not Challenging | Final | Potentially Challenging
30738 | 9/23/2003 | Not Challenging | Final | Not Challenging
30739 | 3/29/2001 | Not Challenging | Final | Not Challenging
30740 | 2/6/2004 | Potentially Challenging | Final | Potentially Challenging
30741 | 3/24/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30742 | 4/15/2004 | Not Challenging | Final | Not Challenging
30743 | 4/27/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30744 | 6/2/2004 | Not Challenging | Final | Challenging
30745 | 10/10/2004 | Not Challenging | Final | Not Challenging
30746 | 10/28/2004 | Not Challenging | Final | Undetermined (NC‐PC)
30747 | 11/6/2004 | Not Challenging | Final | Not Challenging
30748 | 11/27/2004 | Not Challenging | Final | Potentially Challenging
30749 | 1/9/2005 | Not Challenging | Final | Not Challenging
30750 | 5/9/2005 | Undetermined (PC‐CH) | Final | Potentially Challenging
30751 | 3/28/2006 | Not Challenging | Final | Not Challenging
30752 | 4/3/2007 | Potentially Challenging | Final | Potentially Challenging
30753 | 5/16/2007 | Not Challenging | Final | Potentially Challenging
30754 | 2/2/2008 | Not Challenging | Final | Not Challenging
30755 | 4/7/2008 | Not Challenging | Final | Not Challenging
30756 | 11/23/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
30757 | 8/24/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging
30758 | 9/3/2009 | Not Challenging | Final | Not Challenging
40730 | 10/27/2000 | Not Challenging | Final | Not Challenging
40731 | 2/13/2001 | Not Challenging | Final | Potentially Challenging
40732 | 3/8/2001 | Not Challenging | Final | Potentially Challenging
40733 | 3/14/2001 | Potentially Challenging | Final | Potentially Challenging
40734 | 3/19/2001 | Not Challenging | Final | Not Challenging
40735 | 4/4/2001 | Potentially Challenging | Final | Potentially Challenging
40736 | 4/15/2001 | Not Challenging | Final | Potentially Challenging
40737 | 4/17/2001 | Not Challenging | Final | Not Challenging
40738 | 6/5/2002 | Not Challenging | Final | Challenging
40739 | 7/23/2002 | Not Challenging | Final | Not Challenging
40740 | 3/3/2003 | Not Challenging | Final | Not Challenging
40741 | 4/16/2003 | Not Challenging | Final | Potentially Challenging
40742 | 7/7/2003 | Not Challenging | Final | Not Challenging
40743 | 10/7/2003 | Not Challenging | Final | Not Challenging
40744 | 3/24/2004 | Not Challenging | Final | Potentially Challenging
40745 | 10/20/2005 | Not Challenging | Final | Not Challenging
40746 | 8/15/2006 | Potentially Challenging | Final | Not Challenging
40747 | 4/17/2007 | Not Challenging | Final | Not Challenging
40748 | 11/28/2007 | Not Challenging | Final | Not Challenging
40749 | 6/13/2008 | Challenging | Final | Challenging
40750 | 11/16/2009 | Not Challenging | Final | Not Challenging
50356 | 1/11/2000 | Not Challenging | Final | Not Challenging
50357 | 3/21/2000 | Not Challenging | Final | Not Challenging
50358 | 6/1/2000 | Not Challenging | Final | Challenging
50359 | 8/24/2000 | Not Challenging | Final | Not Challenging
50360 | 12/20/2000 | Not Challenging | Final | Not Challenging
50361 | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging
50362 | 7/16/2001 | Not Challenging | Final | Potentially Challenging
50363
50364 | 10/4/2001 | Not Challenging | Final | Not Challenging
50365 | 3/4/2002 | Not Challenging | Final | Potentially Challenging
50366 | 3/8/2002 | Not Challenging | Final | Not Challenging
50367 | 3/14/2002 | Not Challenging | Final | Not Challenging
50368 | 6/6/2002 | Not Challenging | Final | Undetermined (NC‐PC)
50369 | 8/14/2002 | Not Challenging | Final | Potentially Challenging
50370 | 10/23/2002 | Not Challenging | Final | Potentially Challenging
50371 | 11/1/2002 | Not Challenging | Final | Potentially Challenging
50372 | 5/9/2003 | Not Challenging | Final | Not Challenging
50373 | 10/7/2003 | Not Challenging | Final | Not Challenging
50374 | 4/22/2004 | Not Challenging | Final | Potentially Challenging
50375 | 9/30/2004 | Not Challenging | Final | Not Challenging
50376 | 3/24/2005 | Not Challenging | Final | Not Challenging
50377 | 7/2/2005 | Not Challenging | Final | Not Challenging
50378 | 7/27/2005 | Potentially Challenging | Final | Potentially Challenging
50379 | 2/24/2006 | Not Challenging | Final | Not Challenging
50380 | 8/31/2006 | Not Challenging | Final | Not Challenging
50381 | 12/14/2006 | Undetermined (NC‐PC) | Final | Not Challenging
50382 | 1/29/2007 | Not Challenging | Final | Not Challenging
50383 | 3/1/2007 | Not Challenging | Final | Not Challenging
50384 | 3/22/2007 | Not Challenging | Final | Not Challenging
50385 | 5/30/2007 | Not Challenging | Final | Challenging
50386
50387 | 3/29/2008 | Not Challenging | Final | Not Challenging
50388 | 6/8/2008 | Not Challenging | Final | Not Challenging
50389 | 6/23/2008 | Not Challenging | Final | Potentially Challenging
50390 | 10/1/2008 | Not Challenging | Final | Not Challenging
50391 | 7/2/2009 | Not Challenging | Final | Potentially Challenging
50392 | 8/13/2000 | Not Challenging | Final | Not Challenging
50393 | 10/17/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
50394 | 4/21/2001 | Not Challenging | Final | Not Challenging
50395 | 4/16/2001 | Not Challenging | Preliminary | Potentially Challenging
50396 | 5/1/2001 | Not Challenging | Final | Not Challenging
50397 | 1/13/2003 | Not Challenging | Final | Not Challenging
50398 | 12/2/2003 | Not Challenging | Final | Not Challenging
50399 | 2/26/2004 | Not Challenging | Final | Not Challenging
50400 | 8/7/2004 | Not Challenging | Final | Not Challenging
50401 | 10/4/2005 | Not Challenging | Final | Potentially Challenging
50402 | 11/8/2005 | Not Challenging | Final | Not Challenging
50403 | 11/8/2003 | Not Challenging | Final | Undetermined (NC‐PC)
50404 | 11/25/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC)
50405 | 3/4/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging
50406 | 8/21/2007 | Not Challenging | Final | Not Challenging
50407 | 3/11/2008 | Potentially Challenging | Preliminary | Potentially Challenging
50408
50409 | 10/5/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50410 | 9/29/2005 | Not Challenging | Final | Undetermined (NC‐PC)
50411 | 7/9/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50412
50413
50414
50415
50416
50417
50418
50419
50420
50421
50422
50423 | 2/28/2000 | Not Challenging | Final | Not Challenging
50424 | 3/15/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50425 | 3/16/2000 | Potentially Challenging | Final | Potentially Challenging
50426 | 5/2/2000 | Potentially Challenging | Final | Potentially Challenging
50427 | 8/19/2000 | Not Challenging | Final | Not Challenging
50428 | 9/20/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50429 | 3/19/2001 | Not Challenging | Final | Potentially Challenging
50430 | 2/18/2000 | Not Challenging | Final | Not Challenging
50431
50432 | 3/19/2001 | Not Challenging | Final | Not Challenging
50433 | 8/17/2001 | Not Challenging | Final | Undetermined (NC‐PC)
50434 | 10/28/2001 | Not Challenging | Final | Not Challenging
50435 | 7/22/2002 | Not Challenging | Final | Not Challenging
50436 | 8/12/2002 | Not Challenging | Final | Potentially Challenging
50437
50438 | 1/7/2003 | Not Challenging | Final | Not Challenging
50439 | 3/3/2003 | Not Challenging | Final | Not Challenging
50440 | 10/13/2004 | Not Challenging | Final | Undetermined (NC‐PC)
50441 | 10/23/2004 | Not Challenging | Final | Potentially Challenging
50442 | 11/8/2004 | Potentially Challenging | Final | Potentially Challenging
50443 | 3/20/2005 | Not Challenging | Final | Not Challenging
50444 | 4/27/2005 | Not Challenging | Final | Not Challenging
50445 | 4/28/2005 | Not Challenging | Final | Potentially Challenging
50446 | 7/14/2005 | Not Challenging | Final | Not Challenging
50447 | 9/14/2005 | Potentially Challenging | Final | Potentially Challenging
50448 | 10/11/2005 | Potentially Challenging | Final | Potentially Challenging
50449 | 2/21/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50450 | 2/28/2006 | Not Challenging | Final | Not Challenging
50451 | 7/15/2006 | Not Challenging | Final | Potentially Challenging
50452 | 8/18/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50453 | 8/22/2006 | Not Challenging | Final | Potentially Challenging
50454 | 11/8/2006 | Potentially Challenging | Final | Undetermined (NC‐PC)
50455 | 11/30/2006 | Not Challenging | Final | Not Challenging
50456 | 2/15/2007 | Not Challenging | Final | Not Challenging
50457 | 7/28/2007 | Not Challenging | Final | Challenging
50458 | 8/15/2007 | Not Challenging | Final | Undetermined (NC‐PC)
50459 | 2/8/2008 | Not Challenging | Final | Not Challenging
50460 | 4/16/2008 | Not Challenging | Final | Potentially Challenging
50461 | 4/24/2008 | Not Challenging | Final | Potentially Challenging
50462 | 6/12/2008 | Not Challenging | Final | Potentially Challenging
50463 | 4/11/2000 | Not Challenging | Final | Not Challenging
50464 | 4/26/2000 | Not Challenging | Final | Not Challenging
50465
50466 | 2/4/2005 | Not Challenging | Final | Not Challenging
50467 | 2/4/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50468 | 11/2/2007 | Not Challenging | Final | Not Challenging
50469 | 7/28/2008 | Not Challenging | Final | Not Challenging
50470 | 11/19/2008 | Not Challenging | Final | Not Challenging
50471 | 12/2/2008 | Potentially Challenging | Final | Potentially Challenging
50472 | 8/30/2009 | Not Challenging | Final | Not Challenging
50473 | 6/26/2000 | Potentially Challenging | Final with disagreement | Potentially Challenging
50474 | 8/29/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50475 | 10/11/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50476 | 12/19/2000 | Not Challenging | Final | Potentially Challenging
50477 | 3/18/2000 | Potentially Challenging | Final | Potentially Challenging
50478 | 3/19/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50479 | 3/22/2000 | Potentially Challenging | Final | Potentially Challenging
50480 | 4/7/2000 | Not Challenging | Final | Potentially Challenging
50481 | 11/4/2006 | Not Challenging | Final | Not Challenging
50482 | 3/8/2006 | Not Challenging | Final | Potentially Challenging
50483 | 3/11/2008 | Not Challenging | Final | Not Challenging
50484 | 3/23/2008 | Not Challenging | Final | Not Challenging
50485
50486 | 4/20/2008 | Not Challenging | Final | Not Challenging
50487 | 3/6/2009 | Not Challenging | Final | Not Challenging
50488 | 5/27/2009 | Not Challenging | Final | Not Challenging
50489 | 8/30/2009 | Not Challenging | Final | Not Challenging
50490 | 9/16/2009 | Not Challenging | Final | Not Challenging
50491 | 10/16/2009 | Not Challenging | Final | Not Challenging
50492 | 11/2/2009 | Not Challenging | Final | Not Challenging
50493
50494 | 2/5/2009 | Not Challenging | Final | Challenging
50495 | 11/11/2002 | Not Challenging | Final | Not Challenging
50496 | 1/21/2002 | Not Challenging | Final | Not Challenging
50497 | 8/15/2006 | Not Challenging | Final | Not Challenging
50498
50499 | 4/1/2004 | Not Challenging | Final | Not Challenging
50500
50501 | 11/6/2001 | Not Challenging | Final | Not Challenging
50502 | 10/16/2002 | Not Challenging | Final | Not Challenging
50503 | 6/14/2001 | Not Challenging | Final | Potentially Challenging
50504 | 5/20/2002 | Potentially Challenging | Final | Potentially Challenging
50505
50506 | 12/9/2007 | Not Challenging | Final | Potentially Challenging
50507 | 11/15/2005 | Not Challenging | Final | Not Challenging
50508 | 11/26/2005 | Not Challenging | Final | Not Challenging
50509
50510 | 4/19/2000 | Not Challenging | Final | Not Challenging
50511 | 5/15/2004 | Not Challenging | Final | Not Challenging
50512 | 5/31/2000 | Not Challenging | Final | Not Challenging
50513 | 8/27/2003 | Not Challenging | Final | Potentially Challenging
50514 | 4/29/2009 | Not Evaluated | Preliminary | Potentially Challenging
50515 | 11/30/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging
50516 | 10/5/2001 | Not Challenging | Final | Not Challenging
50517 | 10/8/2001 | Not Challenging | Final | Potentially Challenging
50518 | 11/18/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging
50519 | 10/19/2009 | Not Challenging | Final | Potentially Challenging
50520 | 12/7/2001 | Not Challenging | Final | Undetermined (NC‐PC)
50521 | 2/1/2007 | Not Challenging | Final | Potentially Challenging
50522 | 9/8/2003 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50523 | 9/19/2003 | Not Challenging | Final | Not Challenging
50524 | 1/23/2008 | Not Challenging | Final | Not Challenging
50525 | 12/18/2009 | Not Evaluated | Preliminary | Potentially Challenging
50526 | 12/7/2006 | Not Evaluated | Preliminary | Potentially Challenging
50527 | 6/23/2004 | Not Challenging | Final | Not Challenging
50528 | 6/19/2005 | Not Challenging | Final | Not Challenging
50529 | 3/31/2003 | Not Challenging | Final | Not Challenging
50530 | 10/21/2008 | Potentially Challenging | Final | Potentially Challenging
50531
50532
50533
50534 | 1/7/2002 | Not Evaluated | Preliminary | Potentially Challenging
50535 | 1/8/2002 | Not Challenging | Preliminary | Undetermined (NC‐PC)
50536 | 3/21/2002 | Not Evaluated | Preliminary | Potentially Challenging
50537 | 3/23/2002 | Not Challenging | Final | Not Challenging
50538 | 3/27/2002 | Not Evaluated | Preliminary | Potentially Challenging
50539 | 5/22/2002 | Not Challenging | Preliminary | Potentially Challenging
50540 | 5/25/2002 | Not Challenging | Final | Not Challenging
50541 | 4/6/2002 | Not Challenging | Final | Not Challenging
50542 | 7/30/2002 | Not Challenging | Final | Not Challenging
50543 | 3/27/2001 | Potentially Challenging | Final | Potentially Challenging
50544
50545 | 9/18/2003 | Not Challenging | Final | Not Challenging
50546 | 12/1/2004 | Not Challenging | Final | Undetermined (NC‐PC)
50547 | 4/4/2006 | Not Challenging | Final | Not Challenging
50548 | 6/9/2006 | Not Challenging | Final | Not Challenging
50549 | 1/21/2007 | Not Challenging | Final | Not Challenging
50550 | 6/9/2007 | Not Challenging | Final | Not Challenging
50551 | 10/6/2008 | Not Challenging | Final | Not Challenging
50552 | 3/23/2009 | Not Challenging | Final | Not Challenging
50553 | 5/2/2003 | Potentially Challenging | Final | Potentially Challenging
50554 | 5/19/2003 | Not Challenging | Final | Undetermined (NC‐PC)
50555 | 6/25/2003 | Not Challenging | Final | Undetermined (NC‐PC)
50556 | 2/25/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
50557 | 1/16/2001 | Not Challenging | Final | Not Challenging
50558 | 1/2/2007 | Not Challenging | Final | Not Challenging
50559
50560
50561
50562 | 5/28/2005 | Not Challenging | Final | Not Challenging
50563 | 11/16/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
50564 | 1/15/2007 | Not Challenging | Final | Not Challenging
50565 | 8/26/2008 | Not Challenging | Final | Not Challenging
50566 | 9/17/2008 | Not Challenging | Final | Challenging
50567
50568
50569 | 3/24/2004 | Not Challenging | Final | Not Challenging
50570 | 6/21/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
50571 | 7/22/2004 | Not Challenging | Final | Not Challenging
50572 | 10/8/2003 | Not Challenging | Final | Not Challenging
50573 | 8/24/2004 | Not Challenging | Final | Not Challenging
50574 | 9/16/2004 | Not Challenging | Final | Not Challenging
50575 | 9/14/2007 | Not Challenging | Final | Potentially Challenging
50576 | 9/17/2004 | Not Challenging | Final | Not Challenging
50577 | 10/23/2004 | Not Challenging | Final | Not Challenging
50578 | 11/23/2004 | Not Challenging | Final | Not Challenging
50579 | 5/4/2005 | Not Challenging | Final | Not Challenging
50580 | 10/9/2004 | Not Challenging | Final | Challenging
50581 | 6/24/2005 | Not Challenging | Final | Potentially Challenging
50582 | 8/22/2005 | Not Challenging | Final | Not Challenging
50583 | 9/3/2005 | Not Challenging | Final | Not Challenging
50584 | 6/27/2005 | Not Challenging | Final | Not Challenging
50585 | 10/8/2009 | Not Challenging | Final | Not Challenging
50586 | 9/28/2005 | Not Challenging | Final | Potentially Challenging
50587 | 2/4/2006 | Not Challenging | Final | Not Challenging
50588 | 2/4/2006 | Not Challenging | Final | Not Challenging
50589 | 4/15/2006 | Not Challenging | Final | Not Challenging
50590 | 5/6/2006 | Not Challenging | Final | Not Challenging
50591 | 5/29/2006 | Not Challenging | Final | Potentially Challenging
50592 | 7/11/2006 | Not Challenging | Final | Potentially Challenging
50593 | 10/4/2006 | Not Challenging | Final | Not Challenging
50594 | 10/5/2006 | Not Challenging | Final | Not Challenging
50595 | 10/28/2007 | Not Challenging | Final | Not Challenging
50596 | 1/5/2007 | Not Challenging | Final | Not Challenging
50597 | 12/18/2007 | Not Challenging | Final | Not Challenging
50598 | 3/10/2008 | Not Challenging | Final | Not Challenging
50599 | 3/31/2008 | Not Challenging | Final | Potentially Challenging
50600 | 12/2/2008 | Not Challenging | Final | Potentially Challenging
50601 | 8/30/2009 | Not Challenging | Final | Not Challenging
50602
50603 | 2/24/2007 | Not Challenging | Final | Undetermined (NC‐PC)
50604 | 11/27/2009 | Not Challenging | Final | Not Challenging
50605 | 10/4/2009 | Not Challenging | Final | Undetermined (NC‐PC)
50606 | 10/8/2001 | Not Challenging | Final | Not Challenging
50607 | 3/1/1997 | Not Evaluated | Preliminary | Potentially Challenging
50608 | 5/28/1997 | Not Evaluated | Preliminary | Potentially Challenging
50609 | 11/23/2000 | Not Evaluated | Preliminary | Potentially Challenging
50610 | 5/30/2005 | Not Evaluated | Preliminary | Potentially Challenging
50611 | 3/19/2008 | Not Evaluated | Preliminary | Potentially Challenging
50612 | 10/21/2002 | Not Challenging | Final | Not Challenging
50613 | 7/3/2003 | Not Evaluated | Preliminary | Potentially Challenging
50614 | 3/9/2004 | Not Evaluated | Preliminary | Potentially Challenging
50615 | 3/11/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50616 | 3/21/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50617 | 3/29/2005 | Not Evaluated | Preliminary | Potentially Challenging
50618 | 9/14/2005 | Not Challenging | Final | Not Challenging
50619 | 2/8/2006 | Not Evaluated | Preliminary | Potentially Challenging
50620 | 3/27/2008 | Not Challenging | Final | Not Challenging
50621 | 9/11/2007 | Not Challenging | Final | Not Challenging
50622 | 11/8/2009 | Not Challenging | Final | Not Challenging
50623 | 12/15/2000 | Not Challenging | Final | Not Challenging
50624 | 5/14/2003 | Not Challenging | Final | Potentially Challenging
50625 | 1/8/2001 | Not Challenging | Final | Undetermined (NC‐PC)
50626
50627 | 3/24/2001 | Not Challenging | Final | Not Challenging
50628 | 3/9/2000 | Not Challenging | Final | Not Challenging
50629 | 10/16/2000 | Not Challenging | Final | Not Challenging
50630 | 10/22/2000 | Not Challenging | Final | Not Challenging
50631 | 10/27/2000 | Not Challenging | Final | Not Challenging
50632 | 10/27/2000 | Not Challenging | Final | Not Challenging
50633 | 11/12/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50634 | 3/6/2002 | Not Challenging | Final | Not Challenging
50635 | 12/12/2000 | Not Challenging | Final | Not Challenging
50636 | 2/10/2001 | Not Challenging | Final | Not Challenging
50637 | 4/18/2001 | Not Challenging | Final | Not Challenging
50638 | 5/14/2001 | Not Challenging | Final | Not Challenging
50639 | 11/10/2001 | Not Challenging | Final | Not Challenging
50640 | 12/23/2001 | Not Challenging | Final | Not Challenging
50641 | 3/4/2002 | Not Challenging | Final | Not Challenging
50642 | 4/16/2002 | Not Challenging | Final | Not Challenging
50643 | 4/18/2002 | Not Challenging | Final | Not Challenging
50644 | 6/24/2002 | Not Challenging | Final | Not Challenging
50645 | 12/23/2002 | Not Challenging | Final | Not Challenging
50646 | 3/7/2003 | Not Challenging | Final | Not Challenging
50647 | 8/12/2003 | Not Challenging | Final | Undetermined (NC‐PC)
50648 | 12/2/2003 | Not Challenging | Final | Not Challenging
50649 | 4/22/2003 | Not Challenging | Final | Not Challenging
50650 | 9/26/2003 | Not Challenging | Final | Potentially Challenging
50651 | 10/17/2003 | Not Challenging | Final | Not Challenging
50652 | 3/18/2004 | Not Challenging | Final | Not Challenging
50653 | 10/4/2005 | Not Challenging | Final | Not Challenging
50654 | 9/24/2007 | Not Challenging | Final | Not Challenging
50655 | 12/4/2007 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50656 | 8/18/2008 | Not Challenging | Final | Not Challenging
50657 | 3/2/2004 | Not Challenging | Final | Not Challenging
50658 | 4/24/2004 | Not Challenging | Final | Not Challenging
50659 | 8/11/2004 | Not Challenging | Final | Not Challenging
50660 | 9/24/2000 | Not Challenging | Final | Not Challenging
50661 | 4/25/2001 | Not Evaluated | Preliminary | Potentially Challenging
50662 | 6/5/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50663 | 8/12/2004 | Not Challenging | Final | Not Challenging
50664 | 6/29/2001 | Not Challenging | Final | Not Challenging
50665 | 9/17/2004 | Not Challenging | Final | Not Challenging
50666 | 3/22/2005 | Not Challenging | Final | Not Challenging
50667 | 3/28/2005 | Not Challenging | Final | Potentially Challenging
50668 | 4/16/2005 | Not Challenging | Final | Not Challenging
50669 | 1/3/2002 | Not Evaluated | Preliminary | Potentially Challenging
50670 | 10/12/2005 | Not Challenging | Final | Not Challenging
50671 | 10/20/2005 | Not Challenging | Final | Not Challenging
50672 | 4/5/2002 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50673 | 4/5/2002 | Not Evaluated | Preliminary | Challenging
50674 | 9/23/2005 | Not Challenging | Final | Not Challenging
50675 | 8/12/2002 | Not Evaluated | Preliminary | Potentially Challenging
50676 | 11/29/2005 | Not Challenging | Final | Not Challenging
50677 | 9/24/2002 | Not Challenging | Final | Not Challenging
50678 | 3/28/2006 | Not Challenging | Final | Not Challenging
50679 | 10/4/2002 | Not Challenging | Final | Not Challenging
50680 | 8/24/2006 | Not Challenging | Final | Not Challenging
50681 | 11/22/2000 | Not Evaluated | Preliminary | Potentially Challenging
50682 | 4/10/2007 | Not Challenging | Final | Not Challenging
50683 | 5/18/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50684 | 3/8/2007 | Not Challenging | Final | Not Challenging
50685 | 3/30/2007 | Not Challenging | Final | Not Challenging
50686 | 4/4/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging
50687 | 7/23/2007 | Not Challenging | Final | Not Challenging
50688 | 5/28/2004 | Not Challenging | Final | Not Challenging
50689 | 10/17/2005 | Not Evaluated | Preliminary | Potentially Challenging
50690 | 10/24/2005 | Not Evaluated | Preliminary | Potentially Challenging
50691 | 2/15/2008 | Not Challenging | Final | Not Challenging
50692 | 3/24/2008 | Not Evaluated | Preliminary | Potentially Challenging
50693 | 10/13/2008 | Not Evaluated | Preliminary | Potentially Challenging
50694 | 10/24/2009 | Not Challenging | Final | Not Challenging
50695
50696 | 4/21/2008 | Not Challenging | Final | Not Challenging
50697 | 7/16/2008 | Not Challenging | Final | Not Challenging
50698 | 3/17/2009 | Not Challenging | Final | Not Challenging
50699 | 4/7/2000 | Not Challenging | Final | Challenging
50700 | 5/13/2000 | Not Challenging | Final | Potentially Challenging
50701 | 5/24/2000 | Not Challenging | Final | Challenging
50702 | 6/25/2000 | Not Challenging | Final | Not Challenging
50703 | 8/22/2000 | Not Challenging | Final | Challenging
50704 | 12/22/2000 | Not Challenging | Final | Not Challenging
50705 | 4/15/2001 | Not Challenging | Final | Potentially Challenging
50706 | 4/17/2001 | Not Challenging | Final | Not Challenging
50707 | 4/25/2001 | Not Challenging | Final | Not Challenging
50708 | 5/17/2001 | Not Challenging | Final | Not Challenging
50709 | 10/26/2001 | Not Challenging | Final | Not Challenging
50710 | 11/19/2001 | Not Challenging | Final | Not Challenging
50711 | 11/20/2001 | Not Challenging | Final | Not Challenging
50712 | 12/14/2001 | Not Challenging | Final | Not Challenging
50713 | 1/1/2002 | Not Challenging | Final | Not Challenging
50714 | 1/9/2002 | Not Challenging | Final | Not Challenging
50715 | 1/16/2002 | Not Challenging | Final | Not Challenging
50716 | 1/24/2002 | Not Challenging | Final | Not Challenging
50717 | 5/21/2002 | Not Challenging | Final | Not Challenging
50718 | 3/20/2003 | Not Challenging | Final | Not Challenging
50719 | 8/1/2003 | Not Challenging | Final | Not Challenging
50720 | 8/4/2003 | Not Challenging | Final | Challenging
50721 | 8/13/2003 | Not Challenging | Final | Not Challenging
50722 | 10/10/2003 | Not Challenging | Final | Not Challenging
50723 | 1/8/2004 | Not Challenging | Final | Not Challenging
50724 | 3/5/2004 | Not Challenging | Final | Not Challenging
50725 | 3/10/2004 | Not Challenging | Final | Not Challenging
50726 | 10/14/2003 | Not Challenging | Final | Not Challenging
50727
50728 | 1/20/2009 | Potentially Challenging | Final | Potentially Challenging
50729 | 4/4/2008 | Not Challenging | Final | Not Challenging
50730 | 3/1/2006 | Not Challenging | Final | Challenging
50731 | 2/11/2005 | Not Challenging | Final | Not Challenging
50732 | 11/7/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging
50733 | 4/23/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging
50734
50735 | 4/9/2007 | Not Challenging | Final | Not Challenging
50736 | 4/10/2007 | Not Challenging | Final | Potentially Challenging
50737
50738 | 3/13/2003 | Not Challenging | Final | Not Challenging
50739 | 3/28/2001 | Not Challenging | Final | Not Challenging
50740 | 5/16/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging
50741 | 9/18/2000 | Not Evaluated | Final | Potentially Challenging
50742 | 10/4/2006 | Not Challenging | Final | Not Challenging
50743 | 7/17/2008 | Not Challenging | Final | Not Challenging
50744 | 8/3/2001 | Potentially Challenging | Final | Potentially Challenging
50745 | 9/22/2009 | Not Challenging | Final | Not Challenging
50746 | 5/6/2001 | Not Challenging | Final | Undetermined (NC‐PC)
50747 | 2/9/2007 | Not Challenging | Final | Not Challenging
50748 | 9/22/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50749 | 10/28/2008 | Challenging | Final | Challenging
50750 | 1/10/2001 | Not Evaluated | Final | Challenging
50751 | 11/17/2008 | Not Challenging | Final | Not Challenging
50752
50753 | 12/11/2009 | Not Challenging | Final | Not Challenging
50754 | 1/23/2009 | Potentially Challenging | Final | Potentially Challenging
50755
50756 | 9/21/2004 | Not Challenging | Final | Not Challenging
50757 | 9/7/2002 | Not Challenging | Final | Not Challenging
50758 | 6/14/2004 | Not Challenging | Final | Potentially Challenging
50759 | 7/29/2006 | Not Challenging | Final | Not Challenging
50760 | 11/8/2006 | Not Challenging | Final | Not Challenging
50761 | 1/25/2008 | Not Challenging | Final | Not Challenging
50762 | 10/1/2001 | Not Challenging | Final | Not Challenging
50763 | 11/14/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC)
50764 | 1/14/2004 | Not Challenging | Final | Undetermined (NC‐PC)
50765 | 10/12/2004 | Not Challenging | Final | Undetermined (NC‐PC)
50766 | 8/18/2000 | Not Challenging | Final | Potentially Challenging
50767 | 6/1/2001 | Not Challenging | Final | Potentially Challenging
50768 | 1/1/2002 | Potentially Challenging | Final | Potentially Challenging
50769 | 12/6/2002 | Not Challenging | Final | Not Challenging
50770 | 1/30/2003 | Not Challenging | Final | Not Challenging
50771 | 5/6/2003 | Potentially Challenging | Final | Potentially Challenging
50772 | 7/2/2003 | Challenging | Final | Challenging
50773 | 9/11/2003 | Not Challenging | Final | Potentially Challenging
50774 | 1/7/2004 | Not Challenging | Final | Not Challenging
50775 | 2/13/2004 | Not Challenging | Final | Potentially Challenging
50776 | 5/6/2004 | Not Challenging | Final | Potentially Challenging
50777 | 8/5/2004 | Not Challenging | Final | Potentially Challenging
50778 | 10/11/2004 | Not Challenging | Final | Not Challenging
50779 | 10/25/2004 | Not Challenging | Final | Potentially Challenging
50780 | 1/6/2005 | Not Challenging | Final | Potentially Challenging
50781 | 3/10/2005 | Not Challenging | Final | Not Challenging
50782 | 3/11/2005 | Not Challenging | Final | Not Challenging
50783 | 6/27/2005 | Not Challenging | Final | Not Challenging
50784 | 11/20/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging
50785 | 12/3/2005 | Not Challenging | Final | Not Challenging
50786 | 3/10/2006 | Not Challenging | Final | Potentially Challenging
50787 | 1/4/2007 | Not Challenging | Final | Potentially Challenging
50788 | 3/8/2007 | Not Challenging | Final | Potentially Challenging
50789 | 3/4/2007 | Not Challenging | Final | Not Challenging
50790 | 6/7/2007 | Not Challenging | Final | Potentially Challenging
50791 | 10/25/2007 | Not Challenging | Final | Potentially Challenging
50792 | 11/6/2007 | Not Challenging | Final | Potentially Challenging
50793 | 11/18/2007 | Not Challenging | Final | Potentially Challenging
50794 | 3/4/2009 | Not Challenging | Final | Potentially Challenging
50795 | 7/12/2009 | Not Challenging | Final | Not Challenging
50796 | 11/4/2009 | Potentially Challenging | Final | Potentially Challenging
50797 | 11/8/2009 | Not Challenging | Final | Potentially Challenging
50798 | 12/1/2009 | Not Challenging | Final | Potentially Challenging
50799 | 12/12/2009 | Not Challenging | Final | Not Challenging
50800
50801
50802
50803 | 12/1/2009 | Not Challenging | Final | Potentially Challenging
50804 | 1/13/2004 | Not Challenging | Final | Not Challenging
50805 | 2/12/2004 | Not Challenging | Final | Not Challenging
50806 | 8/30/2004 | Not Challenging | Final | Not Challenging
50807 | 8/24/2007 | Not Challenging | Final | Not Challenging
50808 | 3/21/2006 | Not Challenging | Final | Potentially Challenging
50809 | 11/9/2000 | Potentially Challenging | Final | Potentially Challenging
50810 | 6/25/2000 | Not Challenging | Final | Undetermined (NC‐PC)
50811 | 1/9/2001 | Potentially Challenging | Final | Potentially Challenging
50812 | 6/11/2001 | Not Challenging | Final | Not Challenging
50813 | 9/3/2002 | Not Challenging | Final | Potentially Challenging
50814 | 5/31/2005 | Not Challenging | Final | Not Challenging
50815 | 5/19/2005 | Not Challenging | Final | Potentially Challenging
50816 | 11/16/2005 | Not Challenging | Final | Not Challenging
50817 | 2/13/2006 | Not Challenging | Final | Not Challenging
50818 | 3/21/2008 | Not Challenging | Final | Potentially Challenging
50819 | 6/13/2008 | Not Challenging | Final | Not Challenging
50820 | 10/23/2008 | Potentially Challenging | Final | Potentially Challenging
50821 | 10/30/2008 | Potentially Challenging | Final | Potentially Challenging
50822 | 11/7/2008 | Not Challenging | Final | Challenging
50823 | 4/9/2009 | Not Challenging | Final | Potentially Challenging
50824 | 9/13/2009 | Not Challenging | Final | Potentially Challenging
50825 | 10/1/2009 | Not Challenging | Final | Potentially Challenging
50826 | 12/9/2009 | Not Challenging | Final | Not Challenging
50827 | 4/27/2002 | Not Challenging | Final | Potentially Challenging
50828 | 10/2/2003 | Not Challenging | Final | Undetermined (NC‐PC)
50829 | 9/11/2004 | Not Challenging | Final | Potentially Challenging
50830
50831
50832
50833 | 9/23/2008 | Potentially Challenging | Final | Potentially Challenging
50834 | 9/24/2008 | Not Challenging | Final | Potentially Challenging
50835 | 10/1/2009 | Not Challenging | Final | Potentially Challenging
50836
50837 | 7/9/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50838 | 11/19/2001 | Not Evaluated | Preliminary | Not Challenging
50839 | 11/26/2001 | Not Evaluated | Preliminary | Potentially Challenging
50840 | 11/28/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50841 | 11/29/2001 | Not Evaluated | Preliminary | Potentially Challenging
50842 | 8/23/2002 | Not Evaluated | Preliminary | Undetermined (NC‐PC)
50843 | 3/22/2003 | Not Evaluated | Preliminary | Potentially Challenging
50844 | 7/24/2003 | Not Evaluated | Preliminary | Not Challenging
50845 | 12/13/2003 | Not Evaluated | Preliminary | Potentially Challenging
50846 | 1/24/2005 | Not Evaluated | Preliminary | Not Challenging
50847 | 1/27/2005 | Not Evaluated | Preliminary | Potentially Challenging
50848 | 1/30/2005 | Not Evaluated | Preliminary | Potentially Challenging
50849 | 3/8/2005 | Not Evaluated | Preliminary | Potentially Challenging
50850 | 4/1/2005 | Not Evaluated | Preliminary | Not Challenging
50851 | 4/27/2005 | Not Evaluated | Preliminary | Potentially Challenging
50852 | 5/25/2005 | Not Evaluated | Preliminary | Potentially Challenging
50853 | 11/28/2005 | Not Evaluated | Preliminary | Not Challenging
50854 | 9/18/2006 | Not Evaluated | Preliminary | Potentially Challenging
50855 | 4/26/2008 | Not Evaluated | Preliminary | Potentially Challenging
50856 | 1/31/2008 | Not Evaluated | Preliminary | Potentially Challenging
50857 | 11/6/2009 | Not Evaluated | Preliminary | Potentially Challenging
50858
50859
50860 | 12/14/2004 | Not Challenging | Final | Undetermined (NC‐PC)
50861 | 12/20/2004 | Not Challenging | Final | Not Challenging
50862 | 2/9/2006 | Not Challenging | Final | Potentially Challenging
50863 | 9/30/2008 | Not Challenging | Final | Not Challenging
50864 | 9/24/2009 | Not Challenging | Final | Not Challenging
50865 | 1/31/2000 | Not Challenging | Final | Not Challenging
50866 | 3/28/2001 | Potentially Challenging | Final | Potentially Challenging
50867 | 10/31/2000 | Not Challenging | Final | Potentially Challenging
50868 | 7/3/2001 | Not Challenging | Final | Potentially Challenging
50869 | 10/25/2001 | Not Challenging | Final | Potentially Challenging
50870 | 1/8/2002 | Not Challenging | Final | Undetermined (NC‐PC)
50871 | 1/24/2002 | Potentially Challenging | Final | Potentially Challenging
50872 | 3/31/2002 | Not Challenging | Final | Potentially Challenging
50873 | 5/9/2002 | Not Challenging | Final | Not Challenging
50874 | 7/12/2002 | Potentially Challenging | Final | Potentially Challenging
50875 | 11/10/2002 | Not Challenging | Final | Not Challenging
50876 | 11/13/2002 | Potentially Challenging | Final | Potentially Challenging
50877
50878 | 11/12/2002 | Potentially Challenging | Final | Undetermined (NC‐PC)
50879 | 11/15/2002 | Not Challenging | Final | Not Challenging
50880 | 11/15/2002 | Not Challenging | Final | Undetermined (NC‐PC)
50881 | 12/31/2002 | Not Challenging | Final | Potentially Challenging
50882 | 1/20/2003 | Not Challenging | Final | Not Challenging
50883 | 4/18/2003 | Not Challenging | Final | Not Challenging
50884 | 2/23/2004 | Undetermined (NC‐PC) | Final | Challenging
50885 | 6/17/2003 | Not Challenging | Final | Potentially Challenging
50886 | 2/27/2004 | Not Challenging | Final | Not Challenging
50887 | 3/7/2004 | Not Challenging | Final | Not Challenging
50888 | 7/16/2004 | Not Challenging | Final | Potentially Challenging
50889 | 3/22/2005 | Not Challenging | Final | Not Challenging
50890 | 4/3/2005 | Not Challenging | Final | Not Challenging
50891 | 4/8/2005 | Not Challenging | Final | Not Challenging
50892 | 4/12/2005 | Not Challenging | Final | Undetermined (NC‐PC)
50893 | 12/2/2005 | Potentially Challenging | Final | Potentially Challenging
50894 | 3/12/2006 | Not Challenging | Final | Potentially Challenging
50895 | 5/13/2007 | Potentially Challenging | Final | Challenging
50896 | 5/13/2007 | Undetermined (NC‐PC) | Final | Not Challenging
50897 | 12/22/2007 | Not Challenging | Final | Potentially Challenging
50898 | 2/29/2008 | Not Challenging | Final | Potentially Challenging
50899 | 10/27/2008 | Challenging | Final | Challenging
50900 | 5/1/2009 | Not Challenging | Final | Not Challenging
50901 | 8/28/2009 | Not Challenging | Final | Not Challenging

## Fire Timeline and Suppression
FireID | Event Date_FTS | Disposition_FTS | Ignition | Discovery | Duration Certainty | Duration | Suppression Time | Detection Method | Detection Performance | Suppression Method | Suppression Agent
1 | 12/12/2006 | Undetermined | 13:22 | 13:22 | Known | 34 | 34 | Failed Equipment Alarm | Unknow | Unknow | Portable
2 | 1/5/1999 | Not Challenging | 13:11 | 13:11 | Known | 14 | 14 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknow | Hose stream or hose reel | Portable
3 | 1/14/1999 | Challenging | 12:56 | 12:56 | Known | 409 | 409 | Other plant personnel (in vicinity or passerby） | Plant area did not have installed detection capability | Hose stream or hose reel | Portable
5 | 5/18/1999 | Not Evaluated | 18:32 | 18:32 | Known | 173 | 173 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
6 | 7/13/1999 | Potentially Challenging | 13:00 |  | Known | 40 | 40 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water
7 | 10/9/1999 | Undetermined (NC‐PC) | 23:25 | 23:25 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
8 | 5/7/2000 | Potentially Challenging | 7:50 | 7:57 | Known | 37 | 37 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknow | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
9 | 1/3/1990 | Undetermined (PC‐CH) | 7:45 |  | Known | 13 | 13 | Unknown | Unknown | Unknown | Portable
11 | 3/15/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
12 | 3/30/1990 | Not Challenging | 3:41 | 3:41 | Known | 3 | 3 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher Other (specify in comments) | Portable: CO2
13 | 4/10/1990 | Potentially Challenging | 5:41 |  | Known | 9 | 9 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2
14 | 5/24/1990 | Potentially Challenging | 3:15 | 3:23 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable
15 | 5/27/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Single Portable fire extinguisher | Portable: CO2
16 | 6/10/1990 | Not Challenging | 13:31 |  | Known | 8624 | 8624 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Other (specify in comments) | Portable
17 | 6/28/1990 | Potentially Challenging | 3:01 | 3:01 | Known | 29 | 29 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
18 | 7/13/1990 | Potentially Challenging | 13:10 | 13:25 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Unknown | Portable
19 | 8/4/1990 | Challenging | 17:09 | 17:09 | Known | 19 | 19 | Unknown | Unknown | Fixed suppression system ‐ deluge (automatic) | Portable
20 | 8/25/1990 | Challenging | 18:02 |  | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
21 | 9/22/1990 | Challenging | 21:51 |  | Known | 29 | 29 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Portable,Other: Water
22 | 12/3/1990 | Challenging | 4:29 |  | Known | 76 | 76 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel Multiple portable fire extinguishers | Portable: Dry Chemical,Other: Water
23 | 12/19/1990 | Undetermined (PC‐CH) | 12:20 |  | Known | 40 | 40 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Single Portable fire extinguisher Other (specify in comments) | Portable: Dry Chemical
24 | 12/22/1990 | Undetermined (PC‐CH) | 7:45 |  | Known | 120 | 120 | Dedicated Fire Watch | Unknown | Unknown | Portable
25 | 1/11/1991 | Undetermined (PC‐CH) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
26 | 2/14/1991 | Challenging | 21:45 | 21:45 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Single Portable fire extinguisher | Portable: Halon，Other: Water
27 | 1/16/1991 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
28 | 1/23/1991 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable
29 | 2/23/1991 | Potentially Challenging | 0:50 | 0:52 | Known | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
30 | 4/29/1991 | Challenging | 18:42 |  | Known | 200 | 200 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression ‐ manually actuated,Fixed suppression system ‐ deluge (automatic),Fuel supply removed,Supervised burn out | Other: Water
31 | 6/15/1991 | Undetermined (NC‐PC) | 23:50 |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
32 | 6/27/1991 | Potentially Challenging | 21:15 | 21:15 | Known | 28 | 28 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable
33 | 8/1/1991 | Potentially Challenging | 19:31 | 19:31 | Known | 183 | 183 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
34 | 8/11/1991 | Potentially Challenging | 8:55 | 8:55 | Known | 11 | 11 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel Multiple portable fire extinguishers | Portable: CO2,Other: Water
35 | 11/2/1991 | Not Challenging |  | 21:39 | Estimated | 46 | 46 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Portable
36 | 11/9/1991 | Not Challenging | 11:22 | 11:22 | Known | 15 | 15 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated, Hose stream or hose reel, Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water
37 | 11/15/1991 | Not Challenging | 9:28 |  | Known | 34 | 34 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
38 | 3/21/1992 | Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
39 | 5/3/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
40 | 5/22/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Other (specify in comments) | Portable
41 | 6/17/1992 | Potentially Challenging | 15:26 | 15:26 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
42 | 7/3/1992 | Potentially Challenging | 10:29 |  | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable
43 | 7/4/1992 | Challenging |  | 1:50 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
44 | 7/13/1992 | Challenging | 19:10 | 19:10 | Estimated | 13 | 13 | Unknown | Unknown | Hose stream or hose reel, Multiple portable fire extinguishers,Other (specify in comments) | Portable: CO2,Other: Water
45 | 7/29/1992 | Potentially Challenging | 4:15 |  | Known | 16 | 16 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2
46 | 8/4/1992 | Potentially Challenging | 5:52 | 5:52 | Known | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
47 | 8/10/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable
48 | 9/4/1992 | Challenging | 2:14 | 2:14 | Known | 27 | 27 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers,Power Supply Removed | Portable: Dry Chemical,Other: Water
49 | 9/15/1992 | Challenging | 2:43 | 2:43 | Known | 77 | 77 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers | Portable: CO2,Other: AFFF foam
50 | 11/24/1992 | Potentially Challenging | 2:18 | 2:18 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
51 | 2/5/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed | Portable
52 | 6/19/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown | Portable
53 | 7/27/1993 | Not Challenging |  |  | Known | 0 | 0 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Other (specify in comments) | Portable
54 | 8/16/1993 | Not Challenging | 15:09 | 15:09 | Known | 1 | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
55 | 10/13/1993 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemica
56 | 10/21/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable
57 | 11/2/1993 | Not Challenging | 13:00 | 13:00 | Known | 14 | 14 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
58 | 12/25/1993 | Challenging | 13:52 | 13:52 | Known | 210 | 210 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified, Multiple portable fire extinguishers | Portable: CO2,Other: Water
59 | 1/29/1994 | Challenging | 6:54 |  | Known | 20 | 20 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
60 | 2/3/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
61 | 4/3/1994 | Challenging | 6:18 | 6:18 | Known | 167 | 167 | ailed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression ‐ manually actuated, Hose stream or hose reel | Other: Water
62 | 6/6/1994 | Not Challenging | 11:41 | 11:41 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention | Portable
63 | 6/15/1994 | Potentially Challenging |  | 1:40 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
64 | 6/1/1994 | Challenging | 14:55 |  | Known | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
65 | 7/2/1994 | Challenging | 11:44 | 11:44 | Known | 31 | 31 | Fire Watch | Unknown | Hose stream or hose reel,Portable manual system (e.g. CO2 cart),Multiple portable fire extinguishers | Portable: Dry Chemical,Other: CO2
66 | 7/11/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
67 | 7/29/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
68 | 8/10/1994 | Undetermined (PC‐CH) | 13:30 |  | Known | 30 | 30 | Fire Watch | Unknown | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water
69 | 8/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
70 | 10/26/1994 | Not Challenging | 14:26 |  | Known | 569 | 569 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable
71 | 3/1/1995 | Undetermined (PC‐CH) |  | 3:35 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
72 | 4/14/1995 | Challenging | 5:10 | 5:10 | Known | 19 | 19 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water
73 | 6/1/1995 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable
74 | 6/10/1995 | Challenging | 8:57 | 8:57 | Known | 136 | 136 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify],Other: Water
75 | 8/22/1995 | Potentially Challenging | 11:25 |  | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
76 | 10/21/1995 | Challenging | 9:38 |  | Known | 30 | 30 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other:AFFF foam
77 | 12/10/1995 | Not Challenging |  |  | Estimated | 13 | 13 | Unknown | Unknown | Unknown | Portable:
78 | 1/24/1996 | Challenging | 6:15 |  | Known | 13 | 13 | Fire Watch | Plant area had installed detection which actuated | Hose stream or hose reel | Portable: Water
79 | 2/5/1996 | Challenging | 15:45 |  | Known | 37 | 37 | Unknown | Unknown | Unknown | Portable:
80 | 2/29/1996 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
81 | 3/25/1996 | Undetermined (NC‐PC) |  | 20:10 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
82 | 3/27/1996 | Potentially Challenging |  | 20:00 | Known | 14 | 14 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off) | Portable:
83 | 4/4/1996 | Potentially Challenging | 17:00 | 17:00 | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable:
84 | 4/19/1996 | Potentially Challenging | 10:19 |  | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
85 | 5/13/1996 | Not Challenging | 18:48 | 18:48 | Known | 13 | 13 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
86 | 6/23/1996 | Challenging | 17:14 |  | Known | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
87 | 8/19/1996 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
88 | 10/5/1996 | Challenging | 13:13 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
89 | 10/15/1996 | Potentially Challenging | 13:15 |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g.open circuit breaker) | Portable:
90 | 10/17/1996 | Challenging | 16:07 |  | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: CO2，Other: Water
91 | 11/19/1996 | Undetermined (NC‐PC) | 14:59 |  | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
92 | 11/22/1996 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable:
93 | 3/4/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
94 | 8/1/1997 | Potentially Challenging |  | 0:02 | Estimated | 18 | 18 | Fire Watch | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: CO2
95 | 10/9/1997 | Potentially Challenging | 23:02 |  | Known | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher，Other (specify in comments | Portable: CO2
96 | 10/28/1997 | Not Challenging | 8:45 | 8:45 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)，Fuel supply removed (simple manual action e.g. valve turn off) | Portable:
97 | 6/10/1998 | Potentially Challenging | 2:00 | 2:10 | Known | 39 | 39 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
98 | 10/8/1998 | Potentially Challenging |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | Portable:
99 | 10/10/1998 | Not Challenging | 13:12 | 13:12 | Known | 18 | 18 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable:
100 | 5/15/2000 | Challenging | 0:25 | 0:25 | Known | 78 | 78 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2，Other: CO2
101 | 9/3/2000 | Undetermined (PC‐CH) | 14:40 | 14:40 | Known | 29 | 29 | Dedicated Fire Watch | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water
102 | 9/4/2000 | Challenging | 11:32 |  | Known | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
103 | 9/22/2000 | Challenging | 3:46 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
104 | 10/14/2000 | Potentially Challenging |  | 18:15 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
105 | 11/10/2000 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
106 | 2/3/2001 | Challenging | 15:14 |  | Known | 156 | 156 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
107 | 3/21/2001 | Potentially Challenging | 22:11 |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
108 | 4/6/2001 | Not Challenging | 0:00 | 0:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
109 | 4/24/2001 | Undetermined (PC‐CH) | 1:48 | 1:48 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection，capability | Hose stream or hose reel | Other: Water
110 | 6/25/2001 | Potentially Challenging | 4:33 |  | Known | 16 | 16 | Unknown | Unknown | Unknown | Portable:
111 | 8/2/2001 | Challenging | 8:23 |  | Known | 22 | 22 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
112 | 8/3/2001 | Undetermined (PC‐CH) | 8:40 | 8:40 | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown | Portable:
113 | 6/12/2002 | Challenging | 13:45 | 13:45 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
114 | 8/21/2002 | Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
115 | 8/22/2002 | Challenging | 16:32 | 16:32 | Known | 18 | 18 | Ultraviolet flame detector | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified，Multiple portable fire extinguishers，Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water，Other: Water
116 | 3/18/2003 | Not Challenging | 20:37 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
117 | 10/9/2002 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable:
118 | 1/15/2003 | Challenging | 20:10 | 20:10 | Known | 35 | 35 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
119 | 3/18/2003 | Not Challenging | 20:37 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
120 | 4/7/2003 | Potentially Challenging | 22:01 |  | Known | 33 | 33 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other (specify in comments) | Portable:
121 | 4/26/2003 | Undetermined (NC‐PC) | 17:46 | 17:46 | Known | 37 | 37 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart)，Single Portable fire extinguisher | Portable:
122 | 4/29/2003 | Challenging | 2:58 |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated，Hose stream or hose reel | Portable: Other [specify]，Other: CO2
123 | 10/16/2003 | Challenging |  |  | Estimated | 23 | 23 | Unknown | Unknown | Hose stream or hose reel，Single Portable fire extinguisher | Portable: Dry Chemical，Other: AFFF foam
124 | 10/28/2003 | Potentially Challenging | 1:30 | 1:30 | Known | 317 | 317 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
125 | 1/6/2004 | Challenging | 12:40 | 12:40 | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
126 | 5/21/2004 | Undetermined (PC‐CH) | 21:09 | 21:09 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown | Portable:
127 | 6/18/2004 | Challenging | 6:40 | 6:40 | Known | 71 | 71 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
128 | 8/31/2004 | Potentially Challenging | 7:15 | 7:15 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
129 | 11/6/2004 | Potentially Challenging | 2:52 |  | Known | 18 | 18 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable:
130 | 12/14/2004 | Potentially Challenging | 11:40 |  | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable:
131 | 1/14/2005 | Undetermined (PC‐CH) | 9:53 | 9:53 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Water
132 | 3/4/2005 | Undetermined (NC‐PC) | 14:47 | 14:47 | Estimated | 64 | 64 | Other plant personnel (in vicinity or passerby) |  | Unknown | Portable:
133 | 5/4/2005 | Potentially Challenging | 14:10 | 14:10 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable:
134 | 6/27/2005 | Challenging | 3:16 |  | Known | 27 | 27 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
135 | 8/25/2005 | Potentially Challenging | 11:25 | 11:25 | Known | 112 | 112 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel，Multiple portable fire extinguishers
136 | 10/25/2005 | Potentially Challenging | 21:40 | 21:40 | Known | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
137 | 10/29/2005 | Challenging | 13:30 | 13:30 | Known | 28 | 28 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
138 | 2/11/2006 | Potentially Challenging | 15:06 |  | Known | 154 | 154 | Other plant personnel (in vicinity or passerby | Unknown | Unknown | Portable:
139 | 2/24/2006 | Potentially Challenging | 8:36 | 8:36 | Known | 153 | 153 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
140 | 3/20/2006 | Undetermined (NC‐PC) |  | 7:56 | Known | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
141 | 5/1/2006 | Undetermined (PC‐CH) | 4:39 | 4:39 | Estimated | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: Dry Chemical
142 | 5/24/2006 | Challenging |  |  | Estimated | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: CO2
143 | 8/15/2006 | Potentially Challenging | 17:59 | 17:59 | Known | 36 | 36 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel
144 | 10/30/2006 | Potentially Challenging | 12:38 | 12:44 | Known | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
145 | 11/11/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
146 | 2/27/2007 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
147 | 4/5/2007 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable: None
148 | 4/6/2007 | Challenging | 11:09 | 11:09 | Known | 12 | 12 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water
149 | 4/8/2007 | Potentially Challenging | 13:30 | 13:30 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher | Portable: CO2
150 | 4/25/2007 | Challenging | 16:33 |  | Known | 28 | 28 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Unknown
151 | 8/1/2007 | Not Challenging | 1:52 | 1:52 | Known | 21 | 21 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Dry Chemical
152 | 10/23/2007 | Potentially Challenging | 22:58 | 22:58 | Known | 6 | 6 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
153 | 8/16/2008 | Challenging | 23:57 |  | Known | 125 | 125 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
154 | 9/20/2008 | Challenging | 20:05 | 20:05 | Known | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: Water
155 | 11/17/2008 | Undetermined (NC‐PC) | 9:11 | 9:11 | Known | 24 | 24 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
156
157 | 2/1/2009 | Challenging | 21:56 | 21:56 | Known | 31 | 31 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water
158 | 6/26/2009 | Potentially Challenging | 19:49 | 19:49 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
159 | 1/16/1990 | Potentially Challenging | 17:24 | 17:30 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown
160 | 2/7/2009 | Challenging | 10:46 | 10:46 | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Hose stream or hose reel | Other: Water
161 | 4/22/2009 | Potentially Challenging | 4:30 | 5:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
162 | 8/5/2009 | Challenging | 7:50 | 7:50 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
163 | 10/12/2009 | Potentially Challenging | 15:51 | 15:51 | Known | 22 | 22 | Fire Watch | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Unknown
164 | 3/28/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
165
166
167
168 | 11/13/2003 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
169 | 11/13/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
170 | 11/21/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
171
172 | 12/7/2003 | Not Challenging |  | 1:50 | Known | 130 | 130 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Multiple portable fire extinguishers
173 | 12/13/2003 | Not Challenging | 23:16 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed
174 | 12/30/2003 | Not Challenging | 18:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
175 | 11/22/2009 | Challenging | 15:41 | 15:41 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers
176 | 12/12/2009 | Potentially Challenging |  |  | Estimated | 23 | 23 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | Other: Water
177
178
179
180
181 | 2/13/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Gas Ionization | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
182
183
184 | 6/27/1997 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify]
185 | 3/23/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
186 | 5/14/1998 | Not Challenging | 14:40 |  | Known | 14 | 14 | Roving Firewatch | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
187 | 8/16/1999 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
188 | 8/24/1999 | Potentially Challenging |  |  | Estimated | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Unknown,Power supply removed (simple manual action e.g. open circuit,breaker)
189 | 10/14/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
190 | 3/18/1998 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
191 | 11/11/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
192 | 5/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
193 | 7/31/1991 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
194 | 5/22/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
195 | 3/21/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
196
197
198
199 | 1/22/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
200 | 2/6/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
201 | 3/8/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
202 | 3/23/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
203 | 4/6/1990 | Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
204 | 4/9/1990 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
205
206 | 6/11/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
207 | 7/15/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
208 | 8/8/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
209 | 8/22/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
210 | 10/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Dry Chemical
211 | 11/2/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
212 | 12/5/1990 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
213
214 | 3/8/1991 | Potentially Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Multiple portable fire extinguishers
215 | 3/11/1991 | Not Challenging |  |  | Unknown | 0 | 0 |  |  | Unknown
216 | 7/12/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
217 | 7/19/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
218 | 9/12/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
219 | 9/27/1991 | Undetermined (PC‐CH) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
220 | 10/20/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
221 | 10/23/1991 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
222 | 2/1/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
223 | 3/3/1992 | Not Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
224 | 3/8/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
225 | 3/23/1992 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
226 | 4/17/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
227 | 6/9/1992 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed
228 | 8/14/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Automatic fixed ‐ actuation not specified | Other: Water
229 | 8/21/1992 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby)
230 | 8/31/1992 | Potentially Challenging |  |  | Estimated | 85 | 85 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Supervised burn out,Fuel supply removed (simple manual action e.g. valve turn off)
231 | 10/22/1992 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
232 | 10/27/1992 | Not Challenging |  |  | Estimated | 46 | 46 | Unknown | Unknown | Unknown
233 | 11/29/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
234 | 12/16/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
235 | 12/30/1992 | Potentially Challenging |  |  | Estimated | 25 | 25 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
236 | 1/6/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
237 | 3/19/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Other: Water
238 | 4/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
239 | 7/14/1993 | Potentially Challenging |  |  | Estimated | 25 | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
240 | 7/19/1993 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel | Other: Water
241 | 11/3/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
242 | 11/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
243 | 12/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
244 | 12/7/1993 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart)
245 | 12/16/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
246 | 1/12/1994 | Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Hose stream or hose reel | Other: Water
247 | 1/12/1994 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable: Other [specify]
248 | 3/5/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
249 | 3/7/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed
250 | 7/19/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated | Other: Water
251 | 10/11/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
252 | 3/18/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Automatic fixed ‐ thermally actuated
253 | 7/6/1995 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
254 | 9/25/1995 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
255 | 11/19/1995 | Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
256 | 7/22/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
257 | 10/22/1997 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
258 | 11/3/1997 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
259 | 12/26/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify]
260 | 2/3/1998 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
261 | 5/11/1998 | Not Challenging | 19:50 | 19:50 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
262 | 2/19/1999 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
263 | 4/25/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
264 | 10/20/2001 | Not Challenging | 11:01 | 11:01 | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
265 | 9/23/2006 | Not Challenging | 9:40 | 9:40 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
266 | 11/9/2006 | Potentially Challenging |  | 11:30 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
267 | 6/1/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
268 | 4/7/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Single Portable fire extinguisher
269 | 12/12/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
270 | 11/18/2005 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
271 | 10/5/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
272 | 4/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
273 | 5/10/2002 | Not Challenging |  |  | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
274 | 5/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Water,Other: Water
275 | 10/14/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Unknown | Portable: Water
276 | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify]
277 | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify]
278 | 1/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
279
280 | 11/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
281
282 | 4/23/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Other: Water
283 | 11/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
284 | 11/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Water
285 | 12/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
286 | 4/20/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
287 | 8/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
288 | 10/10/2006 | Potentially Challenging |  |  | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
289 | 5/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
290 | 8/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | Portable: Water
291
292 | 10/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments)
293 | 10/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
294 | 10/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water
295 | 10/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
296 | 10/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
297 | 11/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
298 | 12/16/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
299 | 3/4/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable: Water
300 | 3/16/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
301
302 | 12/21/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
303 | 3/1/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
304
305 | 6/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments)
306 | 1/24/2002 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
307 | 10/17/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2
308 | 10/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
309 | 10/23/2005 | Not Challenging | 7:30 | 7:30 | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
310 | 11/18/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
311 | 12/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
312 | 10/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
313 | 11/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
314 | 2/10/2000 | Not Challenging |  | 7:58 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
315
316 | 8/17/2000 | Not Challenging | 16:47 | 16:47 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
317 | 9/27/2003 | Not Challenging | 14:18 | 14:18 | Known | 3 | 3 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: None
318 | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Unknown
319 | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
320 | 10/24/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2
321 | 10/31/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
322 | 3/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
323
324 | 1/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
325 | 3/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
326 | 3/25/2005 | Not Challenging | 3:55 | 3:55 | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
327 | 1/1/2006 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
328 | 9/24/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
329 | 9/25/2006 | Not Challenging |  | 16:29 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Air supply cut off (smothered, covered)
330 | 9/27/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
331
332 | 4/15/2007 |  |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
333 | 5/11/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
334
335 | 8/3/2007 | Potentially Challenging | 11:04 |  | Known | 6 | 6 | Ultraviolet flame detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
336
337 | 8/18/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
338 | 7/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments)
339
340 | 8/7/2009 | Not Challenging |  | 22:40 | Known | 22 | 22 | Installed Fire detector ‐ Type not specified | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
341 | 2/18/2008 | Not Challenging | 21:24 | 21:25 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
342 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
343 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
344 | 10/26/2006 | Not Challenging | 13:27 | 13:27 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
345 | 4/25/2005 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical
346 | 3/1/2002 | Potentially Challenging |  | 20:15 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguishe
347
348
349 | 4/5/2007 | Not Challenging |  | 5:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
350 | 7/11/2002 | Potentially Challenging |  | 8:30 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
351 | 9/26/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
352 | 2/28/2003 | Not Challenging |  | 9:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
353 | 1/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
354 | 10/1/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
355 | 3/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
356 | 4/19/2006 | Potentially Challenging |  | 19:15 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker)
357 | 1/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
358 | 5/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
359 | 3/6/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
360 | 7/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
361 | 2/4/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
362 | 4/16/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown
363 | 5/27/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
364 | 10/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
365 | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
366 | 1/25/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
367 | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
368 | 10/24/2006 | Not Challenging | 5:19 | 5:19 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
369
370
371
372 | 9/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Unknown | Power Supply Removed
373 | 10/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
374 | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
375 | 10/16/2009 | Potentially Challenging | 20:52 | 20:52 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
376 | 6/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
377 | 8/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
378 | 6/24/2002 | Not Challenging |  | 12:00 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
379 | 10/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
380 | 10/29/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
381 | 3/6/2005 | Potentially Challenging |  |  | Estimated | 13 | 13 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
382
383
384 | 3/23/2007 | Not Challenging | 0:20 | 0:20 | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
385 | 4/14/2006 | Not Challenging |  | 2:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
386 | 6/3/2008 | Not Challenging |  | 11:01 | Known | 685 | 685 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon
387 | 7/24/2008 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)Fuel supply removed (simple manual action e.g. valve turn off)
388 | 7/25/2005 | Not Challenging |  | 14:22 | Known | 1025 | 1025 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart) | Other: AFFF foam
389 | 10/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: CO2
390 | 10/29/2007 | Not Challenging |  | 7:40 | Known | 462 | 462 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed by maintenance staff (craft activity required) | Portable: CO2
391
392 | 10/30/2002 | Not Challenging | 14:45 | 14:53 | Known | 11 | 11 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel,Single Portable fire extinguisher | Portable: CO2
393 | 10/30/2004 | Not Challenging |  | 5:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: Dry Chemical
394 | 2/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
395
396
397 | 5/2/2000 | Not Challenging |  | 7:30 | Estimated | 13 | 13 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
398 | 7/7/2000 | Not Challenging |  |  | Known | 0 | 0 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Automatic fixed ‐ actuation not specified | Other: Water
399 | 12/24/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
400 | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
401 | 6/13/2001 | Not Challenging |  | 12:32 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
402
403
404 | 6/12/2001 | Not Challenging |  | 5:45 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
405 | 8/13/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
406 | 6/12/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
407 | 12/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
408 | 6/1/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
409 | 9/21/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
410 | 7/25/2005 | Not Challenging |  |  | Known | 533 | 533 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
411 | 3/8/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
412 | 7/15/2009 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
413
414
415
416 | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
417
418 | 10/8/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
419 | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
420 | 6/24/2001 | Undetermined (NC‐PC) |  | 8:05 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Unknown | Portable: Water
421 | 7/1/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
422 | 3/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
423 | 6/23/2003 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
424 | 3/10/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel
425
426 | 9/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
427 | 2/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
428 | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
429 | 3/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
430 | 10/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
431 | 4/3/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
432
433
434
435
436 | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers
437 | 2/3/2001 | Challenging | 15:14 | 15:14 | Known | 177 | 177 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify]
438 | 6/24/2001 | Challenging |  | 11:02 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
439 | 10/2/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
440 | 1/2/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
441 | 11/23/2003 | Not Challenging |  | 15:16 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
442 | 2/4/2004 | Potentially Challenging |  | 7:35 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
443 | 3/3/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
444 | 6/28/2004 | Challenging |  |  | Unknown |  |  |  | Unknown | Multiple portable fire extinguishers | Portable: Halon
445 | 8/30/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
446 | 10/5/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
447 | 10/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
448 | 11/17/2004 | Not Challenging |  | 11:58 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments)
449 | 12/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
450 | 12/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
451 | 12/13/2004 | Not Challenging |  | 19:45 | Unknown | 0 | 0 | Fire Watch | Unknown | Unknown
452 | 12/18/2004 | Not Challenging |  | 11:15 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
453 | 6/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention),Unknown
454 | 6/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
455 | 6/6/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
456 | 7/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
457 | 2/17/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
458 | 5/4/2006 | Not Challenging | 16:00 | 16:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water
459 | 5/10/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
460 | 9/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
461 | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
462 | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Other (specify in comments)
463 | 11/1/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
464 | 12/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
465 | 1/31/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments)
466 | 2/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Hose stream or hose reel | Other: Water
467 | 2/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
468 | 2/20/2007 | Undetermined (NC‐PC) |  | 15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
469 | 3/19/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
470 | 6/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
471 | 7/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
472 | 7/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
473 | 8/4/2007 | Potentially Challenging | 10:03 | 10:04 | Known | 147 | 147 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
474 | 8/21/2007 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
475 | 9/27/2007 | Potentially Challenging |  |  | Estimated | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments)
476 | 12/6/2007 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments)
477 | 2/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
478 | 3/30/2008 | Not Challenging |  | 18:31 | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
479 | 3/17/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
480 | 4/7/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
481 | 6/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
482 | 2/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
483 | 11/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
484 | 11/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
485 | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed
486 | 8/27/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
487 | 1/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
488 | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
489
490
491 | 4/12/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
492 | 10/19/2000 | Undetermined (NC‐PC)
493
494 | 3/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
495 | 3/20/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
496 | 5/19/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Unknown
497 | 8/14/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
498 | 12/19/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
499 | 12/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
500 | 3/12/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  |  |  | Unknown
501 | 1/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
502 | 11/18/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
503 | 5/14/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
504 | 10/9/2002 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
505 | 9/13/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
506 | 9/12/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
507
508 | 3/14/2005 | Not Challenging | 19:17 | 19:17 | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
509 | 1/19/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
510
511 | 7/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed
512 | 7/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Power Supply Removed
513 | 11/18/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
514 | 4/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
515 | 10/5/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
516 | 10/25/2005 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
517 | 3/23/2006 | Undetermined (PC‐CH) | 0:34 | 0:39 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers,Power Supply Removed,Other (specify in comments)
518 | 3/30/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
519 | 5/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
520 | 6/6/2006 | Potentially Challenging | 1:16 | 1:19 | Known | 11 | 11 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
521 | 12/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
522 | 9/19/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
523 | 9/27/2006 | Not Challenging |  |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
524 | 10/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
525
526 | 1/30/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
527 | 11/10/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
528
529 | 11/28/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
530 | 3/5/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
531 | 8/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
532
533 | 1/27/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
534 | 4/10/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
535 | 6/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
536 | 8/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
537 | 10/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
538 | 10/20/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
539 | 10/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
540 | 10/23/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments)
541 | 10/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
542 | 3/4/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None,Other: None
543 | 8/27/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
544 | 12/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
545 | 6/5/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
546 | 10/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
547 | 11/5/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
548 | 11/13/2002 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Self‐extinguished (no plant staff intervention)
549 | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
550 | 2/2/2005 | Undetermined (NC‐PC) | 5:58 | 5:58 | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
551 | 2/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
552 | 7/31/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
553 | 6/24/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
554 | 6/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
555 | 7/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
556 | 10/14/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
557 | 11/2/2005 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
558 | 12/13/2005 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher
559 | 9/12/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
560 | 5/20/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
561 | 1/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown
562 | 10/9/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
563 | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
564 | 3/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
565 | 4/25/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
566 | 7/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
567 | 7/31/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
568 | 1/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
569 | 5/15/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
570 | 6/3/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed
571 | 9/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
572 | 12/23/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
573 | 1/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
574
575 | 5/18/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
576 | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
577 | 9/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
578 | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
579 | 3/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
580 | 1/6/2003 | Not Challenging | 6:30 | 6:30 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
581 | 4/17/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
582 | 9/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
583
584 | 10/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
585 | 12/10/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
586 | 5/5/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
587 | 5/13/2003 | Not Challenging | 0:00 |  | Known | 30 | 30 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
588 | 11/30/2006 | Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
589
590 | 2/20/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
591 | 7/19/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) |  | Single Portable fire extinguisher,Power Supply Removed
592 | 6/11/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Fuel supply removed
593 | 10/16/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
594 | 1/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
595 | 2/13/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
596 | 6/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
597 | 7/22/2000 | Not Challenging | 17:30 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
598 | 10/12/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
599 |  | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
600 | 1/17/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
601 | 10/28/2004 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
602 | 9/29/2006 | Potentially Challenging |  | 22:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
603 | 11/14/2007 | Potentially Challenging | 16:18 | 16:18 | Known | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
604 | 9/8/2000 | Not Challenging |  | 17:40 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
605 | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
606 | 10/31/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
607 | 11/13/2008 | Undetermined (NC‐PC) | 9:50 | 9:52 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
608
609 |  | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10273 | 10/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10274 | 10/21/2000 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed
10275
10276 | 12/15/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10277 | 12/22/2000 | Not Challenging | 17:24 | 18:35 |  |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
10278 | 4/4/2001 | Not Challenging | 8:45 | 8:45 | Known | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
10279 | 4/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
10280 | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10281
10282 | 8/12/2001 |  | 15:00 | 16:30 | Known | 150 | 150 | Thermal detector (e.g., temperature or rate of rise) | Unknown | Other (specify in comments)
10283 | 2/10/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10284 | 3/10/2004 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed
10285 | 4/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10286 | 5/10/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
10287 | 5/19/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10288 | 5/22/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
10289 | 5/28/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments),Fuel supply removed (simple manual action e.g. valve turn off)
10290 | 6/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10291 | 9/18/2004 | Undetermined (PC‐CH) |  | 17:35 | Known | 104 | 104 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel,Multiple portable fire extinguishers | ortable: Dry Chemical,Other: None
10292 | 1/13/2005 | Not Challenging | 10:32 | 10:32 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None
10293 | 8/16/2005 | Undetermined (PC‐CH) | 22:28 | 22:28 | Known | 5 | 5 | Fire Watch | Unknown | Other (specify in comments)
10294 | 10/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10295 | 10/18/2005 | Not Challenging | 22:52 | 22:52 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Single Portable fire extinguisher
10296 | 8/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10297 | 12/14/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10298 | 2/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10299 | 2/19/2009 | Not Challenging |  | 10:21 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10300 | 6/25/2009 | Not Challenging | 10:40 | 10:40 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10301
10302 | 3/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10303 | 5/18/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10304 | 4/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10305 | 10/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10306
10307 | 10/3/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
10308 | 9/19/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
10309 | 4/18/2006 | Not Challenging | 14:25 | 14:25 | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
10310 | 1/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10311 | 1/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10312 | 2/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10313 | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
10314
10315 | 10/18/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10316 | 11/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10317 | 9/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10318 | 10/16/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
10319 | 1/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10320 | 5/25/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
10321 | 6/1/2005 | Not Challenging |  |  | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10322 | 12/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10323 | 12/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10324 | 12/30/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
10325
10326 | 1/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10327 | 6/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10328 | 7/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10329 | 9/22/2008 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown
10330 | 9/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10331 | 3/24/2009 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
10332
10333
10334 | 3/30/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10335
10336 | 10/2/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10337 | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
10338 | 9/13/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
10339 | 8/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10340
10341 | 5/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
10342
10343 | 8/25/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10344 | 10/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10345 | 1/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10346
10347
10348
10349 | 9/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
10350 | 1/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10351
10352 | 12/11/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10353 | 1/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10354 | 7/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
10355 | 4/26/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10356 | 10/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
10357 | 7/1/2005 | Potentially Challenging |  | 16:50 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
10358 | 7/3/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10359 | 11/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
10360 | 10/13/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
10361 | 5/5/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
10362 | 10/28/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
10363 | 11/5/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10364 | 6/30/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
10365 | 8/22/2008 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
10366
10367 | 10/22/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10368 | 6/28/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2
10369 | 10/4/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10370 | 4/11/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10371 | 10/20/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10372 | 10/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10373 | 4/14/2005 | Potentially Challenging |  | 10:58 | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
10374 | 7/11/2003 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10375
10376 | 3/23/2004 | Challenging |  |  | Estimated | 10 | 10 | Unknown |  | Hose stream or hose reel
10377 | 3/10/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
10378 | 3/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10379 | 3/22/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10380 | 9/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
10381 | 10/24/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
10382 | 3/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10383 | 4/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
10384 | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
10385 | 2/12/2002 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Self‐extinguished (no plant staff intervention)
10386 | 3/1/2003 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10387 | 3/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
10388
10389 | 9/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
10390
10391
10392 | 4/5/2004 | Not Challenging |  | 13:30 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10393 | 11/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10394 | 2/22/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10395 | 7/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
10396 | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10397 | 10/12/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
10398
10399 | 1/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10400
10401 | 5/9/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10402 | 6/27/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker),Fuel supply removed (simple manual action e.g. valve turn off)
10403 | 10/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10404 | 12/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10405 | 1/20/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10406 | Unknown | Not Challenging |  | Known | Known | 80 | 80 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Plant area did not have installed detection capability,Power supply removed (simple manual action e.g. open circuit breaker)
10407 | 6/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Potentially Challenging | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Potentially Challenging
10408
10409 | 12/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10410 | 2/13/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Not Challenging,Self‐extinguished (no plant staff intervention)
10411 | 3/8/2008 | Not Challenging |  |  | Unknown |  |  | Not Challenging | Plant area did not have installed detection capability | Not Challenging
10412 | 2/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure
10413 | 5/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10414 | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10415
10416 | 4/1/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10417 | 4/17/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed
10418 | 2/15/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10419 | 4/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10420 | 4/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10421 | 6/20/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10422 | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10423 | 9/3/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
10424 | 10/19/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10425 | 11/6/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: CO2
10426 | 4/29/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
10427 | 5/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10428 | 6/1/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10429 | 9/21/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10430 | 12/21/2000 | Potentially Challenging |  | 22:22 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
10431
10432 | 10/22/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10433 | 12/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10434 | 5/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10435 | 7/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10436 | 8/11/2004 | Not Challenging |  | 10:20 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10437 | 5/9/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10438
10439
10440
10441 | 3/4/2009 | Potentially Challenging |  | 0:00 | Unknown |  |  | Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher
10442 | 3/9/2009 | Potentially Challenging |  | 7:40 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed
10443 | 7/25/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10444 | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power Supply Removed
10445 | 2/7/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10446 | 4/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10447 | 3/9/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10448 | 10/23/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10449 | 5/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10450 | 6/19/2001 | Potentially Challenging | 20:00 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10451 | 6/5/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10452 | 9/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10453 | 11/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10454 | 2/17/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
10455 | 3/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10456 | 7/19/2002 | Potentially Challenging |  | 11:15 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
10457 | 10/22/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10458 | 1/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
10459 | 2/7/2003 | Not Challenging |  | 10:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10460 | 4/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10461 | 3/6/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10462 | 2/5/2004 | Undetermined (NC‐PC) |  | 22:54 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed,Unknown
10463 | 3/1/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10464 | 3/30/2005 | Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression ‐ manually actuated,Single Portable fire extinguisher,Power Supply Removed | Portable: Other [specify],Other: Other [specify]
10465 | 9/30/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10466 | 8/31/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed | Portable: CO2
10467 | 4/7/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10468 | 10/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10469 | 3/23/2006 | Not Challenging |  | 22:23 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
10470 | 5/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10471 | 12/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed，Other (specify in comments)
10472 | 9/25/2007 | Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) |  | Power Supply Removed
10473 | 1/23/2007 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown
10474 | 2/23/2007 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10475 | [7 empty] | Other plant personnel (in vicinity or passerby)
10476 | 4/10/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10477 | 6/7/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments)
10478 | 7/10/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed，Other (specify in comments)
10479 | 7/23/2008 | Not Challenging |  | 9:22 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
10480 | 7/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10481
10482 | 10/22/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10483 | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10484 | 4/16/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10485 | 4/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10486 | 7/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10487 | 9/4/2007 | Not Challenging |  | 8:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10488 | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10489 | 4/6/2008 | Challenging |  | 7:27 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water
10490 | 4/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10491 | 4/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10492 | 9/30/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10493 | 10/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10494
10495
10496 | 5/14/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10497 | 7/31/2009 | Not Challenging |  | 6:50 | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10498 | 9/26/2009 | Not Challenging |  | 20:42 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10499 | 10/16/2009 | Not Challenging |  | 17:46 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10500
10501
10502
10503
10504 | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10505 | 3/16/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
10506
10507 | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10508 | 3/28/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10509 | 4/1/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10510 | 4/10/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10511
10512 | 6/22/2001 | Not Challenging |  | 22:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker)
10513 | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10514 | 8/26/2001 | Potentially Challenging |  | 23:38 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10515 | 9/30/2001 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers
10516 | 11/20/2001 | Potentially Challenging |  | 12:43 | Estimated | 10 | 10 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10517 | 8/5/2002 | Not Challenging |  | 11:46 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10518 | 8/26/2002 | Not Challenging | 22:15 | 22:15 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
10519 | 9/25/2002 | Not Challenging |  | 3:45 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10520 | 11/26/2002 | Not Challenging |  | 14:45 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water
10521 | 9/10/2003 | Not Challenging |  | 2:15 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | Portable: CO2
10522 | 11/2/2003 | Potentially Challenging |  | 23:30 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10523 | 11/9/2003 | Not Challenging |  | 12:30 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10524 | 1/7/2004 | Potentially Challenging |  | 18:27 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10525 | 5/10/2004 | Not Challenging |  | 13:49 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10526 | 5/30/2004 | Not Challenging |  | 23:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10527
10528 | 9/8/2004 | Not Challenging |  | 12:55 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
10529 | 1/25/2006 | Not Challenging |  | 17:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10530 | 3/15/2006 | Not Challenging |  | 14:30 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
10531 | 3/31/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10532 | 6/28/2006 | Not Challenging |  | 12:15 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker)
10533 | 2/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10534 | 3/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10535 | 3/31/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10536 | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
10537 | 2/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
10538 | 4/1/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10539 | 1/19/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
10540 | 2/4/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
10541 | 3/24/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10542 | 7/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10543 | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10544 | 1/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water
10545 | 5/9/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
10546 | 3/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
10547 | 1/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10548 | 6/25/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
10549 | 10/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
10550 | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Single Portable fire extinguisher
10551 | 7/14/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10552 | 7/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10553 | 4/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10554 | 5/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10555 | 5/5/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher
10556 | 5/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
10557 | 1/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10558 | 1/19/2005 | Potentially Challenging | 16:54 | 16:54 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10559 | 3/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10560 | 3/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10561 | 4/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10562 | 5/23/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10563 | 7/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
10564 | 8/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
10565 | 8/15/2005 | Not Challenging |  | 12:30 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
10566 | 9/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10567 | 12/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10568 | 1/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher
10569 | 2/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10570 | 2/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10571 | 3/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
10572 | 4/13/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10573 | 7/5/2006 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10574 | 7/17/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10575 | 7/18/2006 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
10576 | 7/26/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
10577 | 10/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10578
10579 | 4/4/2008 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
10580 | 4/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10581 | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10582 | 12/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers
10583 | 9/1/2006 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
10584 | 7/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
10585 | 4/24/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10586 | 1/19/2000 | Not Challenging |  | 15:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10587 | 8/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fixed suppression ‐ manually actuated | Other: Other [specify]
10588 | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10589 | 2/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
10590 | 10/3/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10591 | 10/8/2002 | Not Challenging |  | 8:15 | Known | 517 | 517 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10592 | 1/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10593 | 7/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10594 | 1/25/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10595 | 2/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10596 | 11/4/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10597
10598 | 1/3/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
10599 | 3/25/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10600 | 2/18/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10601 | 2/16/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
10602 | 2/13/2008 | Not Challenging |  | 2:55 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10603
10604 | 5/14/2001 | Potentially Challenging | 8:22 | 8:22 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
10605 | 1/31/2006 | Potentially Challenging | 15:29 | 15:29 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
10606 | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10607 | 12/27/2004 | Not Challenging |  | 0:02 | Known | 49 | 49 | Installed Fire detector ‐ Type not specified | Hose stream or hose reel,Multiple portable fire extinguishers | Plant area had installed detection which actuated | Portable: Dry Chemical,Other: Water
10608
10609 | 9/7/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments)
10610
10611 | 8/20/2009 | Potentially Challenging |  | 15:49 | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical
10612
10613
10614 | 2/25/2004 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown
10615 | 10/15/2005 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown
10616
10617 | 2/14/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10618 | 2/15/2000 | Undetermined (PC‐CH) | 16:17 | 16:17 | Known | 13 | 13 | Roving Firewatch | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
10619 | 5/24/2000 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
10620 | 8/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10621 | 8/22/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10622 | 6/25/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown
10623 | 8/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10624 | 10/26/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown
10625 | 9/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10626 | 12/11/2002 | Potentially Challenging | 3:05 | 3:05 | Known | 67 | 67 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10627 | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10628 | 12/30/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10629
10630 | 6/6/2007 | Potentially Challenging | 15:36 | 15:36 | Known |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
10631 | 11/28/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10632 | 3/3/2000 | Challenging | 11:45 | 11:45 | Known | 275 | 275 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Halon
10633 | 3/7/2000 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10634
10635
10636 | 9/26/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
10637
10638 | 3/5/2001 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
10639 | 2/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10640
10641 | 3/11/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10642 | 3/14/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water
10643 | 5/22/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10644 | 11/3/2002 | Potentially Challenging |  |  | Known | 7 | 7 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
10645 | 4/11/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
10646 | 7/17/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
10647 | 8/22/2003 | Potentially Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed
10648 | 3/12/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Self‐extinguished (no plant staff intervention)
10649 | 3/15/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
10650 | 3/20/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
10651
10652 | 3/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
10653 | 4/3/2005 | Not Challenging |  | 4:43 | Known | 334 | 334 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10654 | 2/5/2007 | Not Challenging |  | 11:08 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10655
10656 | 2/22/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
10657 | 6/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
10658 | 12/29/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
10659
10660 | 11/6/2009 | Not Challenging |  | 22:20 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
10661
10662
10663
10664 | 10/2/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10665 | 11/3/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
10666 | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
10667 | 4/26/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
10668 | 4/22/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
10669 | 5/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10670 | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10671 | 6/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10672 | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 |  |  | Unknown
10673 | 9/4/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
10674 | 12/5/2002 | Not Challenging | 6:45 | 6:45 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
10675 | 12/31/2002 | Not Challenging |  | 14:15 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
10676 | 3/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
10677 | 4/4/2003 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention)
10678 | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)
10679 | 1/9/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
10680 | 7/10/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10681 | 11/12/2004 | Not Challenging |  | 14:55 | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown
10682 | 4/2/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10683 | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
10684 | 4/6/2005 | Potentially Challenging |  |  | Known | 0 | 0 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10685 | 4/11/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10686 | 4/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10687 | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
10688 | 10/31/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10689 | 1/26/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10690 | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
10691 | 2/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed,Unknown
10692
10693 | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
10694 | 7/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10695 | 7/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown
10696 | 8/30/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10697 | 2/25/2008 | Not Challenging |  | 9:10 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10698 | 4/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10699 | 4/24/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
10700 | 7/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10701 | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10702 | 2/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10703 | 11/21/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10704 | 3/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10705 | 12/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
10706 | 12/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10707 | 8/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10708 | 9/22/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10709 | 2/1/2005 | Not Challenging | 7:20 | 7:20 | Known | 5 | 5 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10710 | 11/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10711 | 1/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10712 | 10/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10713 | 3/25/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10714
10715 | 2/5/2009 | Potentially Challenging |  | 4:30 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
10716 | 7/26/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10717 | 4/12/2003 | Not Challenging |  | 1:35 | Unknown | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10718 | 5/20/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher
10719 | 6/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10720 | 4/8/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
10721 | 8/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10722 | 9/3/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10723 | 10/4/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10724 | 10/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10725 | 10/29/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
10726 | 11/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10727 | 2/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
10728 | 8/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
10729 | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers
10730 | 3/16/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Self‐extinguished (no plant staff intervention) |  | Unknown
10731 | 6/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10732 | 4/22/2002 | Not Challenging |  | 1:35 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
10733 | 4/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10734 | 4/27/2004 | Not Challenging |  | 15:30 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10735 | 4/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
10736 | 12/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
10737 | 11/30/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10738 | 8/22/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10739 | 4/24/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
10740 | 10/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10741 | 9/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
10742 | 4/11/2004 | Not Challenging | 10:00 | 10:00 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin |  | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
10743 | 4/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out
10744 | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10745 | 7/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10746 | 5/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
10747 | 1/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
10748 | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
10749 | 9/10/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
10750 | 2/28/2009 | Not Challenging |  | 5:10 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
10751 | 1/28/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
10752
10753
10754
20264 | 1/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2
20265 | 2/2/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20266 | 2/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Unknown
20267 | 3/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20268 | 4/19/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20269 | 4/30/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
20270 | 6/7/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20271 | 7/9/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20272 | 9/10/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20273 | 9/18/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
20274 | 10/9/1990 | Potentially Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
20275 | 10/11/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
20276 | 10/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
20277 | 11/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20278 | 11/24/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
20279 | 11/28/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
20280 | 12/5/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20281 | 6/24/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
20282 | 9/17/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20283 | 10/3/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20284 | 10/14/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
20285 | 10/25/1991 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
20286 | 1/23/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
20287 | 2/29/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20288 | 3/9/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20289 | 3/16/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20290 | 4/26/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
20291 | 4/28/1992 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
20292 | 6/25/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
20293 | 9/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20294 | 10/5/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20295 | 10/12/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20296 | 10/23/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown
20297 | 11/17/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20298 | 1/11/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
20299 | 3/9/1993 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
20300 | 3/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20301 | 4/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20302 | 7/25/1993 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20303 | 10/14/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify]
20304 | 11/2/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20305 | 11/18/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20306 | 12/30/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20307 | 1/25/1994 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
20308 | 3/9/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20309 | 3/11/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
20310 | 3/26/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20311 | 4/4/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20312 | 7/27/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
20313 | 9/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20314 | 12/19/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20315 | 2/20/1995 | Not Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
20316 | 2/24/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20317 | 4/10/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20318 | 8/9/1995 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Other [specify]
20319 | 8/15/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | Portable: Other [specify]
20320 | 3/21/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20321 | 7/10/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
20322 | 9/13/1996 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
20323 | 1/8/1997 | Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments) | Portable: Other [specify]
20324 | 8/12/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20325 | 1/16/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify
20326 | 10/12/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20327 | 11/2/1998 | Not Challenging | 5:55 | 5:55 | Known | 7 | 7 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
20328 | 5/6/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Other [specify]
20329 | 9/1/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)
20330 | 10/3/1999 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20331 | 11/4/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
20332 | 12/14/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20333 | 1/12/1990 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
20334 | 2/20/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20335 | 4/13/1990 | Not Challenging |  |  | Unknown | 2 | 2 | Fire Watch | Unknown | Unknown
20336 | 2/14/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
20337 | 4/21/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
20338 | 10/11/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Unknown
20339
20340 | 12/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20341 | 3/31/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20342 | 4/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
20343 | 8/13/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Air supply cut off (smothered, covered)
20344 | 2/20/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
20345 | 3/28/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
20346 | 3/30/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
20347 | 4/15/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20348 | 4/16/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
20349 | 4/23/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
20350 | 6/9/1994 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20351 | 6/21/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
20352 | 6/23/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2
20353 | 7/13/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20354 | 10/8/1994 | Not Challenging |  |  | Known |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20355 | 10/31/1994 | Not Challenging | 9:22 | 9:22 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed
20356 | 2/19/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20357 | 5/24/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
20358 | 1/23/1996 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20359 | 3/3/1996 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
20360 | 5/25/1996 | Undetermined (PC‐CH) |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
20361 | 1/7/1997 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
20362 | 3/2/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20363 | 7/27/1997 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed
20364 | 12/4/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
20365 | 1/13/1998 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20366 | 2/6/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
20367 | 2/24/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
20368 | 6/7/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20369 | 6/14/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
20370 | 7/1/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20371 | 9/9/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
20372 | 11/23/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
20373 | 3/16/1999 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention)
20374 | 3/19/1999 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
20375 | 3/29/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
20376 | 7/29/1999 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
20377 | 2/8/2000 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water
20378 | 2/25/2000 | Potentially Challenging | 23:33 | 23:33 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify]
20379 | 6/20/2000 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
20380 | 8/16/2000 | Potentially Challenging | 15:48 | 15:48 | Known | 21 | 21 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
20381 | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Other [specify]
20382 | 10/23/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
20383 | 11/5/2000 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
20384
20385 | 12/27/2000 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
30265 | 8/5/2008 | Not Challenging | 2:26 | 2:26 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
30266 | 1/20/2009 | Potentially Challenging | 19:26 | 19:26 | Known | 5 | 5 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
30267
30268 | 8/9/2000 | Not Challenging | 12:36 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
30269 | 8/14/2002 | Not Challenging | 15:41 |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed
30270 | 3/16/2003 | Potentially Challenging | 11:35 | 11:35 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
30271 | 9/11/2003 | Undetermined (PC‐CH) | 2:46 | 2:46 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
30272 | 7/9/2004 | Not Challenging | 8:30 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Other: Water
30273
30274
30275 | 1/13/2006 | Not Challenging | 8:56 |  | Unknown |  |  | Unknown | Unknown | Power Supply Removed
30276 | 7/24/2006 | Potentially Challenging | 19:10 | 19:10 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
30277 | 12/3/2007 | Potentially Challenging | 16:59 | 16:59 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
30278 | 10/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical,Other: Other [specify]
30279 | 5/12/2002 | Not Challenging | 11:30 |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
30280
30281 | 6/5/2008 | Potentially Challenging | 13:13 |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
30282 | 11/26/2001 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
30283 | 3/20/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
30284 | 3/12/2004 | Not Challenging |  |  | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
30285 | 11/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
30286 | 6/18/2009 | Potentially Challenging | 16:18 |  | Estimated | 2 | 2 | Fire Watch |  | Single Portable fire extinguisher | Portable: Other [specify]
30287 | 10/1/2009 | Potentially Challenging |  |  | Known | 9 | 9 | Fire Watch | Unknown | Single Portable fire extinguisher
30288 | 4/14/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
30289 | 7/8/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Dry Chemical
30290 | 1/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Portable: CO2
30291 | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical
30292 | 6/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
30293 | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
30294 | 11/7/2001 | Not Challenging | 10:30 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
30295 | 3/15/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
30296 | 11/22/2002 | Potentially Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
30297 | 8/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
30298 | 4/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water
30299 | 4/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
30300 | 5/13/2006 | Not Challenging | 13:13 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
40730 | 10/27/2000 | Not Challenging |  | 14:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
40731 | 2/13/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
40732 | 3/8/2001 | Not Challenging |  | 15:50 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments
40733 | 3/14/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
40734 | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
40735 | 4/4/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered | Portable: Other [specify]
40736 | 4/15/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
40737 | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
40738 | 6/5/2002 | Not Challenging |  | 3:00 | Known | 105 | 105 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water
40739 | 7/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed
40740 | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
40741 | 4/16/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
40742 | 7/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
40743 | 10/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
40744 | 3/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
40745 | 10/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
40746 | 8/15/2006 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Other (specify in comments) | Portable: CO2
40747 | 4/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
40748 | 11/28/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
40749 | 6/13/2008 | Not Challenging |  |  | Known | 9 | 9 | Dedicated Fire Watch | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified,Multiple portable fire extinguishers | Portable: CO2,Other: Water
40750 | 11/16/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50356 | 1/11/2000 | Not Challenging |  | 10:30 | Known | 0 | 0 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50357 | 3/21/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | Other: None
50358 | 6/1/2000 | Not Challenging |  | 10:11 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Hose stream or hose reel,Supervised burn out | Other: Water
50359 | 8/24/2000 | Not Challenging |  | 14:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50360 | 12/20/2000 | Not Challenging |  | 3:30 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50361 | 4/11/2001 | Potentially Challenging |  | 18:10 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments),Power supply removed (simple manual action e.g. open circuit breaker)
50362 | 7/16/2001 | Not Challenging |  | 15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50363
50364 | 10/4/2001 | Not Challenging |  | 10:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed | Portable: None
50365 | 3/4/2002 | Not Challenging |  | 2:10 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments)
50366 | 3/8/2002 | Not Challenging |  | 15:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments)
50367 | 3/14/2002 | Not Challenging | 21:30 | 21:30 | Known | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Other (specify in comments)
50368 | 6/6/2002 | Not Challenging | 4:08 | 4:08 | Known | 1 | 1 | Smoke detector | Plant area had installed detection which actuated | Unknown
50369 | 8/14/2002 | Not Challenging |  | 3:50 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50370 | 10/23/2002 | Not Challenging |  | 13:18 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
50371 | 11/1/2002 | Not Challenging |  | 17:12 | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50372 | 5/9/2003 | Not Challenging |  | 0:30 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed,Other (specify in comments)
50373 | 10/7/2003 | Not Challenging |  | 10:36 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention) | Portable: Dry Chemical
50374 | 4/22/2004 | Not Challenging |  | 7:50 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
50375 | 9/30/2004 | Not Challenging |  | 5:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50376 | 3/24/2005 | Not Challenging |  | 8:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
50377 | 7/2/2005 | Not Challenging |  | 10:15 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50378 | 7/27/2005 | Potentially Challenging | 12:53 | 12:55 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
50379 | 2/24/2006 | Not Challenging | 8:05 | 8:05 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
50380 | 8/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50381 | 12/14/2006 | Not Challenging |  | 8:30 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50382 | 1/29/2007 | Not Challenging | 12:10 | 12:10 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50383 | 3/1/2007 | Not Challenging | 2:00 | 2:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50384 | 3/22/2007 | Not Challenging |  | 0:21 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50385 | 5/30/2007 | Not Challenging |  | 11:30 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
50386
50387 | 3/29/2008 | Not Challenging |  | 14:19 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50388 | 6/8/2008 | Not Challenging |  | 0:44 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed
50389 | 6/23/2008 | Not Challenging | 12:25 | 12:25 | Known | 6 | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50390 | 10/1/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Air supply cut off (smothered, covered)
50391 | 7/2/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
50392 | 8/13/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
50393 | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50394 | 4/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50395 | 4/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
50396 | 5/1/2001 | Not Challenging |  | 23:05 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50397 | 1/13/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50398 | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50399 | 2/26/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50400 | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments)
50401 | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50402 | 11/8/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments)
50403 | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Water
50404 | 11/25/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50405 | 3/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50406 | 8/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50407 | 3/11/2008 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50408
50409 | 10/5/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
50410 | 9/29/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
50411 | 7/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50412
50413
50414
50415
50416
50417
50418
50419
50420
50421
50422
50423 | 2/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50424 | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments)
50425 | 3/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Multiple portable fire extinguishers,Other (specify in comments)
50426 | 5/2/2000 | Potentially Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
50427 | 8/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50428 | 9/20/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50429 | 3/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50430 | 2/18/2000 | Not Challenging |  | 6:21 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
50431
50432 | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50433 | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
50434 | 10/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50435 | 7/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50436 | 8/12/2002 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
50437
50438 | 1/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
50439 | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50440 | 10/13/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50441 | 10/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
50442 | 11/8/2004 | Potentially Challenging | 21:23 | 21:23 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50443 | 3/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50444 | 4/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50445 | 4/28/2005 | Not Challenging | 16:00 | 16:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50446 | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50447 | 9/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50448 | 10/11/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments)
50449 | 2/21/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown
50450 | 2/28/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
50451 | 7/15/2006 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50452 | 8/18/2006 | Undetermined (NC‐PC) |  | 13:00 | Known | 4 | 4 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
50453 | 8/22/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50454 | 11/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50455 | 11/30/2006 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50456 | 2/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50457 | 7/28/2007 | Not Challenging | 16:05 | 16:05 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel,Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water
50458 | 8/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50459 | 2/8/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
50460 | 4/16/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments)
50461 | 4/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50462 | 6/12/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments) | Portable: Water
50463 | 4/11/2000 | Not Challenging |  |  | Estimated | 10 | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50464 | 4/26/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
50465
50466 | 2/4/2005 | Not Challenging |  |  | Unknown |  |  |  | Plant area had installed detection which actuated | Unknown
50467 | 2/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50468 | 11/2/2007 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Unknown
50469 | 7/28/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50470 | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention)
50471 | 12/2/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50472 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50473 | 6/26/2000 | Potentially Challenging |  | 15:13 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50474 | 8/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50475 | 10/11/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
50476 | 12/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50477 | 3/18/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
50478 | 3/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50479 | 3/22/2000 | Potentially Challenging |  | 7:15 | Known | 19 | 19 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: Dry Chemical
50480 | 4/7/2000 | Not Challenging | 19:35 | 19:35 | Known | 4 | 4 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50481 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Other (specify in comments)
50482 | 3/8/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
50483 | 3/11/2008 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50484 | 3/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50485
50486 | 4/20/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
50487 | 3/6/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50488 | 5/27/2009 | Not Challenging | 15:55 | 15:55 | Known | 5 | 5 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
50489 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50490 | 9/16/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50491 | 10/16/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50492 | 11/2/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50493
50494 | 2/5/2009 | Not Challenging | 18:28 | 18:28 | Known | 16 | 16 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
50495 | 11/11/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50496 | 1/21/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
50497 | 8/15/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50498
50499 | 4/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50500
50501 | 11/6/2001 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50502 | 10/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50503 | 6/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50504 | 5/20/2002 | Potentially Challenging | 8:54 | 8:54 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50505
50506 | 12/9/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
50507 | 11/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
50508 | 11/26/2005 | Not Challenging | 0:40 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
50509
50510 | 4/19/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
50511 | 5/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: None
50512 | 5/31/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50513 | 8/27/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50514 | 4/29/2009 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
50515 | 11/30/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50516 | 10/5/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50517 | 10/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
50518 | 11/18/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2
50519 | 10/19/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50520 | 12/7/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50521 | 2/1/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50522 | 9/8/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50523 | 9/19/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50524 | 1/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50525 | 12/18/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50526 | 12/7/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50527 | 6/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
50528 | 6/19/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50529 | 3/31/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
50530 | 10/21/2008 | Potentially Challenging |  | 8:56 | Known | 540 | 540 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50531
50532
50533
50534 | 1/7/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
50535 | 1/8/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50536 | 3/21/2002 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50537 | 3/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50538 | 3/27/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Fuel supply removed
50539 | 5/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50540 | 5/25/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
50541 | 4/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
50542 | 7/30/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50543 | 3/27/2001 | Potentially Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
50544
50545 | 9/18/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50546 | 12/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50547 | 4/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
50548 | 6/9/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50549 | 1/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50550 | 6/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50551 | 10/6/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50552 | 3/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50553 | 5/2/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Halon
50554 | 5/19/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50555 | 6/25/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
50556 | 2/25/2005 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50557 | 1/16/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50558 | 1/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
50559
50560
50561
50562 | 5/28/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50563 | 11/16/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50564 | 1/15/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
50565 | 8/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50566 | 9/17/2008 | Not Challenging | 9:30 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50567
50568
50569 | 3/24/2004 | Not Challenging | 1:25 |  | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
50570 | 6/21/2004 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50571 | 7/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
50572 | 10/8/2003 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
50573 | 8/24/2004 | Not Challenging | 8:37 | 8:38 | Known | 31 | 31 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Power Supply Removed，Self‐extinguished (no plant staff intervention)
50574 | 9/16/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50575 | 9/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50576 | 9/17/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical
50577 | 10/23/2004 | Not Challenging | 0:00 |  | Estimated | 0 | 0 | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
50578 | 11/23/2004 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention)
50579 | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
50580 | 10/9/2004 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50581 | 6/24/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
50582 | 8/22/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
50583 | 9/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50584 | 6/27/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50585 | 10/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50586 | 9/28/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
50587 | 2/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50588 | 2/4/2006 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
50589 | 4/15/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
50590 | 5/6/2006 | Not Challenging | 5:50 |  | Known | 5 | 5 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
50591 | 5/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50592 | 7/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50593 | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50594 | 10/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Plant area did not have installed detection capability | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50595 | 10/28/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Plant area did not have installed detection capability | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50596 | 1/5/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50597 | 12/18/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50598 | 3/10/2008 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
50599 | 3/31/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50600 | 12/2/2008 | Not Challenging |  |  | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required)
50601 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50602
50603 | 2/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50604 | 11/27/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50605 | 10/4/2009 | Not Challenging |  | 23:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
50606 | 10/8/2001 | Not Challenging |  | 4:30 | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50607 | 3/1/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50608 | 5/28/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50609 | 11/23/2000 | Not Evaluated |  |  | Estimated | 0 | 0 | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention)
50610 | 5/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50611 | 3/19/2008 | Not Challenging | 13:07 | 13:07 | Known | 1 | 1 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50612 | 10/21/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50613 | 7/3/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50614 | 3/9/2004 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off)
50615 | 3/11/2004 | Not Evaluated |  | 17:30 | Estimated | 0 | 0 | Dedicated Fire Watch | Unknown | Unknown
50616 | 3/21/2004 | Not Evaluated |  | 3:00 | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
50617 | 3/29/2005 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50618 | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed by maintenance staff (craft activity required)
50619 | 2/8/2006 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50620 | 3/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50621 | 9/11/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50622 | 11/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50623 | 12/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50624 | 5/14/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
50625 | 1/8/2001 | Not Challenging |  | 12:03 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
50626
50627 | 3/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
50628 | 3/9/2000 | Not Challenging |  |  | Unknown | 0 | 0 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50629 | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50630 | 10/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50631 | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50632 | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50633 | 11/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50634 | 3/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
50635 | 12/12/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50636 | 2/10/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50637 | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50638 | 5/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50639 | 11/10/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50640 | 12/23/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
50641 | 3/4/2002 | Not Challenging |  | 18:33 | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50642 | 4/16/2002 | Not Challenging | 10:30 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off)
50643 | 4/18/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
50644 | 6/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50645 | 12/23/2002 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
50646 | 3/7/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
50647 | 8/12/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50648 | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50649 | 4/22/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50650 | 9/26/2003 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50651 | 10/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
50652 | 3/18/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50653 | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
50654 | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50655 | 12/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50656 | 8/18/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50657 | 3/2/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50658 | 4/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
50659 | 8/11/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50660 | 9/24/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
50661 | 4/25/2001 | Not Evaluated |  |  | Unknown |  |  | Unknown | Unknown | Unknown | Unknown
50662 | 6/5/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50663 | 8/12/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50664 | 6/29/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50665 | 9/17/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50666 | 3/22/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
50667 | 3/28/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50668 | 4/16/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50669 | 1/3/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50670 | 10/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50671 | 10/20/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Unknown | Supervised burn out
50672 | 4/5/2002 | Not Evaluated |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50673 | 4/5/2002 | Not Evaluated | 9:58 | 9:58 | Known | 14 | 14 | Other plant personnel (Roving watchstander or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical
50674 | 9/23/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50675 | 8/12/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
50676 | 11/29/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
50677 | 9/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50678 | 3/28/2006 | Not Challenging | 2:28 |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50679 | 10/4/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50680 | 8/24/2006 | Not Challenging |  | 11:45 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required)，Other simple: (e.g. blown out, stamped out; specify in comments)
50681 | 11/22/2000 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50682 | 4/10/2007 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50683 | 5/18/2004 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50684 | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50685 | 3/30/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
50686 | 4/4/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
50687 | 7/23/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50688 | 5/28/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
50689 | 10/17/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off)
50690 | 10/24/2005 | Not Evaluated | 16:55 | 16:55 | Known | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
50691 | 2/15/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required)
50692 | 3/24/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
50693 | 10/13/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50694 | 10/24/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50695
50696 | 4/21/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50697 | 7/16/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
50698 | 3/17/2009 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50699 | 4/7/2000 | Not Challenging |  | 14:25 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Water，Other: Water
50700 | 5/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Unknown | Portable: Water
50701 | 5/24/2000 | Not Challenging |  |  | Estimated |  |  | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: AFFF foam
50702 | 6/25/2000 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown
50703 | 8/22/2000 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
50704 | 12/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50705 | 4/15/2001 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Water
50706 | 4/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50707 | 4/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50708 | 5/17/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50709 | 10/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50710 | 11/19/2001 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
50711 | 11/20/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50712 | 12/14/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Other (specify in comments)
50713 | 1/1/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50714 | 1/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50715 | 1/16/2002 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50716 | 1/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50717 | 5/21/2002 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50718 | 3/20/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50719 | 8/1/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50720 | 8/4/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Supervised burn out | Other: Water
50721 | 8/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50722 | 10/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
50723 | 1/8/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
50724 | 3/5/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown
50725 | 3/10/2004 | Not Challenging |  |  | Unknown
50726 | 10/14/2003 | Not Challenging | 3:15 | 3:15 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
50727
50728 | 1/20/2009 | Potentially Challenging | 19:26 | 19:26 | Known | 5 | 5 | Roving Firewatch | Unknown | Single Portable fire extinguisher | Portable: CO2
50729 | 4/4/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50730 | 3/1/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
50731 | 2/11/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50732 | 11/7/2002 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50733 | 4/23/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
50734
50735 | 4/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
50736 | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50737
50738 | 3/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention)
50739 | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50740 | 5/16/2000 | Undetermined (NC‐PC) | 8:16 |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50741 | 9/18/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
50742 | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50743 | 7/17/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50744 | 8/3/2001 | Potentially Challenging | 18:25 |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
50745 | 9/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50746 | 5/6/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
50747 | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
50748 | 9/22/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50749 | 10/28/2008 | Challenging | 20:10 | 20:10 | Known | 40 | 40 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated
50750 | 1/10/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water
50751 | 11/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50752
50753 | 12/11/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50754 | 1/23/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50755
50756 | 9/21/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50757 | 9/7/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50758 | 6/14/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50759 | 7/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50760 | 11/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50761 | 1/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
50762 | 10/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50763 | 11/14/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required)
50764 | 1/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50765 | 10/12/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50766 | 8/18/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
50767 | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50768 | 1/1/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50769 | 12/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed by maintenance staff (craft activity required)
50770 | 1/30/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50771 | 5/6/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50772 | 7/2/2003 | Challenging | 10:35 | 10:35 | Known | 215 | 215 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Hose stream or hose reel，Portable manual system (e.g. CO2 cart)，Multiple portable fire extinguishers，Power supply removed by maintenance staff (craft activity required)，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2，Other: Water
50773 | 9/11/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50774 | 1/7/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
50775 | 2/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50776 | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50777 | 8/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50778 | 10/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50779 | 10/25/2004 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
50780 | 1/6/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50781 | 3/10/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50782 | 3/11/2005 | Not Challenging |  | 10:35 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
50783 | 6/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50784 | 11/20/2005 | Undetermined (NC‐PC) | 1:53 | 1:53 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50785 | 12/3/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50786 | 3/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50787 | 1/4/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Water
50788 | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50789 | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50790 | 6/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50791 | 10/25/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50792 | 11/6/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50793 | 11/18/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50794 | 3/4/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
50795 | 7/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
50796 | 11/4/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50797 | 11/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
50798 | 12/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
50799 | 12/12/2009 | Not Challenging |  |  | Known | 365 | 365 | Other plant personnel (in vicinity or passerby) | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
50800
50801
50802
50803 | 12/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
50804 | 1/13/2004 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50805 | 2/12/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
50806 | 8/30/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50807 | 8/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50808 | 3/21/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
50809 | 11/9/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
50810 | 6/25/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
50811 | 1/9/2001 | Potentially Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
50812 | 6/11/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50813 | 9/3/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50814 | 5/31/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50815 | 5/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out，Power supply removed (simple manual action e.g. open circuit breaker)
50816 | 11/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
50817 | 2/13/2006 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Air supply cut off (smothered, covered)
50818 | 3/21/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
50819 | 6/13/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
50820 | 10/23/2008 | Potentially Challenging | 16:08 | 16:08 | Known | 7 | 7 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required) | Portable: Dry Chemical
50821 | 10/30/2008 | Potentially Challenging | 12:30 | 12:45 | Known | 33 | 33 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
50822 | 11/7/2008 | Not Challenging | 13:04 | 13:04 | Known | 48 | 48 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon
50823 | 4/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
50824 | 9/13/2009 | Not Challenging |  | 16:20 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50825 | 10/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50826 | 12/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
50827 | 4/27/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50828 | 10/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50829 | 9/11/2004 | Not Challenging | 0:10 | 0:10 | Estimated | 45 | 45 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50830
50831
50832
50833 | 9/23/2008 | Potentially Challenging |  | 4:42 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50834 | 9/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
50835 | 10/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Air supply cut off (smothered, covered)
50836
50837 | 7/9/2001 | Not Evaluated | 17:15 | 17:15 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50838 | 11/19/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
50839 | 11/26/2001 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
50840 | 11/28/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50841 | 11/29/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
50842 | 8/23/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
50843 | 3/22/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
50844 | 7/24/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50845 | 12/13/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
50846 | 1/24/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
50847 | 1/27/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
50848 | 1/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50849 | 3/8/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50850 | 4/1/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50851 | 4/27/2005 | Not Evaluated | 9:41 | 9:41 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
50852 | 5/25/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
50853 | 11/28/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50854 | 9/18/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)，Fuel supply removed (simple manual action e.g. valve turn off)
50855 | 4/26/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
50856 | 1/31/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50857 | 11/6/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
50858
50859
50860 | 12/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50861 | 12/20/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50862 | 2/9/2006 | Not Challenging |  |  | Unknown |  |  | Roving Firewatch | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50863 | 9/30/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
50864 | 9/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
50865 | 1/31/2000 | Not Challenging | 10:05 | 10:05 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
50866 | 3/28/2001 | Potentially Challenging |  | 6:40 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown
50867 | 10/31/2000 | Not Challenging | 9:45 | 9:45 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
50868 | 7/3/2001 | Not Challenging |  | 21:15 | Known | 1289 | 1289 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50869 | 10/25/2001 | Not Challenging |  | 16:28 | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers
50870 | 1/8/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown
50871 | 1/24/2002 | Potentially Challenging |  | 17:00 | Estimated | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
50872 | 3/31/2002 | Not Challenging |  | 2:05 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
50873 | 5/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
50874 | 7/12/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
50875 | 11/10/2002 | Not Challenging |  | 17:35 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
50876 | 11/13/2002 | Potentially Challenging |  | 3:00 | Estimated | 25 | 25 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
50877
50878 | 11/12/2002 | Potentially Challenging |  | 11:56 | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
50879 | 11/15/2002 | Not Challenging |  | 4:39 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
50880 | 11/15/2002 | Not Challenging |  | 10:18 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown
50881 | 12/31/2002 | Not Challenging |  | 14:25 | Estimated | 25 | 25 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
50882 | 1/20/2003 | Not Challenging |  | 5:44 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50883 | 4/18/2003 | Not Challenging |  | 2:25 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher，Air supply cut off (smothered, covered) | Portable: Dry Chemical
50884 | 2/23/2004 | Undetermined (NC‐PC) |  | 17:00 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel | Other: Water
50885 | 6/17/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
50886 | 2/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water
50887 | 3/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
50888 | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
50889 | 3/22/2005 | Not Challenging |  | 11:32 | Estimated | 2 | 2 | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
50890 | 4/3/2005 | Not Challenging |  | 2:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50891 | 4/8/2005 | Not Challenging |  | 10:30 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50892 | 4/12/2005 | Not Challenging |  | 12:00 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50893 | 12/2/2005 | Potentially Challenging |  | 0:05 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
50894 | 3/12/2006 | Not Challenging |  | 3:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
50895 | 5/13/2007 | Potentially Challenging |  | 3:13 | Estimated | 45 | 45 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
50896 | 5/13/2007 | Undetermined (NC‐PC) |  | 16:15 | Estimated | 85 | 85 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50897 | 12/22/2007 | Not Challenging |  | 9:30 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
50898 | 2/29/2008 | Not Challenging |  | 4:06 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
50899 | 10/27/2008 | Challenging |  | 2:44 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
50900 | 5/1/2009 | Not Challenging |  | 14:22 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
50901 | 8/28/2009 | Not Challenging |  | 11:33 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)

## Plant Response
FireID | Event Date_PR | Disposition_PR | Mode Prior | Mode After | Power Level Prior | Power Level After | Power Effect | EAL Declaration
1 | 12/12/2006 | Undetermined | Operate | Hot Standby | 25 | 0 | scram | Unusual Event
2 | 1/5/1999 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
3 | 1/14/1999 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
5 | 5/18/1999 | Not Evaluated | Refueling M | Refueling | 0 | 0 | None | Unusual Event
6 | 7/13/1999 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
7 | 10/9/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 96 | Reduced Power
8 | 5/7/2000 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
9 | 1/3/1990 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event
11 | 3/15/1990 | Unusual Event | Operate | Operate | 50 | 50 | None
12 | 3/30/1990 | Not Challenging | Cold Shutdown M | Cold Shutdown | 0 | 0 | None
13 | 4/10/1990 | Potentially Challenging | Unknown | Unknown |  |  | None
14 | 5/24/1990 | Potentially Challenging | Operate | Operate | 70 | 70 | None | Alert
15 | 5/27/1990 | Cold Shutdown | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
16 | 6/10/1990 | Not Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None | Unusual Event
17 | 6/28/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
18 | 7/13/1990 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
19 | 8/4/1990 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
20 | 8/25/1990 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
21 | 9/22/1990 | Challenging | Operate | Hot Standby | 40 | 0 | Scram | Unusual Event
22 | 12/3/1990 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
23 | 12/19/1990 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event
24 | 12/22/1990 | Undetermined (PC‐CH) | Operate | Operate | 90 | 80 | Reduced Power | Unusual Event
25 | 1/11/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 65 | Reduced Power | Unusual Event
26 | 2/14/1991 | Challenging | Refueling | Refueling | 0 | 0 | None
27 | 1/16/1991 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram
28 | 1/23/1991 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
29 | 2/23/1991 | Potentially Challenging | Hot Standby | Hot Standby | 0 | 0 | None | Unusual Event
30 | 4/29/1991 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
31 | 6/15/1991 | Undetermined (NC‐PC) | Operate | Hot Standby | 75 | 0 | Scram | Alert
32 | 6/27/1991 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram
33 | 8/1/1991 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
34 | 8/11/1991 | Potentially Challenging | Operate | Operate | 91 | 87 | Reduced Power | Unusual Event
35 | 11/2/1991 | Not Challenging | Operate | Operate | 0 | 0 | None | Unusual Event
36 | 11/9/1991 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram | Alert
37 | 11/15/1991 | Not Challenging | Hot Standby | Hot Standby | 0 |  | None | Unusual Event
38 | 3/21/1992 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
39 | 5/3/1992 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Alert
40 | 5/22/1992 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Alert
41 | 6/17/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None
42 | 7/3/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
43 | 7/4/1992 | Challenging | Operate | Hot Shutdown | 95 | 0 | Scram | Alert
44 | 7/13/1992 | Challenging | Operate | Operate | 93 | 73 | Reduced Power | Unusual Event
45 | 7/29/1992 | Potentially Challenging | Operate | Operate | 95 | 95 | None | Unusual Event
46 | 8/4/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert
47 | 8/10/1992 | Not Challenging | Operate | Hot Standby | 73 | 0 | Scram
48 | 9/4/1992 | Challenging | Operate | Startup/Hot Sta | 100 | 1 | Turbine Trip | Unusual Event
49 | 9/15/1992 | Challenging | Operate | Hot Standby | 100 | 0 | Scram
50 | 11/24/1992 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
51 | 2/5/1993 | Not Challenging | Operate | Operate | 100 | 46 | Reduced Power | Unusual Event
52 | 6/19/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
53 | 7/27/1993 | Not Challenging | Operate | Operate | 100 | 45 | Reduced Power
54 | 8/16/1993 | Not Challenging | Operate | Operate | 100 | 100 | None | Alert
55 | 10/13/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
56 | 10/21/1993 | Potentially Challenging | Operate | Operate | 40 | 29 | Reduced Power | Unusual Event
57 | 11/2/1993 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
58 | 12/25/1993 | Challenging | Operate | Hot Shutdown | 93 | 0 | Scram | Alert
59 | 1/29/1994 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
60 | 2/3/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None
61 | 4/3/1994 | Challenging | Operate | Hot Standby | 25 | 0 | Scram | Unusual Event
62 | 6/6/1994 | Not Challenging | Operate | Operate | 100 | 100 | None | Alert
63 | 6/15/1994 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
64 | 6/1/1994 | Challenging | Operate | Operate | 100 | 0 | Scram
65 | 7/2/1994 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
66 | 7/11/1994 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
67 | 7/29/1994 | Potentially Challenging | Operate | Operate | 87 | 87 | None | Unusual Event
68 | 8/10/1994 | Undetermined (PC‐CH) | Operate | Operate | 80 | 80 | None | Unusual Event
69 | 8/29/1994 | Undetermined (NC‐PC) | Operate | Hot Shutdown P | 100 | 0 | Scram
70 | 10/26/1994 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram
71 | 3/1/1995 | Undetermined (PC‐CH) | Operate | Operate | 75 | 75 | None | Unusual Event
72 | 4/14/1995 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
73 | 6/1/1995 | Not Challenging | Hot Standby | Hot Standby | 0 | 0 | None | Unusual Event
74 | 6/10/1995 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
75 | 8/22/1995 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
76 | 10/21/1995 | Challenging | Refueling | Refueling | 0 | 0 | LOOP | Unusual Event
77 | 12/10/1995 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
78 | 1/24/1996 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
79 | 2/5/1996 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
80 | 2/29/1996 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
81 | 3/25/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event
82 | 3/27/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
83 | 4/4/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Alert
84 | 4/19/1996 | Potentially Challenging | Operate | Hot Shutdown P | 100 | 0 | Scram
85 | 5/13/1996 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
86 | 6/23/1996 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
87 | 8/19/1996 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert
88 | 10/5/1996 | Challenging | Operate | Operate | 0 | 0 | None | Unusual Event
89 | 10/15/1996 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO
90 | 10/17/1996 | Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None | Unusual Event
91 | 11/19/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event
92 | 11/22/1996 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
93 | 3/4/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
94 | 8/1/1997 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram
95 | 10/9/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert
96 | 10/28/1997 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
97 | 6/10/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
98 | 10/8/1998 | Potentially Challenging | Refueling | Refueling | 0 | 0 | Entered an LCO | Alert
99 | 10/10/1998 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
100 | 5/15/2000 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
101 | 9/3/2000 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None | Unusual Event
102 | 9/4/2000 | Challenging | Operate | Hot Standby | 100 | 0 | Scram
103 | 9/22/2000 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
104 | 10/14/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
105 | 11/10/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
106 | 2/3/2001 | Challenging | Operate | Hot Standby | 39 | 0 | Scram | Unusual Event
107 | 3/21/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert
108 | 4/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
109 | 4/24/2001 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None | Unusual Event
110 | 6/25/2001 | Potentially Challenging | Operate | Operate | 100 | 60 | Reduced Power | Alert
111 | 8/2/2001 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
112 | 8/3/2001 | Undetermined (PC‐CH) | Operate | Hot Standby | 20 | 0 | Scram | Unusual Event
113 | 6/12/2002 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert
114 | 8/21/2002 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Unusual Event
115 | 8/22/2002 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
116 | 10/3/2002 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
117 | 10/9/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event
118 | 1/15/2003 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
119 | 3/18/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Alert
120 | 4/7/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
121 | 4/26/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event
122 | 4/29/2003 | Challenging | Operate | Hot Standby | 60 | 0 | Scram | Unusual Event
123 | 10/16/2003 | Challenging | Operate | Operate | 100 | 65 | Reduced Power | Unusual Event
124 | 10/28/2003 | Potentially Challenging | Operate | Operate | 100 | 0 | Scram
125 | 1/6/2004 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
126 | 5/21/2004 | Undetermined (PC‐CH) | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
127 | 6/18/2004 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
128 | 8/31/2004 | Potentially Challenging | Operate | Hot Standby | 95 | 0 | Scram
129 | 11/6/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
130 | 12/14/2004 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
131 | 1/14/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event
132 | 3/4/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None | Unusual Event
133 | 5/4/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
134 | 6/27/2005 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
135 | 8/25/2005 | Potentially Challenging |  | Hot Standby | 100 | 0 | Scram | Unusual Event
136 | 10/25/2005 | Potentially Challenging |  | Hot Standby | 0 | 0 | None | Unusual Event
137 | 10/29/2005 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
138 | 2/11/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert
139 | 2/24/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
140 | 3/20/2006 | Undetermined (NC‐PC) | Operate | Operate | 82 | 82 | None | Unusual Event
141 | 5/1/2006 | Undetermined (PC‐CH) | Operate | Operate | 100 | 60 | Reduced Power | Unusual Event
142 | 5/24/2006 | Challenging | Operate | Operate | 100 | 56 | Reduced Power | Unusual Event
143 | 8/15/2006 | Potentially Challenging | Operate | Operate | 98 | 98 | Entered an LCO | Unusual Event
144 | 10/30/2006 | Potentially Challenging | Operate | Operate | 67 | 67 | Entered an LCO | Alert
145 | 11/11/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
146 | 2/27/2007 | Undetermined (PC‐CH) | Operate | Operate | 100 | 50 | Reduced Power | Unusual Event
147 | 4/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Alert
148 | 4/6/2007 | Challenging | Operate | Hot Standby | 93 | 0 | Scram | Unusual Event
149 | 4/8/2007 | Potentially Challenging | Operate | Operate | 95 | 65 | Entered an LCO | Alert
150 | 4/25/2007 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
151 | 8/1/2007 | Not Challenging | Operate | Operate | 100 | 91 | Reduced Power | Unusual Event
152 | 10/23/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert
153 | 8/16/2008 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
154 | 9/20/2008 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event
155 | 11/17/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 48 | Reduced Power | Unusual Event
157 | 2/1/2009 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
158 | 6/26/2009 | Potentially Challenging | Operate | Hot Shutdown | 73 | 0 | Scram | Unusual Event
159 | 1/16/1990 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
160 | 2/7/2009 | Challenging | Operate | Hot Standby | 90 | 0 | Scram
161 | 4/22/2009 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
162 | 8/5/2009 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Alert
163 | 10/12/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
164 | 3/28/1990 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event
168 | 11/13/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
169 | 11/13/2003 | Potentially Challenging | Operate | Operate
170 | 11/21/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
172 | 12/7/2003 | Challenging | Operate | Operate | 100 | 100
173 | 12/13/2003 | Not Challenging | Operate | Operate | 100 | 100
174 | 12/30/2003 | Not Challenging | Operate | Operate | 100 | 100
175 | 11/22/2009 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event
176 | 12/12/2009 | Potentially Challenging | Operate | Operate | 100 | 97 |  | Unusual Event
181 | 2/13/1997 | Potentially Challenging | Operate | Operate
184 | 6/27/1997 | Challenging | Operate | Operate | 100 | 100
185 | 3/23/1998 | Not Challenging | Operate | Operate
186 | 5/14/1998 | Not Challenging | Operate | Operate | 0 | 0 | None
187 | 8/16/1999 | Potentially Challenging | Operate | Operate | 100 | 100
188 | 8/24/1999 | Potentially Challenging | Operate | Operate | 100 | 100
189 | 10/14/1996 | Not Challenging | Operate | Operate
190 | 3/18/1998 | Not Challenging | Operate | Operate
191 | 11/11/1998 | Not Challenging | Operate | Operate
192 | 5/15/1999 | Not Challenging | Operate | Operate | 100 | 100 | None
193 | 7/31/1991 | Not Challenging | Operate | Operate | 97 | 97 | None
194 | 5/22/1990 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
195 | 3/21/1992 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
199 | 1/22/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
200 | 2/6/1990 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
201 | 3/8/1990 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
202 | 3/23/1990 | Potentially Challenging | Operate | Operate | 100 | 100 | None
203 | 4/6/1990 | Challenging | Refueling | Refueling | 0 | 0 | None
204 | 4/9/1990 | Not Challenging | Operate | Operate | 100 | 100 | None
206 | 6/11/1990 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
207 | 7/15/1990 | Undetermined (PC‐CH) | Unknown | Unknown |  |  | None
208 | 8/8/1990 | Potentially Challenging | Operate | Operate | 100 | 100 | None
209 | 8/22/1990 | Not Challenging | Operate | Operate | 100 | 100 | None
210 | 10/16/1990 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
211 | 11/2/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
212 | 12/5/1990 | Not Challenging | Operate | Operate | 0 | 0 | None
214 | 3/8/1991 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
215 | 3/11/1991 | Not Challenging | Operate | Operate | 100 | 100
216 | 7/12/1991 | Potentially Challenging | Operate | Operate | 100 | 100 | None
217 | 7/19/1991 | Potentially Challenging | Operate | Operate | 100 | 100 | None
218 | 9/12/1991 | Undetermined (NC‐PC) | Operate | Operate |  |  | None
219 | 9/27/1991 | Undetermined (PC‐CH) | Unknown | Unknown
220 | 10/20/1991 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
221 | 10/23/1991 | Not Challenging | Refueling | Refueling | 0 | 0 | None
222 | 2/1/1992 | Not Challenging | Operate | Operate | 100 | 100 | None
223 | 3/3/1992 | Not Challenging | Operate | Operate | 100 | 100 | None
224 | 3/8/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
225 | 3/23/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None
226 | 4/17/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
227 | 6/9/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None
228 | 8/14/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None
229 | 8/21/1992 | Challenging | Operate | Operate | 100 | 100
230 | 8/31/1992 | Potentially Challenging | Operate | Operate
231 | 10/22/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None
232 | 10/27/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None
233 | 11/29/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None
234 | 12/16/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None
235 | 12/30/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None
236 | 1/6/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
237 | 3/19/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
238 | 4/1/1993 | Potentially Challenging | Operate | Operate | 100 | 100 | None
239 | 7/14/1993 | Potentially Challenging | Operate | Operate | 100 | 100
240 | 7/19/1993 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None
241 | 11/3/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
242 | 11/13/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
243 | 12/1/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
244 | 12/7/1993 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None
245 | 12/16/1993 | Not Challenging | Operate | Operate | 100 | 100 | None
246 | 1/12/1994 | Challenging | Unknown | Unknown |  |  | None
247 | 1/12/1994 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
248 | 3/5/1994 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None
249 | 3/7/1994 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None
250 | 7/19/1994 | Potentially Challenging | Operate | Operate | 0 | 0 | Scram
251 | 10/11/1994 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
252 | 3/18/1995 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
253 | 7/6/1995 | Potentially Challenging | Operate | Operate | 100 | 100 | None
254 | 9/25/1995 | Undetermined (PC‐CH) | Unknown | Unknown |  |  | None
255 | 11/19/1995 | Challenging | Unknown | Unknown
256 | 7/22/1996 | Undetermined (NC‐PC) | Unknown | Unknown |  |  | Scram
257 | 10/22/1997 | Not Challenging | Operate | Operate | 100 | 100 | None
258 | 11/3/1997 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None
259 | 12/26/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None
260 | 2/3/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None
261 | 5/11/1998 | Not Challenging | Operate | Operate | 100 | 100 | None
262 | 2/19/1999 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
263 | 4/25/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None
264 | 10/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0
265 | 9/23/2006 | Not Challenging | Refueling | Refueling | 0 | 0
266 | 11/9/2006 | Potentially Challenging | Operate | Operate | 100 | 100
267 | 6/1/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
268 | 4/7/2000 | Not Challenging | Operate | Operate | 100 | 100
269 | 12/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None
270 | 11/18/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0
271 | 10/5/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
272 | 4/17/2004 | Not Challenging | Refueling | Refueling | 0 | 0
273 | 5/10/2002 | Not Challenging | Operate | Operate | 97 | 97 | None
274 | 5/7/2003 | Not Challenging | Operate | Operate | 100 | 100
275 | 10/14/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
276 | 11/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0
277 | 11/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0
278 | 1/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
280 | 11/19/2005 | Not Challenging | Refueling | Refueling | 0 | 0
282 | 4/23/2001 | Not Challenging | Refueling | Refueling | 0 | 0
283 | 11/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0
284 | 11/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0
285 | 12/9/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
286 | 4/20/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
287 | 8/10/2006 | Not Challenging | Operate | Operate | 100 | 100
288 | 10/10/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0
289 | 5/28/2007 | Not Challenging | Refueling | Refueling | 0 | 0
290 | 8/22/2007 | Not Challenging | Operate | Operate | 100 | 100
292 | 10/8/2007 | Not Challenging | Refueling | Refueling | 0 | 0
293 | 10/14/2007 | Not Challenging | Refueling | Refueling | 0 | 0
294 | 10/13/2007 | Not Challenging | Refueling | Refueling | 0 | 0
295 | 10/22/2007 | Not Challenging | Refueling | Refueling | 0 | 0
296 | 10/30/2007 | Not Challenging | Refueling | Refueling | 0 | 0
297 | 11/30/2007 | Not Challenging | Unknown | Unknown
298 | 12/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0
299 | 3/4/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
300 | 3/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
302 | 12/21/1999 | Not Challenging | Operate | Operate | 100 | 100
303 | 3/1/2000 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
305 | 6/21/2001 | Not Challenging | Operate | Operate | 100 | 100
306 | 1/24/2002 | Not Challenging | Operate | Operate | 100 | 100
307 | 10/17/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
308 | 10/14/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0
309 | 10/23/2005 | Not Challenging | Refueling | Refueling | 0 | 0
310 | 11/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0
311 | 12/1/2005 | Not Challenging | Refueling | Refueling | 0 | 0
312 | 10/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0
313 | 11/9/2008 | Not Challenging | Refueling | Refueling | 0 | 0
314 | 2/10/2000 | Not Challenging | Operate | Operate | 100 | 100
316 | 8/17/2000 | Not Challenging | Operate | Operate | 55 | 55
317 | 9/27/2003 | Not Challenging |  |  | 0 | 0
318 | 10/5/2000 | Not Challenging | Operate | Operate | 100 | 100
319 | 10/5/2000 | Not Challenging | Operate | Operate | 100 | 100
320 | 10/24/2000 | Potentially Challenging | Operate | Operate | 100 | 100
321 | 10/31/2000 | Not Challenging | Operate | Operate | 100 | 100
322 | 3/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
324 | 1/12/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
325 | 3/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
326 | 3/25/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
327 | 1/1/2006 | Not Challenging | Operate | Operate | 100 | 100
328 | 9/24/2006 | Not Challenging | Refueling | Refueling | 0 | 0
329 | 9/25/2006 | Not Challenging | Refueling | Refueling | 0 | 0
330 | 9/27/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
331 | 4/15/2007 | Not Challenging | Operate | Operate | 100 | 100
332 | 5/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100
333 | 5/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100
335 | 8/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None
337 | 8/18/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
338 | 7/25/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
340 | 8/7/2009 | Not Challenging | Operate | Operate
341 | 2/18/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
342 | 11/4/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
343 | 11/4/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
344 | 10/26/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
345 | 4/25/2005 | Not Challenging | Operate | Operate |  |  | None
346 | 3/1/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
349 | 4/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
350 | 7/11/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
351 | 9/26/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
352 | 2/28/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
353 | 1/21/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
354 | 10/1/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
355 | 3/7/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
356 | 4/19/2006 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
357 | 1/10/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
358 | 5/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
359 | 3/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
360 | 7/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
361 | 2/4/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
362 | 4/16/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
363 | 5/27/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
364 | 10/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
365 | 8/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
366 | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
367 | 10/12/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
368 | 10/24/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
372 | 9/8/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
373 | 10/5/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
374 | 10/13/2009 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
375 | 10/16/2009 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
376 | 6/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
377 | 8/27/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
378 | 6/24/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
379 | 10/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
380 | 10/29/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
381 | 3/6/2005 | Potentially Challenging | Operate | Operate | 100 | 0 | None
384 | 3/23/2007 | Not Challenging | Operate | Operate | 100 | 100
385 | 4/14/2006 | Not Challenging | Operate | Operate | 100 | 100
386 | 6/3/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
387 | 7/24/2008 | Not Challenging | Operate | Operate | 100 | 100
388 | 7/25/2005 | Not Challenging | Operate | Operate | 100 | 100
389 | 10/17/2004 | Not Challenging | Operate | Operate | 100 | 100
390 | 10/29/2007 | Not Challenging | Refueling | Refueling | 0 | 0
392 | 10/30/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
393 | 10/30/2004 | Not Challenging | Operate | Operate | 100 | 100
394 | 2/11/2000 | Not Challenging | Operate | Operate | 100 | 100
397 | 5/2/2000 | Not Challenging | Operate | Operate | 100 | 100
398 | 7/7/2000 | Not Challenging | Operate | Operate | 100 | 100
399 | 12/24/2000 | Not Challenging | Operate | Operate | 100 | 100
400 | 3/28/2001 | Not Challenging | Unknown |  |  |  | None
401 | 6/13/2001 | Not Challenging | Operate | Operate | 100 | 100
404 | 6/12/2001 | Not Challenging | Operate | Operate | 100 | 100
405 | 8/13/2001 | Not Challenging | Operate | Operate | 100 | 100
406 | 6/12/2001 | Not Challenging | Operate | Operate | 100 | 100
407 | 12/1/2001 | Not Challenging | Operate | Operate | 100 | 100
408 | 6/1/2002 | Not Challenging | Operate | Operate | 100 | 100
409 | 9/21/2004 | Not Challenging | Operate | Operate | 100 | 100
410 | 7/25/2005 | Not Challenging | Operate | Operate | 100 | 100
411 | 3/8/2001 | Potentially Challenging | Operate | Operate |  |  | None
412 | 7/15/2009 | Not Challenging | Operate | Operate | 100 | 100
416 | 10/11/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
418 | 10/8/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
419 | 4/5/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
420 | 6/24/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
421 | 7/1/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
422 | 3/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100
423 | 6/23/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
424 | 3/10/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
426 | 9/17/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
427 | 2/3/2003 | Not Challenging | Operate | Operate |  |  | None
428 | 9/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
429 | 3/12/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
430 | 10/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
431 | 4/3/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
436 | 11/21/2000 | Not Challenging | Unknown | Unknown | 0 | 0
437 | 2/3/2001 | Challenging | Operate | : Hot Standby | 39 | 0 | Turbine Trip | Unusual Event
438 | 6/24/2001 | Challenging | Operate | Operate | 100 | 100 | None
439 | 10/2/2002 | Not Challenging | Unknown | Unknown | 0 | 0 | None
440 | 1/2/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
441 | 11/23/2003 | Not Challenging | Operate | Operate |  |  | Reduced Power
442 | 2/4/2004 | Potentially Challenging | Operate | Operate | 100 | 100
443 | 3/3/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
444 | 6/28/2004 | Challenging | Operate | Operate | 100 | 100
445 | 8/30/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
446 | 10/5/2004 | Potentially Challenging | Refueling | Refueling |  |  | None
447 | 10/8/2004 | Not Challenging | Operate | Operate | 100 | 100
448 | 11/17/2004 | Not Challenging | Refueling | Refueling
449 | 12/8/2004 | Not Challenging | Unknown | Unknown
450 | 12/13/2004 | Not Challenging | Refueling | Refueling
451 | 12/13/2004 | Not Challenging | Refueling | Refueling |  |  | None
452 | 12/18/2004 | Not Challenging | Operate | Operate | 100 | 100
453 | 6/3/2005 | Not Challenging | Operate | Operate | 100 | 10
454 | 6/4/2005 | Not Challenging | Operate | Operate | 100 | 100
455 | 6/6/2005 | Not Challenging | Operate | Operate | 100 | 100
456 | 7/7/2005 | Not Challenging | Operate | Operate | 100 | 100
457 | 2/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0
458 | 5/4/2006 | Not Challenging | Unknown | Unknown | 0
459 | 5/10/2006 | Potentially Challenging | Refueling | Refueling |  |  | None
460 | 9/7/2006 | 9/7/2006 | Operate | Operate | 100 | 100
461 | 10/12/2006 | Not Challenging | Unknown | Unknown
462 | 10/18/2006 | Not Challenging | Unknown | Unknown
463 | 11/1/2006 | Not Challenging | Refueling | Refueling |  |  | None
464 | 12/8/2006 | Not Challenging | Operate | Operate | 100 | 100
465 | 1/31/2007 | Not Challenging | Unknown | Unknown
466 | 2/2/2007 | Not Challenging | Unknown | Unknown
467 | 2/13/2007 | Not Challenging | Unknown | Unknown
468 | 2/20/2007 | Undetermined (NC‐PC) | Unknown | Unknown
469 | 3/19/2007 | Not Challenging | Operate | Operate | 100 | 100
470 | 6/29/2007 | Not Challenging | Unknown | Unknown
471 | 7/10/2007 | Not Challenging | Operate | Operate | 100 | 100
472 | 7/17/2007 | Not Challenging | Unknown | Unknown
473 | 8/4/2007 | Potentially Challenging | Operate | Operate | 100 | 100
474 | 8/21/2007 | Potentially Challenging | Operate | Operate | 100 | 100
475 | 9/27/2007 | Potentially Challenging | Operate | Operate | 100 | 100
476 | 12/6/2007 | Not Challenging | Refueling | Refueling
477 | 2/23/2008 | Not Challenging | Operate | Operate | 100 | 100
478 | 3/30/2008 | Not Challenging | Operate | Operate | 100 | 100
479 | 3/17/2000 | Not Challenging | Unknown | Unknown
480 | 4/7/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
481 | 6/29/2000 | Not Challenging | Unknown | Unknown
482 | 2/8/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
483 | 11/9/2000 | Not Challenging | Operate | Operate | 100 | 100
484 | 11/8/2001 | Not Challenging | Unknown | Unknown
485 | 9/14/2001 | Not Challenging | Operate | Operate | 100 | 100
486 | 8/27/2001 | Not Challenging | Operate |  | 39
487 | 1/13/2001 | Not Challenging | Operate | Operate | 100 | 100
488 | 10/16/2000 | Not Challenging | Refueling | Refueling |  |  | None
491 | 4/12/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
492 | 10/19/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
494 | 3/8/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
495 | 3/20/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
496 | 5/19/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
497 | 8/14/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
498 | 12/19/2000 | Undetermined (PC‐CH) | Unknown | Unknown
499 | 12/17/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
500 | 3/12/2001 | Undetermined (PC‐CH) | Operate | Hot Standby0 | 0 | 0 | Scram
501 | 1/24/2001 | Not Challenging | Operate | Operate | 100 | 100
502 | 11/18/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
503 | 5/14/2002 | Not Challenging | Operate | Operate | 100 | 100
504 | 10/9/2002 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0
505 | 9/13/2003 | Not Challenging | Operate | Operate | 100 | 100
506 | 9/12/2003 | Not Challenging | Operate | Operate | 100 | 100
508 | 3/14/2005 | Not Challenging | Refueling | Refueling | 0 | 0
509 | 1/19/2005 | Potentially Challenging | Operate | Operate | 100 | 100
511 | 7/16/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
512 | 7/20/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
513 | 11/18/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
514 | 4/27/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
515 | 10/5/2005 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0
516 | 10/25/2005 | Potentially Challenging | Operate | Operate | 0 | 0
517 | 3/23/2006 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
518 | 3/30/2006 | Not Challenging | Operate | Operate | 100 | 100
519 | 5/4/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
520 | 6/6/2006 | : Potentially Challenging | Operate | Operate | 100 | 100
521 | 12/17/2007 | Not Challenging | Operate | Operate | 100 | 100
522 | 9/19/2006 | Not Challenging | Operate | Operate | 100 | 100
523 | 9/27/2006 | Not Challenging | Operate | Operate | 100 | 100
524 | 10/11/2006 | Not Challenging | Refueling | Refueling | 0 | 0
526 | 1/30/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
527 | 11/10/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
529 | 11/28/2008 | Not Challenging | Operate | Operate | 100 | 100
530 | 3/5/2008 | Not Challenging | Operate | Operate | 100 | 100
531 | 8/24/2009 | Not Challenging | Operate | Operate | 100 | 100
533 | 1/27/2000 | Not Challenging | Unknown | Unknown
534 | 4/10/2000 | Not Challenging | Operate | Operate | 100 | 100
535 | 6/16/2000 | Not Challenging | Operate | Operate | 100 | 100
536 | 8/24/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | Reduced Power
537 | 10/13/2000 | Not Challenging | Refueling | Refueling | 0 | 0
538 | 10/20/2000 | Not Challenging | Refueling | Refueling | 0 | 0
539 | 10/23/2000 | Not Challenging | Refueling | Refueling | 0 | 0
540 | 10/23/2000 | Not Challenging | Refueling | Refueling | 0 | 0
541 | 10/24/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
542 | 3/4/2000 | Not Challenging | Operate | Operate | 100 | 100
543 | 8/27/2001 | Not Challenging | Operate | Operate | 100 | 100
544 | 12/13/2001 | Not Challenging | Operate | Operate | 100 | 100
545 | 6/5/2002 | Not Challenging | Operate | Operate | 100 | 100
546 | 10/9/2002 | Not Challenging | Refueling | Refueling | 0 | 0
547 | 11/5/2002 | Not Challenging | Operate | Operate | 100 | 100
548 | 11/13/2002 | Not Challenging | Operate | Operate | 100 | 100
549 | 7/16/2004 | Not Challenging | Operate | Operate | 100 | 100
550 | 2/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
551 | 2/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
552 | 7/31/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
553 | 6/24/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
554 | 6/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
555 | 7/27/2005 | Not Challenging | Operate | Operate | 100 | 100
556 | 10/14/2005 | Not Challenging | Operate | Operate | 100 | 100
557 | 11/2/2005 | Not Challenging | Operate | Operate | 100 | 100
558 | 12/13/2005 | Potentially Challenging | Operate | Operate | 100 | 100
559 | 9/12/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
560 | 5/20/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
561 | 1/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
562 | 10/9/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
563 | 10/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0
564 | 3/13/2007 | Not Challenging | Operate | Operate | 100 | 100
565 | 4/25/2007 | Not Challenging | Operate | Operate | 100 | 100
566 | 7/2/2007 | Not Challenging | Operate | Operate | 100 | 100
567 | 7/31/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
568 | 1/12/2008 | Not Challenging | Operate | Operate | 100 | 100
569 | 5/15/2008 | Not Challenging | Operate | Operate | 100 | 100
570 | 6/3/2008 | Potentially Challenging | Operate | Operate | 100 | 100
571 | 9/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0
572 | 12/23/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
573 | 1/29/2009 | Not Challenging | Operate | Operate | 100 | 100
575 | 5/18/2009 | Not Challenging | Operate | Operate | 100 | 100
576 | 8/31/2009 | Not Challenging | Operate | Operate | 100 | 100
577 | 9/16/2002 | Not Challenging | Operate | Operate | 100 | 100
578 | 11/8/2003 | Not Challenging | Operate | Operate | 100 | 100
579 | 3/23/2004 | Not Challenging | Operate | Operate | 100 | 100
580 | 1/6/2003 | : Not Challenging | Operate | Operate | 100 | 100
581 | 4/17/2002 | Not Challenging | Operate | Operate | 100 | 100
582 | 9/3/2004 | Not Challenging | Operate | Operate | 100 | 100
584 | 10/8/2001 | Not Challenging | Operate | Operate | 100 | 100
585 | 12/10/2002 | Not Challenging | Operate | Operate | 100 | 100
586 | 5/5/2003 | Not Challenging | Operate | Operate | 100 | 100
587 | 5/13/2003 | Not Challenging | Operate | Operate | 100 | 100
588 | 11/30/2006 | Challenging | Operate | Operate | 100 | 100
590 | 2/20/2005 | Not Challenging | Operate | Operate | 100 | 100
591 | 7/19/2006 | Potentially Challenging | Operate | Operate | 100 | 100
592 | 6/11/2009 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
593 | 10/16/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
594 | 1/28/2000 | Not Challenging | Operate | Operate | 100 | 100
595 | 2/13/2000 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
596 | 6/13/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
597 | 7/22/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
598 | 10/12/2000 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0
599 |  | Not Challenging | Unknown | Unknown | 0
600 | 1/17/2004 | Not Challenging | Operate | Operate | 100 | 100
601 | 10/28/2004 | Not Challenging | Operate | Operate | 100 | 100
602 | 9/29/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0
603 | 11/14/2007 | Potentially Challenging | Operate | Operate | 100 | 100
604 | 9/8/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
605 | 9/14/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
606 | 10/31/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0
607 | 11/13/2008 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0
609 |  | Not Challenging | Unknown | Unknown | 0 | 0
10273 | 10/18/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
10274 | 10/21/2000 | Not Challenging | Operate | Operate | 100 | 100
10276 | 12/15/2000 | Not Challenging | Operate | Operate | 100 | 100
10277 | 12/22/2000 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO
10278 | 4/4/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10279 | 4/14/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10280 | 4/17/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10282 | 8/12/2001 | Not Challenging | Operate | Operate | 100 | 100
10283 | 2/10/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10284 | 3/10/2004 | Not Challenging | Operate | Operate | 100 | 100
10285 | 4/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
10286 | 5/10/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10287 | 5/19/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
10288 | 5/22/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10289 | 5/28/2004 | Not Challenging | Refueling | Unknown |  |  | None
10290 | 6/3/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10291 | 9/18/2004 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
10292 | 1/13/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
10293 | 8/16/2005 | Not Challenging | Operate | Operate | 100 | 100
10294 | 10/9/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10295 | 10/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10296 | 8/21/2008 | Not Challenging | Operate | Operate | 100 | 100
10297 | 12/14/2008 | Not Challenging | Unknown | Unknown
10298 | 2/12/2009 | Not Challenging | Operate | Operate | 100 | 100
10299 | 2/19/2009 | Not Challenging | Unknown | Unknown
10300 | 6/25/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
10302 | 3/10/2000 | Not Challenging | Operate | Operate | 100 | 100
10303 | 5/18/2001 | Not Challenging | Operate | Operate | 100 | 100
10304 | 4/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10305 | 10/25/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10307 | 10/3/2003 | Not Challenging | Operate | Operate | 100 | 100
10308 | 9/19/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10309 | 4/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0
10310 | 1/29/2007 | Not Challenging | Operate | Operate | 100 | 100
10311 | 1/9/2008 | Not Challenging | Operate | Operate | 100 | 100
10312 | 2/9/2009 | Not Challenging | Operate | Operate | 100 | 100
10313 | 4/3/2009 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
10315 | 10/18/2002 | Not Challenging | Operate | Operate | 100 | 100
10316 | 11/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0
10317 | 9/23/2004 | Not Challenging | Operate | Operate
10318 | 10/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0
10319 | 1/7/2005 | Not Challenging | Operate | Operate | 100 | 100
10320 | 5/25/2005 | Not Challenging | Operate | Operate
10321 | 6/1/2005 | Not Challenging | Operate | Operate | 100 | 100
10322 | 12/10/2005 | Not Challenging | Operate | Operate | 100 | 100
10323 | 12/11/2005 | Not Challenging | Operate | Operate | 100 | 100
10324 | 12/30/2005 | Not Challenging | Operate | Operate | 100 | 100
10326 | 1/24/2007 | Not Challenging | Operate | Operate | 100 | 100
10327 | 6/21/2007 | Not Challenging | Operate | Operate | 100 | 100
10328 | 7/17/2007 | Not Challenging | Operate | Operate | 100 | 100
10329 | 9/22/2008 | Not Challenging | Operate | Operate | 100 | 100
10330 | : 9/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10331 | 3/24/2009 | Potentially Challenging | Operate | Operate | 100 | 100
10334 | 3/30/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
10336 | 10/2/2000 | Not Challenging | Operate | Operate | 0 | 0 | None
10337 | 10/11/2000 | : Not Challenging | Operate | Operate | 100 | 100 | None
10338 | 9/13/2001 | Undetermined (PC‐CH) | Operate | Operate |  |  | None
10339 | 8/16/2004 | Not Challenging | Operate | Operate | 100 | 100
10341 | 5/21/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10343 | 8/25/2005 | Not Challenging | Operate | Operate | 100 | 100
10344 | 10/1/2005 | Not Challenging | Operate | Operate | 100 | 100
10345 | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100
10349 | 9/24/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10350 | 1/21/2008 | Not Challenging | Operate | Operate | 100 | 100
10352 | 12/11/2008 | Not Challenging | Operate | Operate | 100 | 100
10353 | 1/5/2009 | Not Challenging | Operate | Operate | 100 | 100
10354 | 7/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
10355 | 4/26/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10356 | 10/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100
10357 | 7/1/2005 | Potentially Challenging | Operate | Operate | 100 | 100
10358 | 7/3/2002 | Potentially Challenging | Operate | Operate | 100 | 100
10359 | 11/16/2000 | Potentially Challenging | Operate | Operate | 100 | 100
10360 | 10/13/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
10361 | 5/5/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10362 | 10/28/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10363 | 11/5/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0
10364 | 6/30/2005 | Potentially Challenging | Operate | Operate | 0 | 0 | None
10365 | 8/22/2008 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0
10367 | 10/22/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
10368 | 6/28/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10369 | 10/4/2002 | Potentially Challenging | Operate | Operate | 100 | 100
10370 | 4/11/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10371 | 10/20/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10372 | 10/22/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10373 | 4/14/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10374 | 7/11/2003 | Potentially Challenging | Operate | Operate | 100 | 100
10376 | 3/23/2004 | Challenging | Hot Standby | Hot Standby | 0 | 0
10377 | 3/10/2000 | Not Challenging | Refueling | Refueling | 0 | 0
10378 | 3/18/2000 | Not Challenging | Operate | Operate | 0 | 0
10379 | 3/22/2000 | Not Challenging | Refueling | Refueling | 0 | 0
10380 | 9/23/2000 | Not Challenging | Operate | Operate | 0 | 0
10381 | 10/24/2000 | Not Challenging | Operate | Operate | 0 | 0
10382 | 3/20/2001 | Not Challenging | Operate | Operate | 100 | 100
10383 | 4/3/2001 | Not Challenging | Operate | Operate | 100 | 100
10384 | 6/26/2001 | Not Challenging | Operate | Operate | 100 | 100
10385 | 2/12/2002 | Not Challenging | Unknown | Unknown | 0 | 0
10386 | 3/1/2003 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0
10387 | 3/4/2003 | Not Challenging | Refueling | Refueling | 0 | 0
10389 | 9/8/2003 | Potentially Challenging | Operate | Operate | 0 | 0 | None
10392 | 4/5/2004 | Not Challenging | Operate | Operate | 0 | 0
10393 | 11/7/2004 | Not Challenging | Operate | Operate | 0 | 0 | None
10394 | 2/22/2005 | Potentially Challenging | Operate | Operate | 0 | 0 | None
10395 | 7/13/2005 | Not Challenging | Operate | Operate | 0 | 0
10396 | 7/14/2005 | Not Challenging | Operate | Operate | 0 | 0 | None
10397 | 10/12/2005 | Potentially Challenging | Operate | Operate | 100 | 100
10399 | 1/31/2006 | Not Challenging | Operate | Operate | 100 | 100
10401 | 5/9/2006 | Not Challenging | Operate | Operate | 100 | 100
10402 | 6/27/2006 | Not Challenging | Operate | Operate | 0 | 0
10403 | 10/31/2006 | Not Challenging | Operate | Operate | 0 | 0
10404 | 12/5/2006 | Not Challenging | Operate | Operate | 100 | 100
10405 | 1/20/2007 | Not Challenging | Operate | Operate | 10 | 10
10406 | 5/5/2007 | Not Challenging | Operate | Operate | 0 | 0
10407 | 6/3/2007 | Potentially Challenging | Operate | Operate | 0 | 0
10409 | 12/12/2007 | Not Challenging | Operate | Operate | 0 | 0
10410 | 2/13/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10411 | 3/8/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10412 | 2/17/2009 | Not Challenging | Operate | Operate | 0 | 0
10413 | 5/17/2009 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10414 | 8/31/2009 | Not Challenging | Operate | Operate | 100 | 100
10416 | 4/1/2007 | Not Challenging | Refueling | Refueling | 0 | 0
10417 | 4/17/2007 | Not Challenging | Refueling | Refueling | 0 | 0
10418 | 2/15/2008 | Not Challenging | Operate | Operate | 100 | 100
10419 | 4/12/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10420 | 4/17/2008 | Not Challenging | Operate | Operate | 100 | 100
10421 | 6/20/2008 | Not Challenging | Operate | Operate | 100 | 100
10422 | 8/25/2008 | Not Challenging | Operate | Operate | 100 | 100
10423 | 9/3/2008 | Not Challenging | Operate | Operate | 100 | 100
10424 | 10/19/2009 | Not Challenging | Operate | Operate | 100 | 100
10425 | 11/6/2009 | Not Challenging | Operate | Operate | 100 | 100
10426 | 4/29/2002 | Not Challenging | Operate | Operate | 100 | 100
10427 | 5/3/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10428 | 6/1/2000 | Not Challenging | Operate | Operate | 100 | 100
10429 | 9/21/2002 | Not Challenging | Refueling | Refueling | 0 | 0
10430 | 12/21/2000 | Potentially Challenging | Operate | Operate | 100 | 100
10432 | 10/22/2003 | Not Challenging | Operate | Operate | 100 | 100
10433 | 12/10/2003 | Not Challenging | Operate | Operate | 100 | 100
10434 | 5/7/2004 | Not Challenging | Refueling | Refueling | 0 | 0
10435 | 7/8/2004 | Not Challenging | Operate | Operate | 100 | 100
10436 | 8/11/2004 | Not Challenging | Operate | Operate | 100 | 100
10437 | 5/9/2005 | Not Challenging | Operate | Operate | 100 | 100
10441 | 3/4/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0
10442 | 3/9/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0
10443 | 7/25/2009 | Potentially Challenging | Operate | Operate | 100 | 100
10444 | 10/13/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10445 | 2/7/2000 | Not Challenging | Operate | Operate | 100 | 100
10446 | 4/11/2000 | Not Challenging | Operate | Operate | 100 | 100
10447 | 3/9/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10448 | 10/23/2001 | Not Challenging | Operate | Operate | 100 | 100
10449 | 5/17/2001 | Not Challenging | Operate | Operate | 100 | 100
10450 | 6/19/2001 | Potentially Challenging | Operate | Operate | 100 | 100
10451 | 6/5/2001 | Not Challenging | Operate | Operate | 100 | 100
10452 | 9/17/2001 | Not Challenging | Operate | Operate | 100 | 100
10453 | 11/20/2001 | Not Challenging | Operate | Operate | 100 | 100
10454 | 2/17/2003 | Not Challenging | Operate | Operate | 100 | 100
10455 | 3/22/2002 | Not Challenging | Operate | Operate | 100 | 100
10456 | 7/19/2002 | Potentially Challenging | Operate | Operate | 100 | 100
10457 | 10/22/2002 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0
10458 | 1/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100
10459 | 2/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100
10460 | 4/9/2003 | Not Challenging | Operate | Operate | 0 | 0
10461 | 3/6/2003 | Not Challenging | Operate | Operate | 100 | 100
10462 | 2/5/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10463 | 3/1/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10464 | 3/30/2005 | Challenging | Operate | Operate | 100 | 100
10465 | 9/30/2004 | Not Challenging | Operate | Operate | 100 | 100
10466 | 8/31/2005 | Potentially Challenging | Operate | Operate | 100 | 100
10467 | 4/7/2005 | Not Challenging | Operate | Operate | 100 | 100
10468 | 10/27/2005 | Not Challenging | Operate | Operate | 0 | 0
10469 | 3/23/2006 | Not Challenging | Operate | Operate | 100 | 100
10470 | 5/5/2006 | Not Challenging | 5/5/2006 | 5/5/2006 | 0 | 0
10471 | 12/26/2007 | Not Challenging | Operate | Operate | 100 | 100
10472 | 9/25/2007 | Challenging | Operate | Operate | 100 | 100
10473 | 1/23/2007 | Not Challenging | Operate | Operate | 100 | 100
10474 | 2/23/2007 | Not Challenging | Operate | Operate | 100 | 100
10476 | 4/10/2007 | Potentially Challenging | Operate | Operate | 100 | 100
10477 | 6/7/2007 | Potentially Challenging | Operate | Operate | 100 | 100
10478 | 7/10/2008 | Not Challenging | Operate | Operate | 100 | 100
10479 | 7/23/2008 | Not Challenging | Operate | Operate | 100 | 100
10480 | 7/23/2008 | Not Challenging | Operate | Operate | 100 | 100
10482 | 10/22/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
10483 | 4/10/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
10484 | 4/16/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
10485 | 4/21/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
10486 | 7/28/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
10487 | 9/4/2007 | Not Challenging | Operate | Operate | 100 | 100
10488 | 9/24/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10489 | 4/6/2008 | Challenging | Operate | Operate | 100 | 100 | None
10490 | 4/9/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
10491 | 4/29/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
10492 | 9/30/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10493 | 10/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
10496 | 5/14/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
10497 | 7/31/2009 | Not Challenging | Operate | Operate | 100 | 100
10498 | 9/26/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
10499 | 10/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
10504 | 3/15/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
10505 | 3/16/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10507 | 3/14/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10508 | 3/28/2001 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 | None
10509 | 4/1/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
10510 | : 4/10/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
10512 | 6/22/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
10513 | 8/20/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
10514 | 8/26/2001 | Potentially Challenging | Operate | Operate | 67 | 67 | None
10515 | 9/30/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
10516 | 11/20/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10517 | 8/5/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
10518 | 8/26/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
10519 | 9/25/2002 | Not Challenging | Operate | Operate | 0 | 0 | None
10520 | 11/26/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
10521 | 9/10/2003 | Not Challenging | Operate | Operate | 100 | 100
10522 | 11/2/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None
10523 | 11/9/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
10524 | 1/7/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None
10525 | 5/10/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10526 | 5/30/2004 | Not Challenging | Operate | Operate | 100 | 100
10528 | 9/8/2004 | Not Challenging | Operate | Operate | 0 | 0
10529 | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100
10530 | 3/15/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
10531 | 3/31/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10532 | 6/28/2006 | Not Challenging | Operate | Operate | 100 | 100
10533 | 2/1/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10534 | 3/21/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10535 | 3/31/2002 | Not Challenging | Refueling | Refueling | 0 | 0
10536 | 12/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10537 | 2/17/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10538 | 4/1/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10539 | 1/19/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10540 | 2/4/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10541 | 3/24/2001 | Not Challenging | Operate | Operate | 0 | 0
10542 | 7/9/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10543 | 9/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10544 | 1/17/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10545 | 5/9/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10546 | 3/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10547 | 1/22/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10548 | 6/25/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
10549 | 10/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10550 | 9/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10551 | 7/14/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10552 | 7/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10553 | 4/17/2000 | Not Challenging | Operate | Operate
10554 | 5/3/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10555 | 5/5/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
10556 | 5/11/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10557 | 1/13/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10558 | 1/19/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
10559 | 3/7/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10560 | 3/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10561 | 4/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10562 | 5/23/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10563 | 7/11/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10564 | 8/10/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10565 | 8/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10566 | 9/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10567 | 12/19/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10568 | 1/12/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10569 | 2/8/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10570 | 2/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10571 | 3/5/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10572 | 4/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10573 | 7/5/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10574 | 7/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10575 | 7/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
10576 | 7/26/2006 | Potentially Challenging | Operate | Operate | 100 | 100
10577 | 10/28/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10579 | 4/4/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
10580 | 4/26/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10581 | 11/19/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
10582 | 12/9/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
10583 | 9/1/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10584 | 7/27/2008 | Not Challenging | Operate | Operate | 100 | 100
10585 | 4/24/2003 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
10586 | 1/19/2000 | Not Challenging | Operate | Operate | 100 | 100
10587 | 8/10/2000 | Not Challenging | Operate | Operate | 100 | 100
10588 | 11/21/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
10589 | 2/3/2001 | Not Challenging | Operate | Operate | 100 | 100
10590 | 10/3/2001 | Not Challenging | Operate | Operate | 100 | 100
10591 | 10/8/2002 | Not Challenging | Operate | Operate | 100 | 100
10592 | 1/7/2003 | Not Challenging | Operate | Operate | 100 | 100
10593 | 7/7/2003 | Not Challenging | Unknown | Unknown
10594 | 1/25/2004 | Not Challenging | Operate | Operate | 100 | 100
10595 | 2/11/2004 | Not Challenging | Unknown | Unknown
10596 | 11/4/2004 | Not Challenging | Operate | Operate | 100 | 100
10598 | 1/3/2006 | Not Challenging | Operate | Operate | 100 | 100
10599 | 3/25/2006 | Potentially Challenging | Operate | Operate | 100 | 100
10600 | 2/18/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10601 | 2/16/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10602 | 2/13/2008 | Not Challenging | Refueling | Refueling | 0 | 0
10604 | 5/14/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None
10605 | 1/31/2006 | Potentially Challenging | Operate | Operate | 100 | 100
10606 | 5/6/2004 | Not Challenging | Refueling | Refueling | 0 | 0
10607 | 12/27/2004 | Not Challenging | Operate | Operate | 100 | 100 |  | Unusual Event
10609 | 9/7/2008 | Not Challenging | Operate | Operate | 100 | 100
10611 | 8/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100
10614 | 2/25/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10615 | 10/15/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
10617 | 2/14/2003 | Refueling | Operate | Operate | 100 | 100
10618 | 2/15/2000 | Undetermined (PC‐CH) | Operate | Operate
10619 | 5/24/2000 | Not Challenging | Refueling | Refueling | 0 | 0
10620 | 8/9/2000 | Not Challenging | Operate | Operate
10621 | 8/22/2000 | Not Challenging | Operate | Operate
10622 | 6/25/2001 | Not Challenging | Operate | Operate | 100 | 100
10623 | 8/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10624 | 10/26/2001 | Not Challenging | Operate | Operate
10625 | 9/28/2002 | Not Challenging | Operate | Operate
10626 | 12/11/2002 | Potentially Challenging | Operate | Operate
10627 | 12/12/2002 | Not Challenging | Operate | Operate
10628 | 12/30/2005 | Undetermined (NC‐PC) | Operate | Operate
10630 | 6/6/2007 | Potentially Challenging | Operate | Operate
10631 | 11/28/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10632 | 3/3/2000 | Challenging | Refueling | Refueling | 0 | 0
10633 | 3/7/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
10636 | 9/26/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10638 | 3/5/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
10639 | 2/16/2001 | Not Challenging | Operate | Operate | 100 | 100
10641 | 3/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
10642 | 3/14/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0
10643 | 5/22/2002 | Potentially Challenging | Operate | Operate | 100 | 100
10644 | 11/3/2002 | Potentially Challenging | Operate | Operate | 100 | 100
10645 | 4/11/2003 | Not Challenging | Operate | Operate | 100 | 100
10646 | 7/17/2003 | Potentially Challenging | Operate | Operate | 100 | 100
10647 | 8/22/2003 | Potentially Challenging | Operate | Operate | 100 | 100
10648 | 3/12/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0
10649 | 3/15/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0
10650 | 3/20/2004 | Not Challenging | Refueling | Refueling | 0 | 0
10652 | 3/10/2005 | Not Challenging | Operate | Operate | 100 | 100
10653 | 4/3/2005 | Not Challenging | Operate | Operate | 100 | 100
10654 | 2/5/2007 | Not Challenging | Operate | Operate | 100 | 100
10656 | 2/22/2008 | Not Challenging | Operate | Operate | 100 | 100
10657 | 6/29/2009 | Not Challenging | Operate | Operate | 100 | 100
10658 | 12/29/2009 | Potentially Challenging | Operate | Operate | 100 | 100
10660 | 11/6/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10664 | 10/2/2000 | Undetermined (NC‐PC) | Operate | Operate
10665 | 11/3/2000 | Undetermined (NC‐PC) | Operate | Operate
10666 | 4/18/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10667 | 4/26/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10668 | 4/22/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10669 | 5/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0
10670 | 6/1/2001 | Not Challenging | Operate | Operate | 100 | 100
10671 | 6/21/2001 | Not Challenging | Operate | Operate | 100 | 100
10672 | 6/26/2001 | Not Challenging | Operate | Operate | 100 | 100
10673 | 9/4/2001 | Not Challenging | Operate | Operate | 100 | 100
10674 | 12/5/2002 | Not Challenging | Operate | Operate | 100 | 100
10675 | 12/31/2002 | Not Challenging | Operate | Operate | 100 | 100
10676 | 3/29/2003 | Not Challenging | Refueling | Refueling | 0 | 0
10677 | 4/4/2003 | Not Challenging | Refueling | Refueling | 0 | 0
10678 | 5/29/2003 | Not Challenging | Operate | Operate
10679 | 1/9/2004 | Not Challenging | Operate | Operate
10680 | 7/10/2004 | Not Challenging | Operate | Operate
10681 | 11/12/2004 | Not Challenging | Operate | Operate
10682 | 4/2/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10683 | 4/5/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10684 | 4/6/2005 | Potentially Challenging | Operate | Operate
10685 | 4/11/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10686 | 4/13/2005 | Not Challenging | Refueling | Refueling | 0 | 0
10687 | 5/4/2005 | Not Challenging | Operate | Operate | 100 | 100
10688 | 10/31/2006 | Not Challenging | Operate | Operate | 100 | 100
10689 | 1/26/2007 | Not Challenging | Operate | Operate | 100 | 100
10690 | 2/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0
10691 | 2/25/2007 | Not Challenging | Refueling | Refueling | 0 | 0
10693 | 3/4/2007 | Not Challenging | Refueling | Refueling | 0 | 0
10694 | 7/10/2007 | Not Challenging | Operate | Operate | 100 | 100
10695 | 7/27/2007 | Not Challenging | Operate | Operate
10696 | 8/30/2007 | Not Challenging | Operate | Operate | 100 | 100
10697 | 2/25/2008 | Not Challenging | Operate | Operate | 100 | 100
10698 | 4/18/2008 | Not Challenging | Operate | Operate | 100 | 100
10699 | 4/24/2008 | Potentially Challenging | Operate | Operate | 100 | 100
10700 | 7/18/2008 | Not Challenging | Operate | Operate | 100 | 100
10701 | 8/25/2008 | Not Challenging | Operate | Operate | 100 | 100
10702 | 2/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10703 | 11/21/2009 | Not Challenging | Operate | Operate | 100 | 100
10704 | 3/28/2002 | Not Challenging | Operate | Operate | 100 | 100
10705 | 12/3/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
10706 | 12/4/2003 | Not Challenging | Unknown | Unknown
10707 | 8/8/2004 | Not Challenging | Operate | Operate
10708 | 9/22/2004 | Undetermined (NC‐PC) | Operate | Operate
10709 | 2/1/2005 | Not Challenging | Operate | Operate | 100 | 100
10710 | 11/21/2005 | Not Challenging | Operate | Operate
10711 | 1/8/2006 | Not Challenging | Operate | Operate
10712 | 10/8/2006 | Not Challenging | Operate | Operate | 100 | 100
10713 | 3/25/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
10715 | 2/5/2009 | Potentially Challenging | Refueling | Refueling
10716 | 7/26/2009 | Not Challenging | Operate | Operate | 100 | 100
10717 | 4/12/2003 | Not Challenging | Refueling | Refueling | 0 | 0
10718 | 5/20/2004 | Not Challenging | Operate | Operate
10719 | 6/1/2005 | Not Challenging | Operate | Operate | 100 | 100
10720 | 4/8/2006 | Undetermined (NC‐PC) | Operate | Operate
10721 | 8/26/2007 | Not Challenging | Operate | Operate
10722 | 9/3/2007 | Not Challenging | Operate | Operate
10723 | 10/4/2007 | Potentially Challenging | Operate | Operate
10724 | 10/7/2007 | Not Challenging | Operate | Operate
10725 | 10/29/2007 | Not Challenging | Operate | Operate | 100 | 100
10726 | 11/4/2007 | Not Challenging | Operate | Operate | 100 | 100
10727 | 2/5/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10728 | 8/23/2009 | Not Challenging | Operate | Operate | 0 | 0
10729 | 4/3/2009 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0
10730 | 3/16/2006 | Not Challenging | Operate | Operate | 100 | 100
10731 | 6/27/2008 | Not Challenging | Operate | Operate | 100 | 100
10732 | 4/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0
10733 | 4/7/2003 | Not Challenging | Refueling | Refueling | 0 | 0
10734 | 4/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0
10735 | 4/28/2006 | Not Challenging | Operate | Operate | 100 | 100
10736 | 12/6/2004 | Not Challenging | Operate | Operate | 100 | 100
10737 | 11/30/2006 | Not Challenging | Operate | Operate
10738 | 8/22/2001 | Not Challenging | Operate | Operate | 100 | 100
10739 | 4/24/2008 | Not Challenging | Operate | Operate | 100 | 100
10740 | 10/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10741 | 9/21/2007 | Not Challenging | Operate | Operate | 100 | 100
10742 | 4/11/2004 | Not Challenging | Unknown | Unknown
10743 | 4/19/2001 | Not Challenging | Operate | Operate | 100 | 100
10744 | 8/17/2001 | Not Challenging | Operate | Operate | 100 | 100
10745 | 7/25/2006 | Not Challenging | Operate | Operate | 100 | 100
10746 | 5/12/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
10747 | 1/15/1999 | Not Challenging | Refueling | Refueling | 0 | 0
10748 | 5/29/2003 | Not Challenging | Operate | Operate | 100 | 100
10749 | 9/10/2009 | Not Challenging | Operate | Operate | 100 | 100
10750 | 2/28/2009 | Not Challenging | Refueling | Refueling | 0 | 0
10751 | 1/28/2000 | Not Challenging | Operate | Operate | 100 | 100
20264 | 2/2/1990 | Undetermined (NC‐PC | Operate | Operate
20265 | 2/2/1990 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20266 | 2/19/1990 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20267 | 3/12/1990 | Undetermined (NC‐PC) | Cold Shutdown | : Cold Shutdown | 0 | 0
20268 | 4/19/1990 D | Undetermined (NC‐PC) | Operate | : Operate | 100 | 100 | None
20269 | 4/30/1990 | Undetermined (NC‐PC) | : Operate | Operate | 100 | 100 | None
20270 | 6/7/1990 | Undetermined (NC‐PC) | Refueling | : Refueling | 0 | 0
20271 | 7/9/1990 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20272 | 9/10/1990 | Undetermined (NC‐PC | Unknown | Unknown
20273 | 9/18/1990 | Potentially Challenging | Operate | Operate P | 100 | 100
20274 | 10/9/1990 | Potentially Challenging | Operate | Operate | 0
20275 | 10/11/1990 | Undetermined (NC‐PC) | Unknown | Unknown
20276 | 10/12/1990 D | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20277 | 11/16/1990 | : Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20278 | 11/24/1990 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0
20279 | 11/28/1990 | : Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20280 | 12/5/1990 | : Undetermined (PC‐CH) | : Cold Shutdown | Cold Shutdown | 0 | 0
20281 | 6/24/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20282 | 9/17/1991 | : Undetermined (NC‐PC) | Unknown | Unknown
20283 | 10/3/1991 | Undetermined (NC‐PC) | Operate | : Operate | 100 | 100
20284 | 10/14/1991 | Undetermined (NC‐PC) | Refueling M | Refueling | 0 | 0
20285 | 10/25/1991 | Not Challenging | Cold Shutdown | : Cold Shutdown | 0 | 0
20286 | 1/23/1992 | Not Challenging | Operate | Operate | 100 | 100
20287 | 2/29/1992 | Undetermined (NC‐PC) | Unknown | Unknown
20288 | 3/9/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20289 | 3/16/1992 | Undetermined (NC‐PC) | Unknown | : Unknown
20290 | 4/26/1992 | Not Challenging | Operate | Operate | 0 | 0
20291 | 4/28/1992 | Potentially Challenging | Refueling | Refueling | 0 | 0
20292 | 6/25/1992 | Undetermined (NC‐PC) | : Operate | Operate | 100 | 100
20293 | 9/1/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20294 | 10/5/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20295 | 10/12/1992 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0
20296 | 10/23/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20297 | 11/17/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20298 | 1/11/1993 | Undetermined (NC‐PC) | Unknown | Unknown
20299 | 3/9/1993 | Not Challenging | Refueling M | : Refueling P | 0 | 0
20300 | 3/30/1993 | Undetermined (NC‐PC) R | Undetermined (NC‐PC) R | Refueling | 0 | 0 | None
20301 | 4/13/1993 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0
20302 | 7/25/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20303 | 10/14/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
20304 | 11/2/1993 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20305 | 11/18/1993 | Not Challenging | Operate | Refueling | 0 | 0 | None
20306 | 12/30/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20307 | 1/25/1994 | Not Challenging | Operate | Operate | 0 | 0
20308 | 3/9/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20309 | 3/11/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20310 | 3/26/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20311 | 4/4/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20312 | 7/27/1994 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20313 | 9/29/1994 | Undetermined (NC‐PC) | Unknown | Unknown
20314 | 12/19/1994 | Undetermined (NC‐PC) | Unknown | Unknown
20315 | 2/20/1995 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20316 | 2/24/1995 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20317 | 4/10/1995 D | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
20318 | 8/9/1995 | Not Challenging | Operate | Operate | 0 | 0 | None
20319 | 8/15/1995 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | Entered an LCO
20320 | 3/21/1996 D | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20321 | 7/10/1996 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
20322 | 9/13/1996 | Undetermined (NC‐PC) | Operate M | Operate
20323 | 1/8/1997 | Challenging | Operate | Operate
20324 | 8/12/1997 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20325 | 1/16/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20326 | 10/12/1998 D | Undetermined (NC‐PC) | Refueling | Refuelin | 0 | 0 | None
20327 | 11/2/1998 | Not Challenging | Operate | Operate | 100 | 100 | None
20328 | 5/6/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20329 | 9/1/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20330 | 10/3/1999 | Undetermined (NC‐PC) | Refueling | : Refueling | 0 | 0
20331 | 11/4/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20332 | 12/14/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20333 | 1/12/1990 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20334 | 2/20/1990 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 | None
20335 | 4/13/1990 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20336 | 2/14/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
20337 | 4/21/1991 | Undetermined (NC‐PC) | Preliminary | Operate | 0 | 0 | None
20338 | 10/11/1991 | 10/11/1991 | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20340 | 12/1/1992 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20341 | 3/31/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20342 | 4/30/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20343 | 8/13/1993 D | Not Challenging | Refueling | Refueling | 0 | 0 | None
20344 | 2/20/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20345 | 3/28/1994 | Not Challenging | Refueling | Refueling P | 0 | 0 | None
20346 | 3/30/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20347 | 4/15/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20348 | 4/16/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20349 | 4/23/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20350 | 6/9/1994 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20351 | 6/21/1994 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20352 | 6/23/1994 | Potentially Challenging | Operate | Operate | 100 | 100 | None
20353 | 7/13/1994 | Potentially Challenging | Operate |  | 100 | 100 | None
20354 | 10/8/1994 | Not Challenging | Operate | Operate | 100 | 100
20355 | 10/31/1994 | Not Challenging | Operate | Operate | 100 | 100 | None
20356 | 2/19/1995 | Potentially Challenging | Operate | Operate | 100 | 100 | None
20357 | 5/24/1995 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram
20358 | 1/23/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20359 | 3/3/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
20360 | 5/25/1996 | Undetermined (PC‐CH) | Unknown | Unknown
20361 | 1/7/1997 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20362 | 3/2/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None
20363 | 7/27/1997 | Not Evaluated | Operate | Operate | 100 | 100 | None
20364 | 12/4/1997 | Undetermined (NC‐PC) | Operate | Operate |  |  | None
20365 | 1/13/1998 | Potentially Challenging | Operate | Operate | 100 | 75 | Reduced Power
20366 | 2/6/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20367 | 2/24/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None
20368 | 6/7/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20369 | 6/14/1998 | Potentially Challenging | Operate | Operate P | 100 | 100 | None
20370 | 7/1/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
20371 | 9/9/1998 | Undetermined (NC‐PC) | Unknown | Unknown
20372 | 11/23/1998 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
20373 | 3/16/1999 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
20374 | 3/19/1999 | Potentially Challenging | Operate | Operate | 100 | 100 | None
20375 | 3/29/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None
20376 | 7/29/1999 | Not Challenging | Operate | Operate | 100 | 100 | None
20377 | 2/8/2000 | Challenging | Operate | Operate | 100 | 100 | None
20378 | 2/25/2000 | Potentially Challenging | Operate | Operate | 59 | 40 | Reduced Power
20379 | 6/20/2000 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO
20380 | 8/16/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert
20381 | 10/17/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20382 | 10/23/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
20383 | 11/5/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
20384 | 12/27/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
20385 | 12/27/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
30265 | 8/5/2008 | Not Challenging | Operate | Operate | 100 | 100
30266 | 1/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100
30268 | 8/9/2000 | Not Challenging | Operate | Operate | 100 | 100
30269 | 8/14/2002 | Not Challenging | Operate | Operate | 100 | 100
30270 | 3/16/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0
30271 | 9/11/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
30272 | 7/9/2004 | Not Challenging | Operate | Operate | 100 | 100
30275 | 1/13/2006 | Not Challenging | Operate | Operate | 100 | 100
30276 | 7/24/2006 | Potentially Challenging | Operate | Operate | 100 | 100
30277 | 12/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100
30278 | 10/15/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30279 | 5/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30281 | 6/5/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0
30282 | 11/26/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30283 | 3/20/2002 | Potentially Challenging | Operate | Operate | 100 | 100
30284 | 3/12/2004 | Not Challenging | Operate | Operate | 100 | 100
30285 | 11/2/2007 | Not Challenging | Operate | Operate | 100 | 100
30286 | 6/18/2009 | Potentially Challenging | Operate | Operate | 100 | 100
30287 | 10/1/2009 | Potentially Challenging | Refueling | Refueling | 0
30288 | 4/14/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30289 | 7/8/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30290 | 1/20/2001 | Not Challenging | Operate | Operate | 100 | 100
30291 | 3/14/2001 | Not Challenging | Operate | Operate |  |  | None
30292 | 6/17/2001 | Not Challenging | Operate | Operate
30293 | 8/20/2001 | Not Challenging | Operate | Operate | 100 | 100
30294 | 11/7/2001 | Not Challenging | Operate | Operate |  |  | None
30295 | 3/15/2002 | Not Challenging | Operate | Operate | 100 | 100
30296 | 11/22/2002 | Potentially Challenging | Refueling | Refueling
30297 | 8/7/2003 | Not Challenging | Cold Shutdown | Cold Shutdown
30298 | 4/13/2006 | Not Challenging | Operate | Operate |  |  | None
30299 | 4/25/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30300 | 5/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30301 | 6/7/2006 | Not Challenging | Operate | Operate
30302 | 1/26/2007 | Potentially Challenging | Operate | Operate |  |  | None
30303 | 6/8/2007 | Not Challenging | Operate | Operate | 100 | 100
30304 | 11/29/2007 | Not Challenging | Operate | Operate |  |  | None
30305 | 12/14/2007 | Not Challenging | Operate | Operate | 100 | 100
30306 | 1/17/2009 | Not Challenging | Operate | Operate | 100 | 100
30307 | 3/27/2000 | Not Challenging | Operate | Operate |  |  | None
30308 | 4/3/2001 | Not Challenging | Operate | Operate | 100 | 100
30309 | 7/21/2001 | Not Challengin | Operate | Operate
30310 | 9/7/2001 | Not Challenging | Operate | Operate |  |  | None
30311 | 9/24/2001 | Not Challenging | Operate | Operate | 10 | 100
30312 | 3/29/2003 | Potentially Challenging | Hot Standby | Hot Standby | 0 | 0 | None
30313 | 11/5/2007 | Not Challenging | Operate | Operate | 100 | 100 | Scram
30314 | 12/19/2001 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
30316 | 3/16/2003 | Not Challenging | Operate | Operate | 100 | 100
30317 | 4/18/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
30318 | 5/16/2005 | Not Challenging | Refueling | Refuelin | 0 | 0
30319 | 7/18/2005 | Not Challenging | Operate | Operate | 100 | 100
30320 | 5/8/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30321 | 11/21/2008 | Not Challenging | Operate | Operate | 100 | 100
30322 | 10/28/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0
30323 | 12/9/2006 | Not Challenging | Operate | Operate | 100 | 100
30324 | 1/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30325 | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30326 | 5/1/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30327 | 3/6/2009 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30330 | 4/30/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
30331 | 10/12/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30332 | 4/6/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
30333 | 7/31/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
30334 | 9/27/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30335 | 1/24/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
30338 | 3/30/2006 | Undetermined (NC‐PC) | Operate | Operate |  |  | None
30339 | 6/21/2000 | Not Challenging | Operate | Operate | 100 | 100
30340 | 11/10/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30341 | 1/2/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30342 | /11/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
30343 | 5/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
30344 | 1/23/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30345 | 8/29/2003 | Not Challenging | Operate | Operate | 100 | 100
30346 | 10/22/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
30347 | 3/27/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30348 | 11/22/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
30350 | 7/26/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30351 | 5/14/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
30354 | 2/8/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
30355 | 2/17/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
30356 | 11/21/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
30357 | 6/20/2007 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
30358 | 8/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
30359 | 1/10/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
30360 | 4/21/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30361 | 4/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
30362 | 12/16/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
30363 | 5/5/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
30364 | 5/26/2003 | Not Challenging | Refueling | Refueling | 0 | 0
30365 | 9/8/2003 | Not Challenging | Operate | Operate | 100 | 100
30366 | 12/2/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
30367 | 3/30/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30368 | 7/6/2004 | Not Challenging | Operate | Operate | 100 | 100
30369 | 10/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30370 | 10/31/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
30371 | 11/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30372 | 11/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30373 | 11/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30374 | 11/30/2005 | Potentially Challenging | Refueling | : Refueling | 0 | 0 | None
30375 | 5/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30376 | 10/14/2007 | Not Challengin | Refueling | Refueling | 0 | 0
30377 | 11/3/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30378 | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30379 | 11/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30380 | 12/17/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
30381 | 4/7/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
30382 | 5/21/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30383 | 2/11/2009 | Not Challenging | Operate | Operate | 100 | 100
30384 | 10/18/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30385 | 10/27/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
30386 | 5/11/2001 | Potentially Challenging | Operate | Operate | 100 | 100
30387 | 5/24/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30388 | 4/6/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0
30389 | 10/18/2005 | Not Challenging | Operate | Operate | 100 | 100
30390 | 5/7/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0
30391 | 11/13/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30392 | 3/20/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30393 | : 3/24/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30394 | 2/2/2003 | Potentially Challenging | Operate | Operate | 100 | 100
30395 | 3/21/2004 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0
30396 | 3/22/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30397 | 4/4/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30398 | 10/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30400 | 9/18/2007 | Not Challenging | Operate | Operate | 100 | 100
30401 | 2/6/2008 | Not Challenging | Operate | Operate | 100 | 100
30402 | 4/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30403 | 9/24/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30404 | 4/21/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30405 | 10/26/2009 | Not Challenging | Operate | Operate | 100 | 100
30407 | 4/30/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0
30408 | 3/19/2001 | Potentially Challenging | Operate | Operate | 100 | 100
30409 | 8/21/2000 | Potentially Challenging | Operate | Operate | 100 | 100
30410 | 10/25/2000 | Potentially Challenging | Operate | Operate | 100 | 100
30411 | 3/28/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30412 | 4/25/2002 | Potentially Challenging | Refueling | Cold Shutdown | 0 | 0
30413 | 4/25/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30414 | 3/28/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30415 | 4/29/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30416 | 4/29/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30417 | 3/20/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30418 | 2/19/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30419 | 10/4/2001 | Not Challenging | Operate | Operate | 0 | 0
30420 | 3/18/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30421 | 3/5/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30422 | 11/27/2001 | Potentially Challenging | Operate | Operate | 0 | 0
30423 | 3/17/2001 | Not Challenging | Refueling | Refueling | 0 | 0
30424 | 4/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
30425 | 10/7/2002 | Potentially Challenging | Operate | Operate | 0 | 0
30426 | 10/31/2002 | Not Challenging | Operate | Operate | 100 | 100
30429 | 5/6/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0
30430 | 1/13/2006 | Not Challenging | Operate |  | 100 | 100
30431 | 6/18/2006 | Not Challenging | Operate | Operate | 100 | 100
30433 | 6/2/2007 | Not Challenging | Operate | Operate | 100 | 100
30434 | 8/12/2007 | Potentially Challenging | Operate | Operate | 100 | 100
30435 | 8/16/2007 | Not Challenging | Operate | Operate | 100 | 100
30436 | 9/30/2000 | Not Challenging | efueling | Refueling | 0 | 0
30437 | 10/6/2000 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
30438 | 5/15/2007 | Not Challenging | Operate | Operate | 0 | 0
30439 | 3/21/2008 | Undetermined (NC‐PC) | Operate | Operate | 100
30440 | 10/26/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30441 | 9/5/2001 | Not Challenging | Operate | Operate | 100 | 100
30442 | 9/5/2001 | Not Challenging | Operate | Operate | 100 | 100
30443 | 12/31/2001 | Not Challenging | Operate | Operate | 100 | 100
30444 | 3/13/2002 | Not Challenging | Refueling | : Refueling | 0 | 0
30445 | 10/18/2002 | Not Challenging | Operate | Operate | 100 | 100
30446 | 4/1/2003 | Potentially Challenging | Operate | Operate | 100 | 100
30447 | 7/11/2004 | Potentially Challenging | Operate | Operate | 0 | 0 | None
30449 | 10/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30452 | 8/8/2008 | Not Challenging | Operate | Operate | 100 | 100
30453 | 1/30/2009 | Potentially Challenging | Operate | Operate | 100 | 100
30454 | 6/22/2009 | Not Challenging | Operate | Operate | 100 | 100
30455 | 3/14/2000 | Not Challenging | Operate | Operate | 100 | 100
30456 | 3/7/2001 | Potentially Challenging | Operate | Operate | 100 | 100
30457 | 10/24/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30458 | 1/18/2003 | Not Challenging | Operate | Operate
30459 | 3/9/2003 | Potentially Challenging | Operate | Operate | 100 | 100
30460 | 3/18/2003 | Potentially Challenging | Operate | Operate | 100 | 100
30461 | 3/23/2004 | Not Challenging | Operate | Operate | 100 | 100
30462 | : 5/24/2004 | Not Challenging | Operate | Operate | 100 | 100
30463 | 10/28/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30464 | 9/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30465 | 9/24/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0
30469 | 11/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100
30471 | 4/4/2008 | Potentially Challenging | Operate | Operate | 100 | 100
30472 | 9/29/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30473 | 9/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0
30474 | 8/12/2002 | Not Challenging | Operate | Operate | 100 | 100
30475 | 4/26/2003 | Not Challenging | Operate | Operate | 100 | 100
30476 | 10/12/2003 | Not Challenging | Operate | Operate | 100 | 100
30478 | 9/9/2005 | Potentially Challenging | Operate | Operate | 100 | 100
30479 | 9/24/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30480 | 9/25/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30481 | 9/25/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30482 | 10/5/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30483 | 10/9/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30485 | 9/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30487 | 12/4/2006 | Not Challenging | Operate | Operate | 100 | 100
30488 | 10/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30489 | 6/21/2009 | Not Challenging | Operate | Operate | 100 | 100
30493 | 7/24/2008 | Not Challenging | Operate | Operate | 100 | 100
30498 | 6/21/2009 | Not Challenging | Operate | Operate | 100 | 100
30500 | 5/29/2002 | Not Challenging | Operate | Operate | 100 | 100
30502 | 10/8/2003 | Not Challenging | Operate | Operate | 100 | 100
30503 | 3/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30504 | 3/17/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30505 | 3/11/2003 | Not Challenging | Operate | Operate | 100 | 100
30506 | 12/17/2003 | Not Challenging | Operate | Operate | 100 | 100
30507 | 7/26/2005 | Potentially Challenging | Operate | Operate | 100 | 100
30508 | 3/26/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0
30509 | 8/11/2009 | Not Challenging | Operate | Operate | 100 | 100
30510 | 1/17/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30511 | 1/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0
30512 | 2/15/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0
30513 | 5/27/2008 | Potentially Challenging | Operat | Operat | 100 | 100
30514 | 3/7/2003 | Not Challenging | Operat | Operat | 100 | 100
30515 | 6/25/2005 | Not Challenging | Operat | Operat | 100 | 100
30516 | 6/25/2005 | Not Challenging | Operat | Operat | 100 | 100
30517 | 7/29/2005 | Not Challenging | Operat | Operat | 100 | 100
30519 | 1/5/2009 | Not Challenging | Operat | Operat | 100 | 100
30520 | 3/1/2000 | Not Challenging | Unknown | Unknown
30521 | 9/11/2000 | Not Challenging | Unknown | Unknown
30522 | 9/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100
30523 | 9/14/2000 | Not Challenging | Operate | Operate | 100 | 100
30524 | 12/14/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30525 | 3/7/2001 | Not Challenging | Operate | Operate | 100 | 100
30526 | 6/12/2001 | Not Challenging | Refueling | Refueling | 0 | 0
30527 | 2/1/2002 | Not Challenging | Operate | Operate | 100 | 100
30528 | 2/24/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30529 | 3/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30530 | 3/23/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30531 | 4/17/2002 | Not Challenging | Operate | Operate | 100 | 100
30532 | 9/12/2000 | Not Challenging | Operate | Operate | 100 | 100
30533 | 2/10/2003 | Not Challenging | Operate | Operate | 100 | 100
30534 | 3/4/2004 | Not Challenging | Operate | Operate | 100 | 100
30535 | 4/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30536 | 9/13/2004 | Not Challenging | Operate | Operate | 100 | 100
30537 | 6/15/2005 | Not Challenging | Operate | Operate | 100 | 100
30538 | 1/23/2005 | Not Challenging | Operate | Operate | 100 | 100
30539 | 2/3/2005 | Not Challenging | Operate | Operate | 100 | 100
30540 | 5/2/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30541 | 7/6/2005 | Not Challenging | Operate | Operate | 100 | 100
30542 | 7/28/2005 | Not Challenging | Operate | Operate | 100 | 100
30543 | 8/24/2005 | Not Challenging | Operate | Operate | 100 | 10
30544 | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0
30545 | 1/16/2006 | Not Challenging | Operate | Operate | 100 | 100
30546 | 4/26/2006 | Not Challenging | Operate | Operate | 100 | 100
30547 | 4/19/2006 | Not Challenging | Operate | Operate | 100 | 100
30548 | 7/24/2006 | Not Challenging | Operate | Operate | 100 | 100
30549 | 9/5/2006 | Not Challenging | Operate | Operate | 100 | 100
30550 | 10/5/2006 | Not Challenging | Operate | Operate | 100 | 100
30551 | 10/20/2006 | Not Challenging | Operate | Operate | 0 | 0
30552 | 5/8/2007 | Not Challenging | Operate | Operate | 100 | 100
30553 | 8/28/2007 | Not Challenging | Operate | Operate | 100 | 100
30554 | 10/17/2007 | Not Challenging | Operate | Operate | 100 | 100
30555 | 4/1/2008 | Not Challenging | Operate | Operate | 100 | 100
30556 | 4/4/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30557 | 4/30/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30558 | 10/20/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30559 | 11/21/2008 | Not Challenging | Operate | Operate | 100 | 100
30560 | 2/4/2009 | Not Challenging | Operate | Operate | 100 | 100
30561 | 4/3/2008 | Not Challenging | Refueling | Refueling | 100 | 100
30562 | 3/17/2008 | Not Challenging | Operate | Operate | 100 | 100
30563 | 3/9/2008 | Not Challenging | Operate | Operate | 100 | 100
30564 | 11/18/2003 | Not Challenging | Operate | Operate | 100 | 100
30565 | 2/11/2000 | Not Challenging | Operate | Operate | 100 | 100
30566 | 9/11/2000 | Potentially Challenging | Operate | Operate | 100 | 100
30567 | 10/17/2000 | Not Challenging | Operate | Operate | 100 | 100
30568 | 1/19/2002 | Not Challenging | Operate | Operate | 100 | 100
30569 | 10/16/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30570 | 3/28/2001 | Not Challenging | Operate | Operate | 100 | 100
30571 | 1/12/2001 | Not Challenging | Refueling | Refueling | 0 | 0
30572 | 5/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0
30573 | 6/6/2004 | Not Challenging | Operate | Operate | 100 | 100
30574 | 11/2/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30576 | 8/15/2006 | Not Challenging | Operate | Operate | 100 | 100
30577 | 3/3/2000 | Not Challenging | Operate | Operate | 100 | 100
30578 | 2/27/2003 | Not Challenging | Operate | Operate | 100 | 100
30579 | 6/6/2007 | Not Challenging | Operate | Operate | 100 | 100
30580 | 6/21/2000 | Not Challenging | Operate | Operate | 100 | 100
30581 | 6/19/2007 | Not Challenging | Operate | Operate | 100 | 100
30582 | 6/7/2000 | Not Challenging | Operate | Operate | 100 | 100
30583 | 6/30/2003 | Not Challenging | Operate | Operate | 100 | 100
30584 | 5/24/2001 | Not Challenging | Operate | Operate | 100 | 100
30585 | 5/3/2001 | Not Challenging | Operate | Operate | 100 | 100
30586 | 1/11/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30587 | 3/4/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30588 | 5/14/2009 | Not Challenging | Operate | Operate | 100 | 100
30589 | 10/11/2009 | Not Challenging | Refueling | Refueling | 0 | 0
30590 | 12/22/2009 | Not Challenging | Operate | Operate | 100 | 100
30591 | 10/17/2005 | Not Challenging | Operate | Operate | 100 | 100
30593 | 2/7/200 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
30594 | 6/17/2007 | Not Challenging | Operate | Operate | 100 | 100
30595 | 10/10/2008 | Not Challenging | Operate | Operate | 100 | 100
30596 | 10/17/2008 | Not Challenging | Operate | Operate | 100 | 100
30597 | 2/5/2009 | Not Challenging | Operate | Operate | 100 | 100
30598 | 11/20/2009 | Not Challenging | Operate | Operate | 100 | 100
30599 | 3/23/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
30600 | 11/9/2001 | Not Challenging | Operate | Operate | 100 | 100
30601 | 9/14/2001 | Not Challenging | Operate | Operate | 100 | 100
30602 | 5/19/2004 | Not Challenging | Operate | Operate | 100 | 100
30603 | 1/13/20 | Not Challenging | Operate | Operate | 100 | 100
30604 | 5/28/2005 | Potentially Challenging | Operate | Operate | 100 | 100
30605 | 9/19/2005 | Not Challenging | Operate | Operate | 100 | 100
30606 | 12/19/2007 | Not Challenging | Operate | Operate | 100 | 100
30607 | 3/20/2001 | Not Challenging | Unknown | Unknown | 0 | 0
30608 | 1/10/2002 | Not Challenging | Operate | Operate | 100 | 100
30609 | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100
30610 | 7/21/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
30693 | 2/3/2004 | Not Challenging | Operate | Operate | 100 | 100
30694 | 8/10/2004 | Not Challenging | Operate | Operate | 100 | 100
30695 | 9/21/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
30696 | 9/26/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30697 | 9/29/2006 | Not Challenging | Refueling | Refueling | 0 | 0
30698 | 2/22/2007 | Not Challenging | Operate | Operate | 100 | 100
30699 | 3/7/2007 | Not Challenging | Operate | Operate | 100 | 100
30700 | 4/19/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30701 | 8/13/2007 | Not Challenging | Operate | Operate | 100 | 100
30702 | 9/11/2007 | Not Challenging | Operate | Operate | 100 | 100
30703 | 10/2/2007 | Not Challenging | Operate | Operate | 100 | 100
30704 | 10/17/2007 | Not Challenging | Operate | Operate | 100 | 100
30705 | 9/20/2007 | Not Challenging | Operate | Operate | 100 | 100
30706 | 6/28/2000 | Not Challenging | Operate | Operate | 100 | 100
30707 | 10/1/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30708 | 2/6/2001 | Not Challenging | Operate | Operate | 100 | 100
30709 | 7/13/2001 | Not Challenging | Operate | Operate | 100 | 100
30710 | 9/19/2001 | Not Challenging | Operate | Operate | 100 | 100
30711 | 11/16/2001 | Not Challenging | Operate | Operate | 100 | 100
30712 | 4/24/2002 | Not Challenging | Operate | Operate | 100 | 100
30713 | 4/29/2002 | Not Challenging | Operate | Operate | 100 | 100
30716 | 9/2/2002 | Not Challenging | Operate | Operate | 100 | 100
30717 | 12/10/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
30718 | 4/15/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30719 | 6/11/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
30720 | 7/2/2003 | Not Challenging | Operate | Operate | 100 | 100
30721 | 8/27/2003 | Not Challenging | Operate | Operate | 100 | 100
30722 | 10/19/2003 | Not Challenging | Operate | Operate | 100 | 100
30723 | 11/3/2008 | Not Challenging | Operate | Operate | 100 | 100
30724 | 11/16/2008 | Not Challenging | Operate | Operate | 100 | 100
30725 | 4/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None
30726 | 5/19/2000 | Not Challenging | Operate | Operate | 100 | 100
30727 | 10/30/2000 | Potentially Challenging | Operate | Operate | 100 | 100
30728 | 12/21/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
30729 | 12/22/2000 | Not Challenging | Refueling | Refueling | 0 | 0
30730 | 3/5/2001 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30731 | 3/19/2001 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
30732 | 12/3/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
30733 | 6/27/2002 | Potentially Challenging | Operate | Operate
30734 | 8/26/2002 | Potentially Challenging | Operate | Operate
30735 | 3/4/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
30736 | 3/13/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
30737 | 5/12/2003 | Not Challenging | Operate | Operate | 100 | 100
30738 | 9/23/2003 | Not Challenging | Operate | Operate | 100 | 100
30739 | 3/29/2001 | Not Challenging | Operate | Operate | 100 | 100
30740 | 2/6/2004 | Potentially Challenging | Operate | Operate | 100 | 100
30741 | 3/24/2004 | Not Challenging | Operate | Operate | 100 | 100
30742 | 4/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30743 | 4/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30744 | 6/2/2004 | Not Challenging | Operate | Operate | 100 | 100
30745 | 10/10/2004 | Not Challenging | Operate | Operate | 100 | 100
30746 | 10/28/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30747 | 11/6/2004 | Not Challenging | Refueling | Refueling | 0 | 0
30748 | 11/27/2004 | Not Challenging | Operate | Operate | 100 | 100
30749 | 1/9/2005 | Not Challenging | Operate | Operate | 100 | 100
30750 | 5/9/2005 | Undetermined (PC‐CH) | Cold Shutdown | Cold Shutdown | 0 | 0
30751 | 3/28/2006 | Not Challenging | Operate | Operate | 100 | 100
30752 | 4/3/2007 | Potentially Challenging | Operate | Operate
30753 | 5/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0
30754 | 2/2/2008 | Not Challenging | Operate | Operate | 100 | 100
30755 | 4/7/2008 | Not Challenging | Operate | Operate | 100 | 100
30756 | 11/23/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
30757 | 8/24/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
30758 | 9/3/2009 | Not Challenging | Unknown | Unknown
40730 | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
40731 | 2/13/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
40732 | 3/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
40733 | 3/14/2001 | Potentially Challenging | Operate | Operate | 100 |  | None
40734 | 3/19/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
40735 | 4/4/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None
40736 | 4/15/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
40737 | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
40738 | 6/5/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
40739 | 7/23/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
40740 | 3/3/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
40741 | 4/16/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
40742 | 7/7/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
40743 | 10/7/200 | Not Challenging | Operate | Operate | 100 | 100 | None
40744 | 3/24/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
40745 | 10/20/2005 | Not Challenging | Refueling | Refueling |  |  | None
40746 | 8/15/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None
40747 | 4/17/2007 | Not Challenging | Refueling | Refueling | 0 | 0
40748 | 11/28/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
40749 | 6/13/2008 | Challenging | Operate | Operate | 100 | 100 | None
40750 | 11/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50356 | 1/11/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50357 | 3/21/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50358 | 6/1/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50359 | 8/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50360 | 12/20/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50361 | 4/11/2001 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50362 | 7/16/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50364 | 10/4/2001 | Not Challenging | Operate | Operate |  |  | None
50365 | 3/4/2002 | Not Challenging | Operate | Operate | 97 | 97 | None
50366 | 3/8/2002 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50367 | 3/14/2002 | Not Challenging | Refueling | Refueling | 0 | 0
50368 | 6/6/2002 | Not Challenging | Operate | Operate | 0 | 0
50369 | 8/14/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50370 | 10/23/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50371 | 11/1/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50372 | 5/9/2003 | Not Challenging | Hot Standby | Hot Standby | 0 | 0 | None
50373 | 10/7/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50374 | 4/22/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50375 | 9/30/2004 | Not Challenging | Operate | Operate | 0 | 0 | None
50376 | 3/24/2005 | Not Challenging | Operate | Operate | 0 | 0 | None
50377 | 7/2/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50378 | 7/27/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50379 | 2/24/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
50380 | 8/31/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
50381 | 12/14/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
50382 | 1/29/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50383 | 3/1/2007 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO
50384 | 3/22/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50385 | 5/30/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50387 | 3/29/2008 | Not Challenging | Refueling | Refueling | 0 | 100 | None
50388 | 6/8/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50389 | 6/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO
50390 | 10/1/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50391 | 7/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50392 | 8/13/2000 | Not Challenging | Operate | Operate | 100 | 100
50393 | 10/17/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50394 | 4/21/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50395 | 4/16/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50396 | 5/1/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50397 | 1/13/2003 | Not Challenging | Operate | Operate | 100 | 100
50398 | 12/2/2003 | Not Challenging | Operate | Operate | 100 | 100
50399 | 2/26/2004 | Not Challenging | Refueling | Refueling | 0 | 0
50400 | 8/7/2004 | Not Challenging | Operate | Operate | 100 | 100
50401 | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0
50402 | 11/8/2005 | Not Challenging | Operate | Operate | 100 | 100
50403 | 11/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50404 | 11/25/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50405 | 3/4/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50406 | 8/21/2007 | Not Challenging | Unknown | Unknown
50407 | 3/11/2008 | Potentially Challenging | Operate | Operate | 100 | 100
50409 | 10/5/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
50410 | 9/29/2005 | Not Challenging | Operate | Operate | 100 | 100
50411 | 7/9/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
50423 | 2/28/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50424 | 3/15/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50425 | 3/16/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
50426 | 5/2/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50427 | 8/19/2000 | Not Challenging | Operate | Operate | 100 | 100
50428 | 9/20/2000 | Not Challenging | Operate | Operate | 100 | 100
50429 | 3/19/2001 | Not Challenging | Operate | Operate | 100 | 100
50430 | 2/18/2000 | Not Challenging | Operate | Operate | 100 | 100
50432 | 3/19/2001 | Not Challenging | Unknown | Unknown
50433 | 8/17/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50434 | 10/28/2001 | Not Challenging | Operate | Operate | 100 | 100
50435 | 7/22/2002 | Not Challenging | Operate | Operate | 100 | 100
50436 | 8/12/2002 | Not Challenging | Operate | Operate | 100 | 100
50438 | 1/7/2003 | Not Challenging | Operate | Operate | 100 | 100
50439 | 3/3/2003 | Not Challenging | Operate | Operate | 100 | 100
50440 | 10/13/2004 | Not Challenging | Operate | Operate | 100 | 100
50441 | 10/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0
50442 | 11/8/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50443 | 3/20/2005 | Not Challenging | Operate | Operate | 100 | 100
50444 | 4/27/2005 | Not Challenging | Operate | Operate | 100 | 100
50445 | 4/28/2005 | Not Challenging | Operate | Operate | 53 | 53 | None
50446 | 7/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50447 | 9/14/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50448 | 10/11/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50449 | 2/21/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
50450 | 2/28/2006 | Not Challenging | Refueling | Refueling | 0 | 0
50451 | 7/15/2006 | Not Challenging | Operate | Operate | 100 | 100
50452 | 8/18/2006 | Undetermined (NC‐PC) | Operate | Operate | 97 | 97 | None
50453 | 8/22/2006 | Not Challenging | Operate | Operate | 100 | 100
50454 | 11/8/2006 | Not Challenging | Operate | Operate | 100 | 100
50455 | 11/30/2006 | Not Challenging | Operate | Operate | 100 | 100
50456 | 2/15/2007 | Not Challenging | Operate | Operate | 100 | 100
50457 | 7/28/2007 | Not Challenging | Operate | Operate | 100 | 100
50458 | 8/15/2007 | Not Challenging | Operate | Operate | 100 | 100
50459 | 2/8/2008 | Not Challenging | Operate | Operate | 100 | 100
50460 | 4/16/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50461 | 4/24/2008 | Not Challenging | Operate | Operate | 100 | 100
50462 | 6/12/2008 | Not Challenging | Operate | Operate | 100 | 100
50463 | 4/11/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50464 | 4/26/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50466 | 2/4/2005 | Not Challenging | Operate | Operate | 100 | 100
50467 | 2/4/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50468 | 11/2/2007 | Not Challenging | Refueling | Refueling | 0 | 0
50469 | 7/28/2008 | Not Challenging | Operate | Operate | 100 | 100
50470 | 11/19/2008 | Not Challenging | Operate | Operate | 100 | 100
50471 | 12/2/2008 | Not Challenging | Operate | Operate | 0 | 0 | None
50472 | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100
50473 | 6/26/2000 | Potentially Challenging | Operate | Operate | 100 | 100
50474 | 8/29/2000 | Not Challenging | Operate | Operate | 100 | 100
50475 | 10/11/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100
50476 | 12/19/2000 | Not Challenging | Unknown | Unknown
50477 | 3/18/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
50478 | 3/19/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50479 | 3/22/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0
50480 | 4/7/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50481 | 11/4/2006 | Not Challenging | Operate | Operate | 100 | 100
50482 | 3/8/2006 | Not Challenging | Unknown | Unknown
50483 | 3/11/2008 | Not Challenging | Operate | Operate | 100 | 100
50484 | 3/23/2008 | Not Challenging | Operate | Operate | 100 | 100
50486 | 4/20/2008 | Not Challenging | Operate | Operate | 100 | 100
50487 | 3/6/2009 | Not Challenging | Operate | Operate | 100 | 100
50488 | 5/27/2009 | Not Challenging | Operate | Operate | 100 | 100
50489 | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100
50490 | 9/16/2009 | Not Challenging | Operate | Operate | 100 | 100
50491 | 10/16/2009 | Not Challenging | Operate | Operate | 100 | 100
50492 | 11/2/2009 | Not Challenging | Operate | Operate | 100 | 100
50494 | 2/5/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50495 | 11/11/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50496 | 1/21/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50497 | 8/15/2006 | Not Challenging | Operate | Operate |  |  | None
50499 | 4/1/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50501 | 11/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50502 | 10/16/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50503 | 6/14/2001 | Not Challenging | Operate | Operate |  |  | None
50504 | 5/20/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50506 | 12/9/2007 | Not Challenging | Operate | Operate | 100 | 100
50507 | 11/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50508 | 11/26/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50510 | 4/19/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50511 | 5/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50512 | 5/31/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50513 | 8/27/2003 | Not Challenging | Operate | Operate | 77 | 77 | None
50514 | 4/29/2009 | Not Evaluated | Operate | Operate | 100 | 100 | None
50515 | 11/30/2001 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50516 | 10/5/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50517 | 10/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50518 | 11/18/2001 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
50519 | 10/19/2009 | Not Challenging | Operate | Operate |  |  | None
50520 | 12/7/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50521 | 2/1/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50522 | 9/8/2003 | Undetermined (NC‐PC) | Operate | Operate
50523 | 9/19/2003 | Not Challenging | Operate | Operate |  |  | None
50524 | 1/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50525 | 12/18/2009 | Not Evaluated | Operate | Operate | 100 | 100 | None
50526 | 12/7/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None
50527 | 6/23/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50528 | 6/19/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50529 | 3/31/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50530 | 10/21/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50534 | 1/7/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None
50535 | 1/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50536 | 3/21/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None
50537 | 3/23/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50538 | 3/27/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None
50539 | 5/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50540 | 5/25/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50541 | 4/6/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50542 | 7/30/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50543 | 3/27/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0
50545 | 9/18/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50546 | 12/1/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50547 | 4/4/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
50548 | 6/9/2006 | Not Challenging | Operate | Operate | 0 | 0 | None
50549 | 1/21/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 100 | 100 | None
50550 | 6/9/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50551 | 10/6/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50552 | 3/23/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50553 | 5/2/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50554 | 5/19/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50555 | 6/25/2003 | Not Challenging | Operate | Operate | 100 | 100
50556 | 2/25/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50557 | 1/16/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50558 | 1/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50562 | 5/28/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50563 | 11/16/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
50564 | 1/15/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50565 | 8/26/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50566 | 9/17/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50569 | 3/24/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50570 | 6/21/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
50571 | 7/22/2004 | Not Challenging | Operate | Operate | 100 | 100
50572 | 10/8/2003 | Not Challenging | Operate | Operate | 0 | 0 | None
50573 | 8/24/2004 | Not Challenging | Operate | Operate | 100 | 100
50574 | 9/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50575 | 9/14/2007 | Not Challenging | Cold Shutdown M | Cold Shutdown | 0 | 0 | None
50576 | 9/17/2004 | Not Challenging | Operate | Operate | 100 | 100
50577 | 10/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0
50578 | 11/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0
50579 | 5/4/2005 | Not Challenging | Operate | Operate | 100 | 100
50580 | 10/9/2004 | Not Challenging | Operate | Operate | 100 | 100
50581 | 6/24/2005 | Not Challenging | Operate | Operate | 100 | 100
50582 | 8/22/2005 | Not Challenging | Operate | Operate | 100 | 100
50583 | 9/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | Reduced Power
50584 | 6/27/2005 | Not Challenging | Operate | Operate | 100 | 100
50585 | 10/8/2009 | Not Challenging | Operate | Operate | 100 | 100
50586 | 9/28/2005 | Not Challenging | Operate | Operate | 100 | 100
50587 | 2/4/2006 | Not Challenging | Operate | Operate | 100 | 100 | Reduced Power
50588 | 2/4/2006 | Not Challenging | Operate | Operate | 100 | 100
50589 | 4/15/2006 | Not Challenging | Refueling | Refueling | 0 | 0
50590 | 5/6/2006 | Not Challenging | Operate | Operate | 100 | 100
50591 | 5/29/2006 | Not Challenging | Operate | Operate | 100 | 100
50592 | 7/11/2006 | Not Challenging | Operate | Operate | 100 | 100
50593 | 10/4/2006 | Not Challenging | Operate | Operate | 100 | 100
50594 | 10/5/2006 | Not Challenging | Operate | Operate | 100 | 100
50595 | 10/28/2007 | Not Challenging | Operate | Operate | 0 | 0
50596 | 1/5/2007 | Not Challenging | Operate | Operate | 100 | 100
50597 | 12/18/2007 | Not Challenging | Operate | Operate | 100 | 100
50598 | 3/10/2008 | Not Challenging | Operate | Operate | 100 | 100
50599 | 3/31/2008 | Not Challenging | Operate | Operate | 100 | 100
50600 | 12/2/2008 | Not Challenging | Operate | Operate | 100 | 100
50601 | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100
50603 | 2/24/2007 | Not Challenging | Operate | Operate | 73 | 73 | None
50604 | 11/27/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50605 | 10/4/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50606 | 10/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50607 | 3/1/1997 | Not Evaluated | Operate | Operate | 100 | 100 | None
50608 | 5/28/1997 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50609 | 11/23/2000 | Not Evaluated | Operate | Operate | 100 | 100 | None
50610 | 5/30/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50611 | 3/19/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None
50612 | 10/21/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None
50613 | 7/3/2003 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50614 | 3/9/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50615 | 3/11/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50616 | 3/21/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50617 | 3/29/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None
50618 | 9/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50619 | 2/8/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None
50620 | 3/27/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50621 | 9/11/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50622 | 11/8/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50623 | 12/15/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50624 | 5/14/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50625 | 1/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50627 | 3/24/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50628 | 3/9/2000 | Not Challenging | Operate | Operate | 100 | 100
50629 | 10/16/2000 | Not Challenging | Operate | Operate | 100 | 100
50630 | 10/22/2000 | Not Challenging | Operate | Operate | 100 | 100
50631 | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100
50632 | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100
50633 | 11/12/2000 | Not Challenging | Unknown | Unknown
50634 | 3/6/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50635 | 12/12/2000 | Not Challenging | Operate | Operate | 100 | 100
50636 | 2/10/2001 | Not Challenging | Operate | Operate | 100 | 100
50637 | 4/18/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50638 | 5/14/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50639 | 11/10/2001 | Not Challenging | Operate | Operate | 100 | 100
50640 | 12/23/2001 | Not Challenging | Operate | Operate | 100 | 100
50641 | 3/4/2002 | Not Challenging | Operate | Operate | 100 | 100
50642 | 4/16/2002 | Not Challenging | Operate | Operate | 100 | 100
50643 | 4/18/2002 | Not Challenging | Operate | Operate | 100 | 100
50644 | 6/24/2002 | Not Challenging | Operate | Operate | 100 | 100
50645 | 12/23/2002 | Not Challenging | Operate | Operate | 100 | 100
50646 | 3/7/2003 | Not Challenging | Operate | Operate | 100 | 100
50647 | 8/12/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50648 | 12/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50649 | 4/22/2003 | Not Challenging | Operate | Operate | 100 | 100
50650 | 9/26/2003 | Not Challenging | Unknown | Unknown
50651 | 10/17/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50652 | 3/18/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50653 | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50654 | 9/24/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50655 | 12/4/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
50656 | 8/18/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50657 | 3/2/2004 | Not Challenging | Operate | Operate | 100 | 100
50658 | 4/24/2004 | Not Challenging | Refueling | Refueling | 0 | 0
50659 | 8/11/2004 | Not Challenging | Operate | Operate | 100 | 100
50660 | 9/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50661 | 4/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50662 | 6/5/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50663 | 8/12/2004 | Not Challenging | Operate | Operate | 100 | 100
50664 | 6/29/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50665 | 9/17/2004 | Not Challenging | Operate | Operate | 100 | 100
50666 | 3/22/2005 | Not Challenging | Operate | Operate | 100 | 100
50667 | 3/28/2005 | Not Challenging | Operate | Operate | 100 | 100
50668 | 4/16/2005 | Not Challenging | Operate | Operate | 100 | 100
50669 | 1/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50670 | 10/12/2005 | Not Challenging | Refueling | Refueling | 0 | 0
50671 | 10/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0
50672 | 4/5/2002 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50673 | 4/5/2002 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50674 | 9/23/2005 | Not Challenging | Operate | Operate | 100 | 100
50675 | 8/12/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None
50676 | 11/29/2005 | Not Challenging | Operate | Operate | 100 | 100
50677 | 9/24/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50678 | 3/28/2006 | Not Challenging | Operate | Operate | 100 | 100
50679 | 10/4/2002 | Not Challenging | Operate | Operate | 0 | 0 | None
50680 | 8/24/2006 | Not Challenging | Operate | Operate | 100 | 100
50681 | 11/22/2000 | Not Evaluated | Operate | Operate | 100 | 100 | None
50682 | 4/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0
50683 | 5/18/2004 | Not Evaluated | Operate | Operate | 100 | 100 | None
50684 | 3/8/2007 | Not Challenging | Operate | Operate | 100 | 100
50685 | 3/30/2007 | Not Challenging | Refueling | Refueling | 0 | 0
50686 | 4/4/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0
50687 | 7/23/2007 | Not Challenging | Operate | Operate | 100 | 100
50688 | 5/28/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50689 | 10/17/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50690 | 10/24/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50691 | 2/15/2008 | Not Challenging | Operate | Operate | 100 | 100
50692 | 3/24/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None
50693 | 10/13/2008 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50694 | 10/24/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50696 | 4/21/2008 | Not Challenging | Operate | Operate | 100 | 100
50697 | 7/16/2008 | Not Challenging | Operate | Operate | 100 | 100
50698 | 3/17/2009 | Not Challenging | Operate | Operate | 100 | 100
50699 | 4/7/2000 | Not Challenging | Operate | Operate | 100 | 100
50700 | 5/13/2000 | Not Challenging | Refueling | Refueling | 0 | 0
50701 | 5/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | Turbine Trip
50702 | 6/25/2000 | Not Challenging | Operate | Operate | 100 | 100
50703 | 8/22/2000 | Not Challenging | Operate | Operate | 100 | 100
50704 | 12/22/2000 | Not Challenging | Operate | Operate | 100 | 100
50705 | 4/15/2001 | Not Challenging | Operate | Operate | 100 | 100
50706 | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100
50707 | 4/25/2001 | Not Challenging | Operate | Operate | 100 | 100
50708 | 5/17/2001 | Not Challenging | Operate | Operate | 10 | 10
50709 | 10/26/2001 | Not Challenging | Refueling | Refueling | 0 | 0
50710 | 11/19/2001 | Not Challenging | Operate | Operate | 100 | 100
50711 | 11/20/2001 | Not Challenging | Operate | Operate | 100 | 100
50712 | 12/14/2001 | Not Challenging | Operate | Operate | 80 | 80
50713 | 1/1/2002 | Not Challenging | Operate | Operate | 100 | 100
50714 | 1/9/2002 | Not Challenging | Operate | Operate | 100 | 100
50715 | 1/16/2002 | Not Challenging | Operate | Operate | 100 | 100
50716 | 1/24/2002 | Not Challenging | Operate | Operate | 100 | 100
50717 | 5/21/2002 | Not Challenging | Operate | Operate | 100 | 100
50718 | 3/20/2003 | Not Challenging | Unknown | Unknown | 0 | 0
50719 | 8/1/2003 | Not Challenging | Operate | Operate | 100 | 100
50720 | 8/4/2003 | Not Challenging | Operate | Operate | 100 | 100
50721 | 8/13/2003 | Not Challenging | Operate | Operate | 100 | 100
50722 | 10/10/2003 | Not Challenging | Operate | Operate | 100 | 100
50723 | 1/8/2004 | Not Challenging | Operate | Operate | 100 | 100
50724 | 3/5/2004 | Not Challenging | Operate | Operate | 100 | 100
50725 | 3/10/2004 | Not Challenging | Operate | Operate | 100 | 100
50726 | 10/14/2003 | Not Challenging | Refueling | Refueling | 0 | 0
50728 | 1/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100
50729 | 4/4/2008 | Not Challenging | Refueling | Refueling | 0 | 0
50730 | 3/1/2006 | Not Challenging | Operate | Operate | 100 | 100
50731 | 2/11/2005 | Not Challenging | Operate | Operate | 100 | 100
50732 | 11/7/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
50733 | 4/23/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
50735 | 4/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50736 | 4/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50738 | 3/13/2003 | Not Challenging | Operate | Operate | 100 | 100
50739 | 3/28/2001 | Not Challenging | Operate | Operate | 100 | 100
50740 | 5/16/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
50741 | 9/18/2000 | Not Evaluated | Operate | Operate | 100 | 100
50742 | 10/4/2006 | Not Challenging | Operate | Operate | 100 | 100
50743 | 7/17/2008 | Not Challenging | Operate | Operate | 100 | 100
50744 | 8/3/2001 | Potentially Challenging | Operate | Operate | 100 | 100
50745 | 9/22/2009 | Not Challenging | Operate | Operate | 100 | 100
50746 | 5/6/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0
50747 | 2/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50748 | 9/22/2000 | Not Challenging | Operate | Operate | 100 | 100
50749 | 10/28/2008 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event
50750 | 1/10/2001 | Not Evaluated | Operate | Operate | 100 | 100
50751 | 11/17/2008 | Not Challenging | Operate | Operate | 100 | 100
50753 | 12/11/2009 | Not Challenging | Operate | Operate | 100 | 100
50754 | 1/23/2009 | Potentially Challenging | Operate | Operate | 100 | 100
50756 | 9/21/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50757 | 9/7/2002 | Not Challenging | Operate | Operate | 100 | 100
50758 | 6/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50759 | 7/29/2006 | Not Challenging | Operate | Operate | 100 | 100
50760 | 11/8/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50761 | 1/25/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50762 | 10/1/2001 | Not Challenging | Unknown | Unknown |  |  | None
50763 | 11/14/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
50764 | 1/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50765 | 10/12/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50766 | 8/18/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50767 | 6/1/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50768 | 1/1/2002 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50769 | 12/6/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50770 | 1/30/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50771 | 5/6/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50772 | 7/2/2003 | Challenging | Operate | Operate | 100 | 100 | None
50773 | 9/11/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50774 | 1/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50775 | 2/13/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50776 | 5/6/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50777 | 8/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50778 | 10/11/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50779 | 10/25/2004 | Not Challenging | Operate | Operate | 100 | 100
50780 | 1/6/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50781 | 3/10/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50782 | 3/11/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50783 | 6/27/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50784 | 11/20/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None
50785 | 12/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50786 | 3/10/2006 | Not Challenging | Operate | Operate | 100 | 100 | None
50787 | 1/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50788 | 3/8/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50789 | 3/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50790 | 3/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50791 | 10/25/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50792 | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50793 | 11/18/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50794 | 3/4/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50795 | 7/12/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50796 | 11/4/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50797 | 11/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50798 | 12/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50799 | 12/12/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50803 | 12/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50804 | 1/13/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50805 | 2/12/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50806 | 8/30/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50807 | 8/24/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50808 | 3/21/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50809 | 11/9/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50810 | 6/25/2000 | Not Challenging | Operate | Operate | 100 | 100 | None
50811 | 1/9/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50812 | 6/11/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50813 | 9/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50814 | 5/31/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50815 | 5/19/2005 | Not Challenging | Operate | Operate | 100 | 1010 | None
50816 | 11/16/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50817 | 2/13/2006 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO
50818 | 3/21/2008 | Not Challenging | Operate | Operate | 100 | 100
50819 | 6/13/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50820 | 10/23/2008 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50821 | 10/30/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50822 | 11/7/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50823 | 4/9/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50824 | 9/13/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50825 | 10/1/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50826 | 12/9/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50827 | 4/27/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50828 | 10/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50829 | 9/11/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50833 | 9/23/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50834 | 9/24/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50835 | 10/1/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50837 | 7/9/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50838 | 11/19/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50839 | 11/26/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50840 | 11/28/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50841 | 11/29/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50842 | 8/23/2002 | Not Evaluated | Operate | Operate | 0 | 0 | None
50843 | 3/22/2003 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50844 | 7/24/2003 | Not Evaluated | Operate | Operate | 100 | 100 | None
50845 | 12/13/2003 | Not Evaluated | Operate | Operate | 100 | 100 | None
50846 | 1/24/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50847 | 1/27/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50848 | 1/30/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50849 | 3/8/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None
50850 | 4/1/2005 | Not Evaluated | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50851 | 4/27/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None
50852 | 5/25/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None
50853 | 11/28/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None
50854 | 9/18/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None
50855 | 4/26/2008 | Not Evaluated | Refueling | Refueling | 0 | 0 | None
50856 | 1/31/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None
50857 | 11/6/2009 | Not Evaluated | Unknown | Unknown |  |  | None
50860 | 12/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50861 | 12/20/2004 | Not Challenging | Operate | Operate | 100 | 100 | None
50862 | 2/9/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50863 | 9/30/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50864 | 9/24/2009 | Not Challenging | Operate | Operate | 100 | 100 | None
50865 | 1/31/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50866 | 3/28/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50867 | 10/31/2000 | Not Challenging | Operate | Operate | 0 | 0 | None
50868 | 7/3/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50869 | 10/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None
50870 | 1/8/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50871 | 1/24/2002 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50872 | 3/31/2002 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50873 | 5/9/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50874 | 7/12/2002 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50875 | 11/10/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50876 | 11/13/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50878 | 11/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50879 | 11/15/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50880 | 11/15/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50881 | 12/31/2002 | Not Challenging | Operate | Operate | 100 | 100 | None
50882 | 1/20/2003 | Not Challenging | Operate | Operate | 100 | 100
50883 | 4/18/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None
50884 | 2/23/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 1010 | None
50885 | 6/17/2003 | Not Challenging | Operate | Operate | 100 | 100 | None
50886 | 2/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50887 | 3/7/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50888 | 7/16/2004 | Not Challenging | Operate |  | 0 | 0 | None
50889 | 3/22/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50890 | 4/3/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50891 | 4/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50892 | 4/12/2005 | Not Challenging | Refueling | Refueling | 0 | 0
50893 | 12/2/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None
50894 | 12/2/2005 | Not Challenging | Operate | Operate | 100 | 100 | None
50895 | 5/13/2007 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
50896 | 5/13/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None
50897 | 12/22/2007 | Not Challenging | Operate | Operate | 100 | 100 | None
50898 | 2/29/2008 | Not Challenging | Operate | Operate | 100 | 100 | None
50899 | 10/27/2008 | Challenging | Operate | Operate | 100 | 100 | None
50900 | 5/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None
50901 | 8/28/2009 | Not Challenging | Operate | Operate | 100 | 100 | None