## Fire Event Summaries
FireID | Event Date_FES | Disposition_FES | Plant Area | Building | System | Component Group | Component | Voltage | Current Type | HP or kVA | ICES Component
50907 | 1/9/2010 | Potentially Challenging | N/A | Auxiliary Building (PWR) | Aux. Bldg. Environmental Control System | Electric Motor | Fans | N/A | N/A |  | Blowers, compressors, fans, vacuum pumps, cooling units
50908 | 1/20/2010 | Challenging |  | Other (specify in comments) | No Industry Std. Name for this system | Generator | Other generator (specify in comme |  |  |  | Generators, inverters, motor generators
50909 | 3/7/2010 | Challenging | N/A | Turbine Building | Medium Voltage Power System (601V to 35kV) | Bus Duct | IsoPhase Bus Duct | 13 KV or gre | AC |  | Electrical conductors, bus, cable, wire
50910 | 3/28/2010 | Challenging |  | Turbine Building | Normal AC Lighting System | Cable/Wiring |  | 4KV | AC |  | Circuit breakers, contactors, motor controllers, manual switches
50911 | 4/18/2010 | Potentially Challenging |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  | Valves, dampers
50912 | 5/5/2010 | Challenging |  | Sewage Treatment | Medium Voltage Power System (601V to 35kV) | Electrical panel | Electric bus bar or bus duct | 4KV | AC |  | Electrical conductors, bus, cable, wire
50913 | 5/12/2010 | Potentially Challenging |  | Turbine Building | Main Generator System | Generator | Main turbine generator |  |  |  | Pipes, fittings, rupture discs
50914 | 6/8/2010 | Potentially Challenging | Main Control Room | Control building | Plant Protection System | Electrical panel | Other instrument/control cabinet |  |  |  | Filters, strainers, screens
50916 | 7/13/2010 | Potentially Challenging | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the main |  |  |  | Annunciator modules, alarms
50917 | 7/13/2010 | Potentially Challenging | N/A | Circulating Water Pump house/ | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 4KV | AC | 1500 | Pumps, eductors
50919 | 8/22/2010 | Undetermined (PC-CH) | N/A | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Pumps, eductors
50921 | 10/11/2010 | Potentially Challenging | Cable vault/tunnel area | Other (specify in comments) | Containment Spray System | Electrical panel | Circuit breaker or other distributio |  |  |  | Circuit breakers, contactors, motor controllers, manual switches
50922 | 11/7/2010 | Challenging |  | Main Transformer or Switch Yar | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors
50923 | 12/19/2010 | Undetermined (NC-PC) | Fuel handling area | Other (Specify in comments) | Electrical panel |  |  | N/A | NA |  | Control board/panel
50925 | 2/8/2011 | Potentially Challenging | N/A | Auxiliary Building (PWR) | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) | N/A | NA |  | Annunciator modules, alarms
50926 | 2/12/2011 | Challenging | Switchgear Room | Other (specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Electric bus bar or bus duct | 480V | AC |  | Transformers, shunt reactors
50928 | 3/23/2011 | Potentially Challenging |  | Control building | No Industry Std. Name for this system | Other |  |  |  |  | Power Tools
50930 | 3/29/2011 | Potentially Challenging | Containment/Drywell | Reactor Building (BWR) | No Industry Std. Name for this system | Other | No breakdown | N/A | NA |  | Vehicle
50931 | 5/1/2011 | Potentially Challenging | N/A | Reactor Building (BWR) | Control Rod Drive System | Electric Motor | MG set | N/A | NA |  | Generators, inverters, motor generators
50935 | 6/7/2011 | Challenging | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Load center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches
50936 | 6/25/2011 | Challenging | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches
50939 | 10/4/2011 | Potentially Challenging |  | Auxiliary Building (PWR) |  | Electrical panel | Inverter | N/A | NA |  | Generators, inverters, motor generators
50942 | 11/1/2011 | Potentially Challenging | Potentially Challenging | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | N/A | NA | 3000 | Motors (electric, hydraulic, pneumatic)
50944 | 11/16/2011 | Potentially Challenging | N/A | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC |  | Valves, dampers
50945 | 12/21/2011 | Potentially Challenging | N/A | Diesel Generator Building |  | Electric heaters |  |  |  |  | Electric heaters
50946 | 1/23/2012 | Potentially Challenging | Containment/Drywell | Containment (PWR) | No Industry Std. Name for this system | Electrical panel | Other instrument/control cabinet |  |  |  | Crane, hoist, or lifting device
50949 | 4/2/2012 | Potentially Challenging | N/A | Auxiliary Building (PWR) | CVC/Makeup and Purification System | Other |  |  |  |  | Pipes, fittings, rupture discs
50950 | 5/21/2012 | Undetermined (PC-CH) | Cable vault/tunnel area | Other (specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring | No breakdown | 13 KV or gre | AC |  | Circuit breakers, contactors, motor controllers, manual switches
50951 | 5/24/2012 | Undetermined (NC-PC) | N/A | Turbine Building | Feedwater System | Junction Boxes | No breakdown |  |  |  | Motors (electric, hydraulic, pneumatic)
50952 | 6/21/2012 | Potentially Challenging | N/A | Turbine Building | Feedwater System | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors
50956 | 10/22/2012 | Challenging | N/A | Service Water Pump house | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 600V | AC |  | Transformers, shunt reactors & Circuit breakers, contactors, motor controllers, manual switches
50968 | 4/18/2012 | Potentially Challenging | N/A | Turbine Building | Hydrogen Supply System | Other |  | N/A | NA |  | Control board/panel
50969 | 11/11/2012 | Challenging | N/A | Main Transformer or Switch Yar | Switchyard System | Transformers | Oil-filled Transformer | : Other (specif | AC | 345 | Transformers, shunt reactors
50977 | 1/8/2013 | Challenging | N/A | Main Transformer or Switch Yar | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors
50982 | 12/20/2010 | Challenging | N/A | Turbine Building | Main Generator Output Power System | Electrical panel | Electric bus bar or bus duct |  |  |  | Generators, inverters, motor generators
50983 | 9/22/2010 | Challenging | N/A | Main Transformer or Switch Yar | Switchyard System | Transformers | Oil-filled Transformer |  |  |  | Transformers, shunt reactors
50985 | 3/26/2012 | Potentially Challenging |  | Turbine Building |  | Other | No breakdown |  |  |  | Waste Bin
50986 | 3/28/2010 | Challenging | N/A | Turbine Building | Feedwater System | Pumps | Turbine-driven pump | N/A | NA |  | Pumps, eductors
50992 | 11/17/2010 | Potentially Challenging | N/A | Service Water Pump house | No Industry Std. Name for this system | Other |  | N/A | NA
50994 | 2/13/2013 | Potentially Challenging | N/A | Turbine Building | No Industry Std. Name for this system | Other | No breakdown | N/A | NA |  | Transient Combustible
51002 | 11/10/2010 | Not Challenging/Undeter | Main Control Room | Control building | Reactor Coolant System | Electrical panel | Main control board (i.e., the main |  |  |  | Motors (electric, hydraulic, pneumatic)
51005 | 4/30/2010 | Potentially Challenging | N/A | Turbine Building | No Industry Std. Name for this system | Other |  | N/A | NA |  | Transient Combustible
51007 | 1/6/2013 | Potentially Challenging |  | Circulating Water Pump house/ | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) |  |  |  | Crane, hoist, or lifting device
51013 | 11/29/2010 | Undetermined (NC-PC) | N/A | Turbine Building | No Industry Std. Name for this system | Other | No breakdown | N/A | NA |  | Transient Combustible
51014 | 3/27/2012 | Undetermined (NC-PC) |  |  | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51026 | 3/30/2010 | Potentially Challenging | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | N/A | NA |  | Blowers, compressors, fans, vacuum pumps, cooling units
51027 | 5/24/2010 | Potentially Challenging |  | Reactor Building (BWR) | Fuel Pool Cooling and Purification System | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors
51032 | 5/2/2010 | Undetermined (NC-PC) |  | Turbine Building | Turbine Lube Oil System | Pumps |  |  |  |  | Motors (electric, hydraulic, pneumatic)
51040 | 4/11/2012 | Challenging |  | Turbine Building | Condensate System | [5 empty] | Heat exchanger, condenser, steam generator
51044 | 3/11/2010 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply Building | Other | No breakdown |  |  |  | Room
51048 | 3/24/2010 | Potentially Challenging |  | Reactor Building (BWR) | [6 empty] | Power Tools
51051 | 4/6/2011 | Undetermined (NC-PC) |  | Turbine Building | Main Turbine System | [5 empty] | Transient Combustible
51057 | 5/2/2011 | Potentially Challenging | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 480V | AC |  | Transformers, shunt reactors
51081 | 12/14/2010 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51082 | 4/4/2011 | Undetermined (NC-PC) |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Power Tools
51085 | 4/27/2012 | Potentially Challenging | Switchgear Room | Turbine Building | DC Power System | Electrical panel | Load center | 250VDC | DC |  | Power Tools
51088 | 4/5/2011 | Potentially Challenging |  | Control building | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators
51090 | 2/15/2013 | Potentially Challenging |  | Circulating Water Pump house/ | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches
51092 | 3/20/2013 | Potentially Challenging |  | Auxiliary Building (PWR) | Aux. Bldg. Environmental Control System | [5 empty] | Instrument controllers
51093 | 1/17/2013 | Challenging |  | Main Transformer or Switch Yar | Switchyard System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors
51109 | 10/15/2010 | Undetermined (NC-PC) |  | Turbine Building | No Industry Std. Name for this system | [5 empty] | Transient Combustible
51111 | 11/2/2010 | Undetermined (NC-PC) |  | Turbine Building | No Industry Std. Name for this system | [5 empty] | Transient Combustible
51113 | 10/5/2010 | Potentially Challenging |  | Circulating Water Pump house/ | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 480V | AC |  | Motors (electric, hydraulic, pneumatic)
51117 | 3/11/2013 | Potentially Challenging |  | Containment (PWR) | No Industry Std. Name for this system | Other | No breakdown | 110V | AC |  | Power Tools
51118 | 4/12/2011 | Potentially Challenging |  | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabinet |  |  |  | 12/31/2011
51125 | 12/31/2011 | Potentially Challenging |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors
51132 | 4/2/2012 | Potentially Challenging |  | Other (specify in comments) | Fuel Pool Cooling and Purification System | Electrical panel | Other (specify in comments) |  |  |  | Pumps, eductors
51135 | 3/12/2013 | Undetermined (NC-PC) |  | Other (specify in comments) | Main/Reheat Steam System | Main/Reheat Steam System | No breakdown |  |  |  | Power Tools
51136 | 1/19/2011 | Potentially Challenging |  | Other (specify in comments) | Fire Detection System | Other | No breakdown |  |  |  | Power Tools
51140 | 11/4/2010 | Potentially Challenging |  | Service Water Pump house |  | Pumps | Diesel driven pumps |  |  |  | Pumps, eductors
51146 | 4/3/2013 | Potentially Challenging |  | Control building | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators
51152 | 4/11/2013 | Challenging |  | Turbine Building, Other (specify |  | Boilers | No breakdown |  |  |  | Floor/roof
51153 | 1/28/2010 | Potentially Challenging |  | Turbine Building | [6 empty] | Transient Combustible
51154 | 8/2/2012 | Potentially Challenging |  | Turbine Building | Hydrogen Supply System | [5 empty] | Valves, dampers
51157 | 9/20/2010 | Undetermined (NC-PC) |  | Other (specify in comments) | Yard Handling and Maintenance System | [5 empty] | Transient Combustible
51158 | 10/4/2012 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51160 | 9/25/2010 | Challenging |  | Other (specify in comments) | Hydrogen Supply System | [5 empty] | Pipes, fittings, rupture discs
51162 | 10/10/2010 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | [5 empty] | Transient Combustible
51164 | 9/19/2011 | Undetermined (NC-PC) |  | Turbine Building | Yard Handling and Maintenance System | Yard Handling and Maintenance System | No breakdown |  |  |  | Transient Combustible
51166 | 6/10/2012 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51168 | 12/3/2012 | Undetermined (NC-PC) |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51171 | 7/13/2012 | Potentially Challenging |  | Auxiliary Building (PWR) | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51172 | 3/21/2013 | Potentially Challenging |  | Turbine Building | Condensate System | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches
51176 | 5/4/2013 | Potentially Challenging |  | Reactor Building (BWR) | Control Rod Drive System | Pumps | Electric motor driven pumps |  |  |  | Governors, couplings, gear boxes
51180 | 5/16/2010 | Potentially Challenging |  | Auxiliary Building (PWR) | Yard Handling and Maintenance System | Electrical panel | Other instrument/control cabinet |  |  |  | Transient Combustible
51181 | 9/14/2010 | Potentially Challenging |  | Turbine Building | DC Power System | Outlets |  |  |  |  | Batteries, battery chargers
51184 | 12/2/2011 | 12/2/2011 |  | Turbine Building
51186 | 4/20/2013 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible
51187 | 4/17/2013 | Challenging |  | Main Transformer or Switch Yar | Main Generator Output Power System | Transformers |  | 13 KV or gre | AC |  | Transformers, shunt reactors
51188 | 5/20/2013 | Undetermined (PC-CH) |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors
51190 | 4/2/2012 | Potentially Challenging | Battery Room | Battery Room | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators
51191 | 4/27/2013 | Potentially Challenging |  | Turbine Building |  | Generator | Main turbine generator |  |  |  | Transient Combustible
51193 | 5/21/2013 | Potentially Challenging |  | Radwaste Building | Administration Building | Other | No breakdown |  |  |  | Transient Combustible
51194 | 7/2/2013 | Challenging |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Electric bus bar or bus duct | 13 KV or gre | AC |  | Circuit breakers, contactors, motor controllers, manual switches
51196 | 7/11/2013 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators
51199 | 7/26/2013 | Challenging |  | Main Transformer or Switch Yar | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Generators, inverters, motor generators
51201 | 2013-08-08 | Challenging |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) |  |  | 480V | AC |  | Transformers, shunt reactors
51207 | 9/2/2013 | Potentially Challenging |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Turbines (steam, gas)
51209 | 7/31/2013 | Undetermined (NC-PC) |  | Main Transformer or Switch Yar | Medium Voltage Power System (601V to 35kV) | Electrical panel | Other (specify in comments) | 110V | AC |  | Transformers, shunt reactors
51216 | 1/3/2010 | Potentially Challenging |  | Circulating Water Pump house/ |  | Electrical panel | Other instrument/control cabinet |  |  |  | Bistable, switch (mechanical, electronic)
51219 | 2/12/2010 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators
51220 | 3/26/2010 | Undetermined (NC-PC) |  | Turbine Building | No Industry Std. Name for this system | Other |  |  |  |  | Electric heaters
51221 | 7/20/2011 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Engines (gas, diesel)
51222 | 10/12/2011 | Challenging | Cable vault/tunnel area | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  |  |  |  | Electrical conductors, bus, cable, wire
51231 | 4/7/2014 | Undetermined (NC-PC) |  | Other (specify in comments) | Yard Handling and Maintenance System | Other |  |  |  |  | Vehicle
51254 | 10/13/2012 | Potentially Challenging |  | Turbine Building | Aux. Bldg. Environmental Control System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic)
51256 | 6/13/2013 | Undetermined (NC-PC) | Switchgear Room | Reactor Building (BWR) | Medium Voltage Power System, Class 1E | Electrical panel | Switchgear |  |  |  | Circuit breakers, contactors, motor controllers, manual switches
51257 | 5/16/2011 | Potentially Challenging | Switchgear Room |  | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  | Circuit breakers, contactors, motor controllers, manual switches
51258 | 7/10/2013 | Challenging |  | Turbine Building | No Industry Std. Name for this system | Lighting Ballasts |  |  |  |  | Illumination source
51265 | 8/24/2012 | Potentially Challenging | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  |  |  |  | Electrical conductors, bus, cable, wire
51273 | 4/2/2013 | Undetermined (NC-PC) |  | Main Transformer or Switch Yar | Medium Voltage Power System (601V to 35kV) | Transformers |  |  |  |  | Transformers, shunt reactors
51274 | 12/9/2012 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Load center |  |  |  | 21
51276 | 8/14/2013 | Potentially Challenging | Fuel handling area | Reactor Building (BWR) | [6 empty] | Reactor Building (BWR)
51278 | 11/5/2013 | Challenging |  | Challenging | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 4KV | AC |  | Electrical conductors, bus, cable, wire
51280 | 12/21/2014 | Potentially Challenging |  | Circulating Water Pump house/ |  | Pumps |  |  |  |  | Electric heaters
51287 | 10/6/2013 | Potentially Challenging |  | Main Transformer or Switch Yar | Switchyard System | Electrical panel | Other (specify in comments) |  |  |  | Control board/panel
51289 | 10/26/2013 | Potentially Challenging |  | Circulating Water Pump house/ | [6 empty] | Electric heaters
51291 | 12/9/2013 | Challenging |  | Turbine Building | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Potential | 7KV | AC |  | Transformers, shunt reactors
51293 | 11/6/2013 | Potentially Challenging |  | Turbine Building | [6 empty] | Room
51295 | 11/1/2013 | Potentially Challenging |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Transient Combustible
51296 | 11/30/2013 | Potentially Challenging |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic)
51304 | 1/18/2014 | Potentially Challenging |  | Auxiliary Building (PWR) |  | Electrical panel | Inverter | 250VDC | DC | 50 | Generators, inverters, motor generators
51308 | 4/7/2012 | Potentially Challenging |  | Reactor Building (BWR) |  | Other |  |  |  |  | Crane, hoist, or lifting device
51309 | 3/7/2014 | Potentially Challenging |  | Warehouse |  | Electrical panel | Load center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches
51310 | 4/17/2014 | Potentially Challenging |  | Turbine Building | Yard Handling and Maintenance System | Other |  |  |  |  | Transient Combustible
51315 | 3/20/2014 | Potentially Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators
51316 | 4/12/2014 | Potentially Challenging |  | Containment (PWR) | No Industry Std. Name for this system | Other |  |  |  |  | Power Tools
51317 | 4/2/2014 | Challenging |  | Turbine Building | Instrument and Uninterruptible Power System | Cable/Wiring |  |  |  |  | Pipes, fittings, rupture discs
51318 | 4/3/2014 | Potentially Challenging |  | Main Transformer or Switch Yar | Low Voltage Power System (600V and less) | Other |  | 480V | AC |  | Electronic power supply
51322 | 6/19/2014 | Undetermined (NC-PC) |  | Diesel Generator Building | No Industry Std. Name for this system | Other |  |  |  |  | Crane, hoist, or lifting device
51324 | 5/23/2014 | Potentially Challenging |  | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Inverter |  |  |  | Transformers, shunt reactors
51328 | 7/27/2014 | Potentially Challenging |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic)
51331 | 9/4/2014 | Potentially Challenging |  | Diesel Generator Building |  | Electrical panel | Other (specify in comments) |  |  |  | Control board/panel
51332 | 10/6/2014 | Challenging |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabinet |  |  |  | Control board/panel
51335 | 9/15/2014 | Potentially Challenging |  | Other (specify in comments) | No Industry Std. Name for this system | Other |  |  |  |  | Manual Tools
51339 | 9/28/2014 | Potentially Challenging |  | Other (specify in comments) | Containment Spray System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic)
51354 | 3/28/2010 | Potentially Challenging |  | Turbine Building |  | Pumps | Electric motor driven pumps | 4KV | AC |  | Motors (electric, hydraulic, pneumatic)
51366 | 4/21/2010 | Potentially Challenging |  | Containment (PWR) |  | Other |  |  |  |  | Circuit breakers, contactors, motor controllers, manual switches
51374 | 3/1/2014 | Undetermined (NC-PC) |  | Reactor Building (BWR) | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) |  |  |  | Electronic power supply
51377 | 12/12/2013 | Potentially Challenging |  | Other (specify in comments) | Aux. Bldg. Environmental Control System | Electrical panel | Motor control center | 4KV | AC |  | Blowers, compressors, fans, vacuum pumps, cooling units

## Fire Event Attributes
FireID | Event Date_FEA | Disposition_FEA | Fire Cause | Fire Type | Combustible Group | Type | Form | Temperature | Smoke | Damage Extent | Collateral Damage | Collateral Damage | Feet Above | Feet Laterally | Collateral Description | Suppression Effects | Evidence of secondary ignition | Smoke | Heat Damage
50907 | 1/9/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component |  | Lube Oil or Grease | Contained within component |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished
50908 | 1/20/2010 | Challenging | Mechanical equipment malfunction/failure | Flaming combustion – internal to component |  |  |  |  | Outside area, smoke only in fire plume | Confined to room of origin |  |  | 10 | 10 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal Damage was limited t | 0 ft Vertical, 0 ft Horizontal | 10 ft vertical 10 ft horizontal Damage was limited | 2 ft vertical 2 ft horizontal Fuel Supply - Lube O
50909 | 3/7/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Explosion | Insulation | Type not specified | Single Cable Tray |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50910 | 3/28/2010 | Challenging | High Energy Arc Fault (HEAF) | Arc/electric discharge | In-Situ | Other electrical or electronic equipment | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to structure of origin |  |  | 25 | 25 | 25 ft Vertical, 25 ft Horizontal extinguishment | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal spacial separation | 25 ft vertical 25 ft horizontal extinguishment | 25 ft vertical 25 ft horizontal extinguishment
50911 | 4/18/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – external to component | Liquid | Lube Oil or grease |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 |  | 3 | 3
50912 | 5/5/2010 | Challenging | Electrical arcing or sparks (non-HEAF) |  | Gas | Hydrogen | Ambient pressure, within a component |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50913 | 5/12/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – external to component | Gas | Hydrogen | Jet from a pressurized source |  | No smoke present | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50914 | 6/8/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire was extinguished promptly. | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe
50916 | 7/13/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50917 | 7/13/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50919 | 8/22/2010 | Undetermined (PC-CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | In-Situ | Thermal insulation materials | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal The fire was extinguished using a dry chemical extinguisher and | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Proper fire fighting | 0 ft vertical 0 ft horizontal The fire was extingu
50921 | 10/11/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage due to fire. | 0 ft vertical 0 ft horizontal Fire was promptly ex | 0 ft vertical 0 ft horizontal No evidence of secon | 0 ft vertical 0 ft horizontal No smoke damage | 0 ft vertical 0 ft horizontal Fire was extinguishe
50922 | 11/7/2010 | Challenging | High Energy Arc Fault (HEAF) | Explosion | Liquid | Transformer Oil | Contained within component |  | Outside area, smoke only in fire plume | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50923 | 12/19/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal Power to the heater | 0 ft vertical 0 ft horizontal No suppression was u | 0 ft vertical 0 ft horizontal There was no evidenc | 1 ft vertical 1 ft horizontal Power to the heater | 1 ft vertical 1 ft horizontal Power to the heater
50925 | 2/8/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Type not specified | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal Suppression via CO2, | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal The Unit 1 Equipment
50926 | 2/12/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | Explosion | In-Situ | Other electrical or electronic equipment |  |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 20 | 20 | 5 ft vertical 2 ft horizontal Phase to phase fault | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 20 ft vertical 20 ft horizontal Smoke affected the | 5 ft vertical 2 ft horizontal When the metallic bu
50928 | 3/23/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Transient | Temporary electrical wiring or equipment |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50930 | 3/29/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Transient | Temporary electrical wiring or equipment |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0.4 | 0.4 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0.4 ft vertical 0.4 ft horizontal Quick detection
50931 | 5/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – internal to component |  | Other electrical or electronic equipment | NA | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50935 | 6/7/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge |  | Other electrical or electronic equipment | NA |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 12 | 12 | 3 ft vertical 3 ft horizontal Deenergized electric | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12 ft vertical 12 ft horizontal Cabinets and suppr | 6 ft vertical 6 ft horizontal Deenergized electric
50936 | 6/25/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In-Situ | Type not specified | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | Yes collateral damage occurred | Yes | 4 | 2 | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal THE AREA EFFECTED BY | 0 ft vertical 0 ft horizontal | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE
50939 | 10/4/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50942 | 11/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure | Other (specify) | Liquid | Lube Oil or grease |  |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Separation distance | 0 ft vertical 0 ft horizontal None. No suppression | 0 ft vertical 0 ft horizontal None. | 0 ft vertical 0 ft horizontal Smoke spread from lo | 0 ft vertical 0 ft horizontal Design of motor bear
50944 | 11/16/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50945 | 12/21/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component |  | Type not specified | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 1 | 2 | 0 ft vertical 0 ft horizontal Fire extinguished wi | 0 ft vertical 0 ft horizontal Suppression system d | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal Very light smoke, no | 1 ft vertical 2 ft horizontal Fire extinguished wi
50946 | 1/23/2012 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge |  | Cellulosic materials including wood, paper or ot | NA, Insulation Multiple Bundles |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal steel cabinet | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal steel cabinet
50949 | 4/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component |  | Hydrogen | Jet from a pressurized source | Outside area, elevated temperatures only in the fire plume | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50950 | 5/21/2012 | Undetermined (PC-CH) | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | Insulation | Thermoset | Single Cable |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 1 | 3 | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Three CO2 extinguish | 0 ft vertical 0 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Fault occurred in an | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w
50951 | 5/24/2012 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Arc/electric discharge | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 5 | 3 | 5 ft vertical 3 ft horizontal Electrical fault occ | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 5 ft vertical 3 ft horizontal Electrical fault occ | 5 ft vertical 3 ft horizontal Electrical fault occ
50952 | 6/21/2012 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Fire not observed and fire type indeterminate from post-inspection | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal Insulation was the o | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Detection and dispat
50956 | 10/22/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 | 3 ft vertical 3 ft horizontal Design of the electr | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal Design of the electr | 1 ft vertical 1 ft horizontal Design of the electr
50968 | 4/18/2012 | Potentially Challenging | Personnel error during test and maintenance activity | Flaming combustion – external to component | Gas | Hydrogen | Jet from a pressurized source |  | No smoke present | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50969 | 11/11/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | Explosion | In-Situ | Other electrical or electronic equipment | Ambient pressure, within a component | Outside area, elevated temperatures only in the fire plume | Outside area, smoke only in fire plume | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50977 | 1/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Explosion | Liquid | Transformer Oil | Contained within |  | Outside area, smoke only in fire plume | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 40 | 0 | 40 ft vertical 0 ft horizontal Exterior fire | 0 ft vertical 0 ft horizontal None, due to suppres | 0 ft vertical 0 ft horizontal Contained at the tra | 0 ft vertical 0 ft horizontal No smoke damage | 40 ft vertical 0 ft horizontal Exterior Fire
50982 | 12/20/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Gas | Hydrogen | Jet from a pressurized source |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None
50983 | 9/22/2010 | Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | In-Situ | Other (specify) |  |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire team putting ou | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal Fire team putting ou
50985 | 3/26/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown | Transient | Temporary electrical wiring or equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50986 | 3/28/2010 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – external to component | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50992 | 11/17/2010 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Transient | Trash (i.e., solid refuse collected for disposal) |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
50994 | 2/13/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Gas | Acetylene | NA | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51002 | 11/10/2010 | Not Challenging/Undeter | Personnel error during test and maintenance activity | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51005 | 4/30/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – internal to component | Transient | Temporary electrical wiring or equipment |  | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal No physical suppress | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal The Air Arc Machine
51007 | 1/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51013 | 11/29/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Arc/electric discharge |  | Other electrical or electronic equipment |  |  | Unknown | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51014 | 3/27/2012 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Unknown | Transient | Temporary electrical wiring or equipment |  |  | Unknown | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51026 | 3/30/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – external to component | In Situ | Other (specify) |  |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 10 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal | 1 ft vertical 1 ft horizontal
51027 | 5/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Insulation | Type not specified | Other (Specify | Unknown | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51032 | 5/2/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In Situ | Other (specify) |  |  | Unknown | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The motor casing con | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51040 | 4/11/2012 | Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  |  |  | Unknown | Confined to part of room or area of origin |  |  | 30 | 10 | 30 ft vertical 10 ft horizontal Acetylene/oxygen b | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Contained mostly ins | 30 ft vertical 10 ft horizontal Damage was limited
51044 | 3/11/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | Liquid | Fuel Oil |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51048 | 3/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Transient |  |  |  | Unknown | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51051 | 4/6/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Unknown | Transient | Other (specify) |  |  | Unknown | Unknown | Unknown | Unknown | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51057 | 5/2/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment | NA | None or insignificant – temperature at or close to ambient | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Fire confined to tra
51081 | 12/14/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Transient | Other (specify) | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51082 | 4/4/2011 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment | NA |  | No smoke present | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51085 | 4/27/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51088 | 4/5/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment |  |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51090 | 2/15/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51092 | 3/20/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Insulation | Type not specified | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51093 | 1/17/2013 | Challenging | Unknown | Explosion | Liquid | Transformer Oil | Contained within component |  | Outside area, smoke only in fire plume | Confined to part of room or area of origin |  |  | 0 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 10 ft horizontal Off site fire depar | 0 ft vertical 0 ft horizontal
51109 | 10/15/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Smoldering combustion – internal to component | Transient | Cellulosic materials including wood, paper or ot |  |  | Unknown | Confined to the object of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51111 | 11/2/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) |  | Transient | Other (specify) |  |  | Unknown | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51113 | 10/5/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | Liquid | Lube Oil or grease | Contained within |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51117 | 3/11/2013 | Potentially Challenging | Personnel error during test and maintenance activity | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51118 | 4/12/2011 | Potentially Challenging |  | Flaming combustion – external to component | In-Situ | Other electrical or electronic equipment |  |  | Unknown | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51125 | 12/31/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | In-Situ | Other (specify) |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51132 | 4/2/2012 | Potentially Challenging | Unknown | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal De-energized compone | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51135 | 3/12/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Smoldering combustion – internal to component | nsulation | Type not specified | Single Cable |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51136 | 1/19/2011 | Potentially Challenging |  |  | Transient | Temporary electrical wiring or equipment | Single Cable |  | Outside area, smoke only in fire plume | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal isolated location | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51140 | 11/4/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – external to component | Liquid | Lube Oil or grease | Leak - Oil soaked |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51146 | 4/3/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Thermal insulation materials | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Distance of transfor | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No smoke damage. | 0 ft vertical 0.3 ft horizontal Cabinet wall paint
51152 | 4/11/2013 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – external to component | In-Situ | Other (specify) | NA |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 12 | 5 ft vertical 8 ft horizontal Fire Brigade respons | 30 ft vertical 0 ft horizontal Ground floor floor | 0 ft vertical 2 ft horizontal configuration and lo | 0 ft vertical 0 ft horizontal Origin of fire was o | 8 ft vertical 12 ft horizontal Fire Brigade respon
51153 | 1/28/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Transient | Cellulosic materials including wood, paper or ot |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51154 | 8/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – external to component | Gas | Hydrogen | Jet from a pressurized source |  | No smoke present | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51157 | 9/20/2010 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Transient | Cellulosic materials including wood, paper or ot |  |  | Outside area, smoke only in fire plume | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51158 | 10/4/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – internal to component | Transient | Other (specify) |  | None or insignificant – temperature at or close to ambient | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51160 | 9/25/2010 | Challenging | Mechanical equipment malfunction/failure | Flaming combustion – external to component | Gas | Hydrogen | Ambient pressure, within a compartment |  | Outside area, smoke only in fire plume | Confined to part of room or area of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51162 | 10/10/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | In-Situ | Thermal insulation materials |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51164 | 9/19/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) |  | Transient | Other (specify) | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51166 | 6/10/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Transient | Other Transient Combustible (specify) | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51168 | 12/3/2012 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Transient | Cellulosic materials including wood, paper or ot | NA |  | Very light smoke (detectable odor no visibility reduction) | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51171 | 7/13/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51172 | 3/21/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51176 | 5/4/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – internal to component | Liquid | Lube Oil or Grease | Contained within reservoir |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51180 | 5/16/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other (specify) | NA |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished
51181 | 9/14/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Arc/electric discharge | In-Situ | Other electrical or electronic equipment |  |  | No smoke present | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51184 | 12/2/2011 | 12/2/2011 | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | In-Situ | Structural component |  |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51186 | 4/20/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Gas | Other (specify) | Other (specify) |  | Very light smoke (detectable odor no visibility reduction) | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51187 | 4/17/2013 | Challenging | High Energy Arc Fault (HEAF) | Arc/electric discharge | Liquid | Transformer Oil | Contained within component |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 1 | 2 | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 2 ft horizontal Suppression was conc | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 1 ft horizontal The fire was outside | 1 ft vertical 2 ft horizontal Cable was charred, b
51188 | 5/20/2013 | Undetermined (PC-CH) | Mechanical equipment malfunction/failure | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment | NA |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished.
51190 | 4/2/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51191 | 4/27/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – internal to component | Liquid | Transformer Oil | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51193 | 5/21/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Liquid | Other (specify) | Other (specify) |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51194 | 7/2/2013 | Challenging | High Energy Arc Fault (HEAF) | Arc/electric discharge | In-Situ | Interior finish | NA |  | No smoke present | Confined to the object of origin (broad/extensive damage) | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51196 | 7/11/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51199 | 7/26/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | In-Situ | Other electrical or electronic equipment | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 20 | 30 ft vertical 20 ft horizontal The arc flash thre | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal The arc flash threw | 30 ft vertical 20 ft horizontal Smoke was moderate | 30 ft vertical 20 ft horizontal The arc flash thre
51201 | : 8/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (broad/extensive damage) |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Damage was confined | 0 ft vertical 0 ft horizontal Damage was confined
51207 | 9/2/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – external to component | Liquid | Lube Oil or grease | Contained within component |  | Unknown | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51209 | 7/31/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Fire not observed and fire type indeterminate from post-inspection | In-Situ | Other (specify) | NA |  | No smoke present | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
51216 | 1/3/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No
51219 | 2/12/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51220 | 3/26/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – internal to component | Transient | Temporary thermal insulation materials |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51221 | 7/20/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Flaming combustion – internal to component | In-Situ | Thermal insulation materials |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51222 | 10/12/2011 | Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Thermal insulation materials |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51231 | 4/7/2014 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Transient | Other (Specify) | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 3 | 3 | 2 ft Vertical, 2 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 2 ft Vertical, 2 ft Horizontal | 3 ft Vertical, 3 ft Horizontal
51254 | 10/13/2012 | Potentially Challenging |  | Fire not observed and fire type indeterminate from post-inspection | In-Situ | Thermal insulation materials |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Small fire involving motor windings no damage to other compo | 0 ft Vertical, 0 ft Horizontal Suppressed by opening breaker, no other actions required | 0 ft Vertical, 0 ft Horizontal No secondary ignition noted | 0 ft Vertical, 0 ft Horizontal Light smoke produced, ventilation in turbine building | 0 ft Vertical, 0 ft Horizontal No adjacent components exposed to heat.
51256 | 6/13/2013 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In-Situ | Other electrical or electronic equipment | NA |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51257 | 5/16/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  |  | Unknown | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51258 | 7/10/2013 | Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | In-Situ | Other electrical or electronic equipment | Type not specified |  | No smoke present | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51265 | 8/24/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51273 | 4/2/2013 | Undetermined (NC-PC) | Human Error | Arc/electric discharge | Transient | Temporary electrical wiring or equipment | NA |  | No smoke present | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 5 | 5 | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal No suppression required. Fire self-extinguished with loss of po | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h
51274 | 12/9/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Fire not observed and fire type indeterminate from post-inspection | In-Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51276 | 8/14/2013 | Potentially Challenging | Human Error | Explosion | Gas | Hydrogen | Ambient pressure, within a compartment |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51278 | 11/5/2013 | Challenging | Electrical failure resulting in overheating materials | Arc/electric discharge | Insulation | Cable Tray Stack | Type not specified |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | Vertical Distance (ft): 3.00 | Vertical Distance (ft): 3.00 | Damage limited to |  |  | Vertical Distance (ft): 7.00; Horizontal Distance (ft): 80.00 | Vertical Distance (ft): 3.00; Horizontal Distance (ft): 5.0
51280 | 12/21/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Liquid | Lube Oil or Grease | Other (specify) |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51287 | 10/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51289 | 10/26/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – external to component | In-Situ | Thermal insulation materials | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire.
51291 | 12/9/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | In-Situ | Other electrical or electronic equipment | NA |  | Outside area, smoke only in fire plume | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 50 | 20 | 50 ft Vertical, 20 ft Horizontal Transformer fire outdoors, concrete separation walls betwe | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51293 | 11/6/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Flaming combustion – external to component | Transient | Trash (i.e., solid refuse collected for disposal) | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti
51295 | 11/1/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – external to component | Liquid | Other (specify) | Leak - Oil soaked Insulation |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51296 | 11/30/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51304 | 1/18/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Fire not observed and fire type indeterminate from post-inspection | In Situ | Thermal insulation materials | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. no secondary i | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. No damage be
51308 | 4/7/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51309 | 3/7/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – internal to component | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51310 | 4/17/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment |  |  | No smoke present | Confined to the object of origin (localized/single subcomponent) | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51315 | 3/20/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Flaming combustion – internal to component | Liquid | Lube Oil or Grease | Other (specify) |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51316 | 4/12/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | In Situ | Other electrical or electronic equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51317 | 4/2/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | Insulation | Single Cable Tray | Type not specified |  | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil | Confined to part of room or area of origin | -1 | -1 | 10 | 10 | 2 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 2 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 10 ft Vertical, 10 ft Horizontal fire suppression equipment put out fire quickly to prevent fu | 4 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth
51318 | 4/3/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal The 480VAC connector was located outside of the building. All | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w
51322 | 6/19/2014 | Undetermined (NC-PC) |  | Flaming combustion – internal to component | Transient | Other (specify) |  |  | No smoke present | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51324 | 5/23/2014 | Potentially Challenging | Electrical failure resulting in overheating materials |  | In Situ | Other electrical or electronic equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | -1 | -1 | 1 | 1 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 1 ft Horizontal Quick Fire brigade response. | 0.25 ft Vertical, 0 ft Horizontal Fire was limited to inside of the 3KI inverter. The metal cabi
51328 | 7/27/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Fire not observed and fire type indeterminate from post-inspection | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51331 | 9/4/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da
51332 | 10/6/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – external to component | In Situ | Other electrical or electronic equipment | NA |  | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire | Confined to part of room or area of origin | -1 | -1 | 8 | 3 | 1 ft Vertical, 1 ft Horizontal Fire immediately extinguished by site operator in room with po | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 8 ft Vertical, 3 ft Horizontal Fire initiated in closed electrical component control cabinet. S | 2 ft Vertical, 2 ft Horizontal Fire immediately extinguished by site operator in room with po
51335 | 9/15/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment | Type not specified |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord
51339 | 9/28/2014 | Potentially Challenging | Mechanical equipment malfunction/failure | Flaming combustion – external to component | Liquid | Lube Oil or Grease | Contained within component |  | Very light smoke (detectable odor no visibility reduction) | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off
51354 | 3/28/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to object of origin (component) do not result in flames or heat output external to the comp | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51366 | 4/21/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – external to component | Transient | Temporary electrical wiring or equipment |  |  | Very light smoke (detectable odor no visibility reduction) | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51374 | 3/1/2014 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Arc/electric discharge | Transient | Temporary electrical wiring or equipment | NA |  | Very light smoke (detectable odor no visibility reduction) | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
51377 | 12/12/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Flaming combustion – internal to component | In-Situ | Other electrical or electronic equipment | NA |  | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal

## Fire Severity Evaluation
FireID | Event Date_FSE | Disposition_FSE | Override | Comment on Disposition | Automatic Determination | Automatic Determination Basis
50907 | 1/9/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50908 | 1/20/2010 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage.Potentially Challenging Criteria:Fire Type, Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50909 | 3/7/2010 | Challenging |  | Agree with challenging fire classification - however this is a weather-induced event further complicated by the condition of the cracked noryl insulation. | Challenging | Challenging Criteria: Fire Type,Potentially Challenging Criteria:Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline:No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50910 | 3/28/2010 | Challenging |  |  | Challenging | Challenging Criteria: Ignition Factor Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50911 | 4/18/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Ignition Factor Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50912 | 5/5/2010 | Challenging |  |  | Challenging | Challenging Criteria: Detection Method Suppression Method Potentially Challenging Criteria: First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50913 | 5/12/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50914 | 6/8/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50916 | 7/13/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
50917 | 7/13/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50919 | 8/22/2010 | Undetermined (PC-CH) |  |  | Challenging | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50921 | 10/11/2010 | Potentially Challenging | Other | Determined to be PC from event writeup | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50922 | 11/7/2010 | Challenging |  |  | Challenging | Challenging Criteria: Ignition Factor Fire Type Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50923 | 12/19/2010 | Undetermined (NC-PC) |  | Does not appear to be active fire, only smoke. U(NC-PC) because of multiple mentions of fire and active suppression, removing power. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
50925 | 2/8/2011 | Potentially Challenging |  | Meets PC criteria OB3 (Page B-3 of EPRI 1025284) for damage beyond initial circuit card as the two adjacent cards were damaged | Potentially Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50926 | 2/12/2011 | Challenging |  |  | Challenging | Challenging Criteria: Fire Type Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50928 | 3/23/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50930 | 3/29/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50931 | 5/1/2011 | Potentially Challenging |  | Some uncertainity exists in classification if active intervention was involved "after securing the MG set the fire extinguished without applying any fire suppresant" | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50935 | 6/7/2011 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50936 | 6/25/2011 | Challenging |  |  | Challenging | Challenging Criteria: Collateral Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50939 | 10/4/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50942 | 11/1/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Smoldering Fire with Moderate Smoke or Temperature Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: Timeline uses known values: 631 minutes Not Challenging Evaluation:
50944 | 11/16/2011 | Potentially Challenging | Other | Flash seen coming from motor control center. Listed fire type as arc/electrical discharge as that is what was observed. This may have defaulted to a NC, although appears this event is at least PC. | NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: No criteria met
50945 | 12/21/2011 | Potentially Challenging |  | Does not meet T&M override because timeline is greater than 5 minutes. This was complicated by a screw lodged in the starter preventing the contacts from opening. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50946 | 1/23/2012 | Potentially Challenging | Other | There was electrical discharge which resulted in soot deposits and damage internal to cabinet, but self extinguished. Fire was self extinguished, but there was evidence of arcing and tentatively screened in. There are pictures in the cause analysis. | NC | No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
50949 | 4/2/2012 | Potentially Challenging | Other | 3" flame in outside environment. Likely PC (not CH) | Challenging | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
50950 | 5/21/2012 | Undetermined (PC-CH) |  |  | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Collateral Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Heavy Smoke Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50951 | 5/24/2012 | Undetermined (NC-PC) |  |  | Challenging | Challenging Criteria: Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50952 | 6/21/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50956 | 10/22/2012 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50968 | 4/18/2012 | Potentially Challenging |  | Agree with PC. Fire was self extinguished but a significant flame of 4-6 feet was observed and had the potential to cause damage if secondary combustibles were nearby. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50969 | 11/11/2012 | Challenging |  |  | Challenging | Challenging Criteria: Fire Type Suppression Method Potentially Challenging Criteria: Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50977 | 1/8/2013 | Challenging |  |  | Challenging | Challenging Criteria: Fire Type Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50982 | 12/20/2010 | Challenging |  | Challenging, but likely does not fit into an PRA bin. | Challenging | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50983 | 9/22/2010 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50985 | 3/26/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
50986 | 3/28/2010 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- >=10 minutes Suppression Method Potentially Challenging Criteria: Fire Type Fire Suppression Method Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
50992 | 11/17/2010 | Potentially Challenging |  | Left as PC, but classification hinges on the fire type | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
50994 | 2/13/2013 | Potentially Challenging | Other | Flame observed with personnel injury/burns. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
51002 | 11/10/2010 | Not Challenging/Undeter | Test and Maintenance | Maintenance Activity Override for at power conditions- Reactor was in Mode 5 undergoing maintenance on a system required for power operations. Reactor coolant pump handswitch began to flame (candle size) when it was switched into the on position during PMT. The flame self extinguished or was blown out by operator in attendance and was limited to the switch. Switch is located on the main control board in the control room. The fire was due to a wiring error during maintenance. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
51005 | 4/30/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
51007 | 1/6/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51013 | 11/29/2010 | Undetermined (NC-PC) |  | Overrode severity algorithm as there was observed arcing "the collection of debris caused an arc to develop. The debris flashed and burnt rapidly and the fire was self extinguished" which is consistent with EPRI 1025284 Page 5-6 for exclusions for self-extinguished fires. This was a welding/grinding fire that caused a junction box arc. | NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
51014 | 3/27/2012 | Undetermined (NC-PC) |  |  | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51026 | 3/30/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51027 | 5/24/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51032 | 5/2/2010 | Undetermined (NC-PC) |  | Not clear this was a fire or pump internal arcing fault that stopped when pump tripped. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51040 | 4/11/2012 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51044 | 3/11/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51048 | 3/24/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51051 | 4/6/2011 | Undetermined (NC-PC) |  |  | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51057 | 5/2/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51081 | 12/14/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51082 | 4/4/2011 | Undetermined (NC-PC) |  | Fire was apparently small, of unknown duration, and suppression method. May have self suppressed. Otherwise could be considered PC. | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51085 | 4/27/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51088 | 4/5/2011 | Potentially Challenging |  | PC since fixed fire suppression system actuated. Appears fire limited to T&M period since PMT resulted in fire due to wiring error. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51090 | 2/15/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51092 | 3/20/2013 | Potentially Challenging |  | UE, fire in the auxiliary building supply HVAC unit. A supply unit heater was operating outside of its intended design. Smoke detector activated the pre-action feature of the fixed suppression system but the sprinklers did not heat up enough to discharge. The fire self-extinguished when the unit was de-energized by a plant worker. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51093 | 1/17/2013 | Challenging |  | Located outside the PA, but in the switchyard. | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Fire Type Extent of Fire Damage Suppression Method Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51109 | 10/15/2010 | Undetermined (NC-PC) |  | Many fire event details missing, although fire appears insignificant and unlikely to be of any risk signficance. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51111 | 11/2/2010 | Undetermined (NC-PC) |  |  | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51113 | 10/5/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51117 | 3/11/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation:
51118 | 4/12/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: Timeline uses known values: 4 minutes Not Challenging Evaluation:
51125 | 12/31/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51132 | 4/2/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51135 | 3/12/2013 | Undetermined (NC-PC) |  |  | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51136 | 1/19/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51140 | 11/4/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51146 | 4/3/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: Timeline uses known values: 20 minutes Not Challenging Evaluation:
51152 | 4/11/2013 | Challenging |  | This is a larger roof fire and associated with the auxiliary boiler building. Might be risk signficant. | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51153 | 1/28/2010 | Potentially Challenging |  | Potentially Challenging | This event involved poor housekeeping and was limited by the amount of transient combustible material, but could have been worse if additional materials were ignited. Took 9 minutes to extiguish, so PC not HW override seems appropriate. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51154 | 8/2/2012 | Potentially Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Potentially Challenging Criteria: Fire Type First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51157 | 9/20/2010 | Undetermined (NC-PC) | Outside Protected Are | Generally cigarette butt fires in designated areas are NC. This is not a designated smoking area or butt can fire, but an "inappropriately discarded cigarette butt" per the report. Since the magnitude,and actual location are inconsequntial from a risk perspective, it was classified as Undetermined, i.e. it could be treated as PC or NC. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51158 | 10/4/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation:
51160 | 9/25/2010 | Challenging |  | The location of the fire was not risk signficant, but the fire itself was fairly extensive, although easily extinguished without collateral damage to the area. It could have been more problematic if fire was located elsewhere, therefore CH classification is appropriate. | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51162 | 10/10/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51164 | 9/19/2011 | Undetermined (NC-PC) |  | Probable event classifications: 9/19/2011 - NC (proposed) or U 9/20/2011 - PC (proposed) or U 9/20/2011 - NC (proposed) or U 9/23/2011 - NC (proposed) or U | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51166 | 6/10/2012 | Potentially Challenging | Hot Work | No fire watch was stationed at the location, although fire watch did observe the fire and extinguish it. Also, fire produced flames 1-2 ft high which are relatively large for a hot work override to apply. | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51168 | 12/3/2012 | Undetermined (NC-PC) | Hot Work | Appears to have been hot work error and roving fire watch detected fire, so hot work override does not apply. U(NC-PC) due to uncertainty about fire watch, | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51171 | 7/13/2012 | Potentially Challenging | Other | Flaming combustion external to initiating component and fire damage to nearby combustibles; but was apparently self limited in extent (cords, bucket, light stick). The employee who detected the fire notified the fire brigade and then extinguished the fire. | Challenging | Challenging Criteria: Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51172 | 3/21/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51176 | 5/4/2013 | Potentially Challenging |  | May also be considered as NC since fire self extinguished after about 7 minutes. However, not clear if pump was turned off before self-extinguished. Also, flame was small (candle flame). | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51180 | 5/16/2010 | Potentially Challenging |  | This is a small and inconsequential fire that seems to have very limited potential to propagate. However, it does not appear to meet any override criteria. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51181 | 9/14/2010 | Potentially Challenging | Other | Battery was discovered arcing to a metal wall and giving off fumes. Battery charger was de-energized. Fire brigade stopped the arcing with a dry chemical extinguisher and moved the battery away from the wall. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51184 | 12/2/2011 | 12/2/2011 | Hot Work | Hor work crew failed to follow area work prep requirements; unknown fire duration, unknown fire suppression. Because the fire was in the roof, it may be considered for NC by location. | Potentially Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51186 | 4/20/2013 | Potentially Challenging |  | A worker was welding in a confined space and ignited flammable gas which caused a flash fire. The fire brigade was dispatched but the flammable gas burned off and self extinguished. | Challenging | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51187 | 4/17/2013 | Challenging |  |  | Challenging | Challenging Criteria: Ignition Factor Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51188 | 5/20/2013 | Undetermined (PC-CH) |  | Turbine Aux Oil Pump motor tripped, motor windings were on fire. This resulted in plant shutdown because of the loss of the aux oil pump. Fire brigade extinguished the fire with several CO2 extinguishers. | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Type Heavy Smoke Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51190 | 4/2/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51191 | 4/27/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51193 | 5/21/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51194 | 7/2/2013 | Challenging |  |  | Challenging | Challenging Criteria: Ignition Factor Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51196 | 7/11/2013 | Potentially Challenging | Diesel Exhaust | Does not meet all diesel exhaust override conditions: flame size, length, oil soked insulation. Pic shows damage. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation:
51199 | 7/26/2013 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51201 | : 8/8/2013 | Challenging | Other | Photos show signifcant electric arc/discharge damage. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation:
51207 | 9/2/2013 | Potentially Challenging |  | Smoke was coming from the A Main Feedwater Pump. AUO reported flames from the lagging on the turbine side of the pump. Oil soaked the lagging which ignited under operating heat. The fire brigade extinguished the fire with multiple fire extinguishers. Typical fire from oil soaked lagging. | Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type Fire Suppression Method Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 25 minutes
51209 | 7/31/2013 | Undetermined (NC-PC) | Other | Although apparently self extinguished, the nature and duration of the fire was not known. There was possible fire damage to wiring near the fire ignition source. Therefore, although fire was localized, some evidence of spreading occurred. Since the fire self extinguished without signficant spread, it could be PC or NC. | NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
51216 | 1/3/2010 | Potentially Challenging |  | May also be considered as U(NC-PC) due to unknown fire size, but stated as small, limited damage, unknown time line, and single fire extinguisher used for suppression. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51219 | 2/12/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51220 | 3/26/2010 | Undetermined (NC-PC) | Other | Event appears to be more smoldering and arcing which occurred under the purview of the dedicated fire watch and then fire brigade as the fire was extinguished by removing power. Small flame noted, associated with tape, and event suppression exceeded 5 min for hot work override. Thus could be PC. However, small flame was momentary and fire watch oversight could be considered fire control as the primary observations were smoke and some sparking. Thus NC is also considered. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51221 | 7/20/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51222 | 10/12/2011 | Challenging |  |  | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51231 | 4/7/2014 | Undetermined (NC-PC) |  | Somewhat limited applicability as a transient fire igntion source. U(NC-PC) due to uncertainty about applicability due to location. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51254 | 10/13/2012 | Potentially Challenging |  | Fire lasted about 10 minutes and pump had to be replaced. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51256 | 6/13/2013 | Undetermined (NC-PC) |  | Extent of damage appears to be localized to single breaker due to arcing with no subsequent fire; could also be NC. Investigation revealed evidence of a significant arcing fault in the 13.8 kV Bus 11 cubicle. | NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
51257 | 5/16/2011 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51258 | 7/10/2013 | Challenging |  | Meets definition of challenging, but was relatively small and inconsequential fire. | Challenging | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Fire Type First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51265 | 8/24/2012 | Potentially Challenging | Meets definition of challenging, but was relatively small and inconsequential fire. |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51273 | 4/2/2013 | Undetermined (NC-PC) |  | Arc flash large enough to burn employees in vicinity conducting maintenance activity: borderline PC or NC | NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished
51274 | 12/9/2012 | Potentially Challenging |  | The extent of damage seems significant within the load center to be potentially damaging if not terminated in a timely manner. | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51276 | 8/14/2013 | Potentially Challenging |  | Changed to PC from CH as magnitude of the "deflagration" was not sufficient to damage other equipment nearby. | Challenging | Challenging Criteria: Fire Type Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51278 | 11/5/2013 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51280 | 12/21/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51287 | 10/6/2013 | Potentially Challenging |  | T/M override does not appear to apply as testing was not PMT | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51289 | 10/26/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51291 | 12/9/2013 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51293 | 11/6/2013 | Potentially Challenging |  | Because of the magnitude of the fire and possible time line, hot work override may not apply. However, the fire watch did see the fire at its start and extinguished it before the fire brigade arrived and declared to fire extinguished (10 min). PC classification due to limited CH potential. | Challenging | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51295 | 11/1/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51296 | 11/30/2013 | Potentially Challenging |  | Fire occurred during routine T/M, but not PMT required for T/M override | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51304 | 1/18/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51308 | 4/7/2012 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51309 | 3/7/2014 | Potentially Challenging |  | The substation is panel located within the protected area. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51310 | 4/17/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51315 | 3/20/2014 | Potentially Challenging | Test and Maintenance | Fire occurred during trouble shooting of components that had failed previously. T&M staff was fully prepared, small fire, detected and suppressed fire immediately. PC per NRC review: Known condition appears to be pre-existing to the M&T on 3/20/14. EDG was run previously with this condition; smoke observed. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51316 | 4/12/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m
51317 | 4/2/2014 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51318 | 4/3/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51322 | 6/19/2014 | Undetermined (NC-PC) | Other | Not clear if fire occurred when equipment was powered up and if staff using eguipment detected and suppressed (removed power) fire. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51324 | 5/23/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51328 | 7/27/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51331 | 9/4/2014 | Potentially Challenging |  | Although fire occurred during trouble shooting with fire watch in attendance, conditions were such that fire could have occurred during other periods when maintenance was not being performed. The initial test was a performance test of Appendix R Isolation Sequence. This may or may not have been a maintenance test, but does not appear to be related to the specifics of the subsequent fire. | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51332 | 10/6/2014 | Challenging |  |  | Challenging | Challenging Criteria: Extent of Fire Damage Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51335 | 9/15/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51339 | 9/28/2014 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51354 | 3/28/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51366 | 4/21/2010 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51374 | 3/1/2014 | Undetermined (NC-PC) |  |  | Undetermined(NC-PC) | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:
51377 | 12/12/2013 | Potentially Challenging |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:

## Fire Timeline and Suppression
FireID | Event Date_FTS | Disposition_FTS | Ignition | Discovery | Duration Certainty | Duration | Estimated Duration | Suppression Time | Detection Method | Detection Performance | Suppression Method | Suppression Agent Portable | Suppression Agent Other
50907 | 1/9/2010 | Potentially Challenging |  | 19:25 | 1 |  |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Multiple portable fire extinguishers
50908 | 1/20/2010 | Challenging |  | 13:17 | 1 |  |  | 98 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
50909 | 3/7/2010 | Challenging |  | 11:16 | 1 |  |  | 0 | Installed Fire detector - Type not specified, Plant employee | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50910 | 3/28/2010 | Challenging |  | 18:52 | 1 |  |  | 249 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Initial Suppression Method Successful
50911 | 4/18/2010 | Potentially Challenging |  | 4:00 | 2 | 2 | <5 minutes | 2 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Supervised burn out | Initial Suppression Method Successful
50912 | 5/5/2010 | Challenging |  | 9:39 | 1 |  |  | 211 | Thermal detector (e.g., temperature or rate of rise) | Plant area did not have installed detection capability | Automatic fixed - actuation not specified Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50913 | 5/12/2010 | Potentially Challenging |  |  | 3 |  |  | 0 | Plant employee | Unknown | Supervised burn out,Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
50914 | 6/8/2010 | Potentially Challenging |  | 11:21 | 1 |  |  | 3 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
50916 | 7/13/2010 | Potentially Challenging |  | 15:49 | 1 |  |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
50917 | 7/13/2010 | Potentially Challenging |  | 0:46 | 1 |  |  | 24 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
50919 | 8/22/2010 | Undetermined (PC-CH) |  | 15:29 | 1 |  |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Hose stream or hose reel Single Portable fire extinguisher | Initial Suppression Method Successful
50921 | 10/11/2010 | Potentially Challenging |  | 8:24 | 1 |  |  | 7 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
50922 | 11/7/2010 | Challenging |  | 18:38 | 3 |  |  | 1 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic) | Initial Suppression Method Successful
50923 | 12/19/2010 | Undetermined (NC-PC) |  | 23:51 | 1 |  |  | 45 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50925 | 2/8/2011 | Potentially Challenging |  |  | 1 |  |  | 8 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Portable manual system(e_g_ CO2 cart) | Initial Suppression Method Successful
50926 | 2/12/2011 | Challenging |  | 12:13 | 1 |  |  | 56 | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments)Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50928 | 3/23/2011 | Potentially Challenging |  | 14:00 | 1 |  |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
50930 | 3/29/2011 | Potentially Challenging |  | 0:56 | 1 |  |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
50931 | 5/1/2011 | Potentially Challenging |  | 2:44 | 1 |  |  | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50935 | 6/7/2011 | Challenging |  | 9:30 | 1 |  |  | 223 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Gas Ionization | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
50936 | 6/25/2011 | Challenging |  | 7:38 | 1 |  |  | 37 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50939 | 10/4/2011 | Potentially Challenging |  | 5:55 | 1 |  |  | 6 | Smoke detector | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
50942 | 11/1/2011 | Potentially Challenging |  | 10:26 | 1 |  |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50944 | 11/16/2011 | Potentially Challenging |  | 2:14 | 1 |  |  | 19 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50945 | 12/21/2011 | Potentially Challenging |  | 10:02 | 1 |  |  | 10 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50946 | 1/23/2012 | Potentially Challenging |  | 17:50 | 1 |  |  | 29 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50949 | 4/2/2012 | Potentially Challenging |  | 19:29 | 1 |  |  | 49 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
50950 | 5/21/2012 | Undetermined (PC-CH) |  | 14:57 | 1 |  |  | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Initial Suppression Method Successful
50951 | 5/24/2012 | Undetermined (NC-PC) |  | 13:50 | 1 |  |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50952 | 6/21/2012 | Potentially Challenging |  | 14:51 | 1 |  |  | 17 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Initial Suppression Method Successful
50956 | 10/22/2012 | Challenging |  | 18:46 | 1 |  |  | 22 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
50968 | 4/18/2012 | Potentially Challenging |  | 13:35 | 1 |  |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
50969 | 11/11/2012 | Challenging |  | 3:56 | 1 |  |  | 162 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Thermal detector (e.g.,temperatur | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel | Initial Suppression Method Successful
50977 | 1/8/2013 | Challenging |  | 16:40 | 1 |  |  | 16 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel | Initial Suppression Method Successful
50982 | 12/20/2010 | Challenging |  | 0:45 | 1 |  |  | 15 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Initial Suppression Method Successful
50983 | 9/22/2010 | Challenging |  | 21:35 | 1 |  |  | 19 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel | Initial Suppression Method Successful | None
50985 | 3/26/2012 | Potentially Challenging |  | 22:45 | 1 |  |  | 58 | Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure
50986 | 3/28/2010 | Challenging |  | 18:18 | 1 |  |  | 184 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
50992 | 11/17/2010 | Potentially Challenging |  | 11:00 | 3 |  |  | 0 | Very early smoke detection system (incipient detection) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Initial Suppression Method Successful
50994 | 2/13/2013 | Potentially Challenging |  | 22:05 | 1 |  |  | 2 | Dedicated Fire Watch | Fuel supply removed (simple manual action e.g valve turn off) |  | Initial Suppression Method Successful
51002 | 11/10/2010 | Not Challenging/Undeter |  | 13:58 | 1 |  |  | 1 | Plant employee | Unknown | Other simple: (e.g. blown out, stamped out;specify in comments) | Initial Suppression Method Successful
51005 | 4/30/2010 | Potentially Challenging |  | 15:35 | 1 |  |  | 4 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
51007 | 1/6/2013 | Potentially Challenging |  | 9:01 | 1 |  |  | 19 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
51013 | 11/29/2010 | Undetermined (NC-PC) |  |  | 3 |  |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51014 | 3/27/2012 | Undetermined (NC-PC) |  | 16:49 | 1 |  |  | 2 | Unknown | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) | Initial Suppression Method Successful
51026 | 3/30/2010 | Potentially Challenging |  | 4:20 | 1 |  |  | 6 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51027 | 5/24/2010 | Potentially Challenging |  |  | 2 | 2 | <5 minutes | 2 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) | Initial Suppression Method Successful
51032 | 5/2/2010 | Undetermined (NC-PC) |  |  | 1 |  |  | 525 | Staff conducting test/maintenance on equipment of fire origin | Unknown |  | Initial Suppression Method Successful
51040 | 4/11/2012 | Challenging |  | 18:10 | 1 |  |  | 37 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Initial Suppression Method Successful
51044 | 3/11/2010 | Potentially Challenging |  | 12:20 | 11 |  |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Initial Suppression Method Successful | Initial Suppression Method Successful
51048 | 3/24/2010 | Potentially Challenging |  | 1:10 | 1 |  |  | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel Supply Removed,Single Portable fire extinguisher | Initial Suppression Method Successful
51051 | 4/6/2011 | Undetermined (NC-PC) |  | 2:07 | 1 |  |  | 0 |  | Unknown |  | Initial Suppression Method Successful
51057 | 5/2/2011 | Potentially Challenging |  | 9:54 | 1 |  |  | 8 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.gopen circuit breaker) | Initial Suppression Method Successful
51081 | 12/14/2010 | Potentially Challenging |  | 15:00 | 1 |  |  | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments),Other simple: (e.g. blown out, stamped out;specify in comments) | Initial Suppression Method Successful
51082 | 4/4/2011 | Undetermined (NC-PC) |  | 4:00 | 3 |  |  | 0 | Plant employee | Unknown | Unknown | Initial Suppression Method Successful
51085 | 4/27/2012 | Potentially Challenging |  | 10:22 | 1 |  |  | 10 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51088 | 4/5/2011 | Potentially Challenging |  | 9:39 | 1 |  |  | 10 | Smoke detector, Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
51090 | 2/15/2013 | Potentially Challenging |  | 8:59 | 1 |  |  | 9 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Initial Suppression Method Successful
51092 | 3/20/2013 | Potentially Challenging |  | 2:12 | 1 |  |  | 48 | Smoke detector, Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Initial Suppression Method Successful
51093 | 1/17/2013 | Challenging |  | 14:25 | 1 |  |  | 34 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Multiple portable fire extinguishers | Initial Suppression Method Successful
51109 | 10/15/2010 | Undetermined (NC-PC) |  |  | 3 |  |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown |  | Initial Suppression Method Successful
51111 | 11/2/2010 | Undetermined (NC-PC) |  |  | 3 |  |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Initial Suppression Method Successful
51113 | 10/5/2010 | Potentially Challenging |  | 8:50 | 1 |  |  | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51117 | 3/11/2013 | Potentially Challenging |  | 14:50 | 2 | 2 | <5 minutes | 2 | Other plant personnel (in vicinity or passerby), Plan employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51118 | 4/12/2011 | Potentially Challenging | 15:20 |  | 1 | 4 |  | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51125 | 12/31/2011 | Potentially Challenging |  | 13:25 | 1 |  |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51132 | 4/2/2012 | Potentially Challenging |  | 16:03 | 1 |  |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51135 | 3/12/2013 | Undetermined (NC-PC) |  | 10:55 | 1 |  |  | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51136 | 1/19/2011 | Potentially Challenging |  |  | 1 |  |  | 163 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Initial Suppression Method Successful
51140 | 11/4/2010 | Potentially Challenging |  | 9:43 | 1 |  |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out;specify in comments) | Initial Suppression Method Successful
51146 | 4/3/2013 | Potentially Challenging | 6:32 | 7:00 | 1 | 20 |  | 20 | Smoke detector, Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51152 | 4/11/2013 | Challenging |  | 14:55 | 1 |  |  | 113 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel | Initial Suppression Method Successful
51153 | 1/28/2010 | Potentially Challenging |  | 17:20 | 1 |  |  | 9 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure |  | Initial Suppression Method Successful
51154 | 8/2/2012 | Potentially Challenging |  | 3:20 | 1 |  |  | 119 | Plant employee | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g valve turn off) | Initial Suppression Method Successful
51157 | 9/20/2010 | Undetermined (NC-PC) |  | 12:00 | 1 |  |  | 0 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) | Initial Suppression Method Successful
51158 | 10/4/2012 | Potentially Challenging |  | 4:00 | 1 |  |  | 3 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered | Initial Suppression Method Successful
51160 | 9/25/2010 | Challenging |  | 9:35 | 1 |  |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Initial Suppression Method Successful
51162 | 10/10/2010 | Potentially Challenging |  | 10:00 | 3 |  |  | 0 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51164 | 9/19/2011 | Undetermined (NC-PC) |  | 20:00 | 3 |  |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51166 | 6/10/2012 | Potentially Challenging |  | 16:45 | 1 |  |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51168 | 12/3/2012 | Undetermined (NC-PC) |  | 21:45 | 1 |  |  | 0 | Roving Firewatch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51171 | 7/13/2012 | Potentially Challenging |  | 9:35 | 3 |  |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | Initial Suppression Method Successful
51172 | 3/21/2013 | Potentially Challenging |  | 11:00 | 1 |  |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Portable manual system(e_g_ CO2 cart) | Initial Suppression Method Successful
51176 | 5/4/2013 | Potentially Challenging |  | 7:43 | 1 |  |  | 7 | Smoke detector | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51180 | 5/16/2010 | Potentially Challenging |  | 16:05 | 1 |  |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Air supply cut off (smothered, covered | Initial Suppression Method Successful
51181 | 9/14/2010 | Potentially Challenging |  | 22:22 | 3 |  |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
51184 | 12/2/2011 | 12/2/2011 |  | 13:00 | 3 |  |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability |  | Initial Suppression Method Successful
51186 | 4/20/2013 | Potentially Challenging |  | 10:00 | 1 |  |  | 0 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51187 | 4/17/2013 | Challenging |  | 20:29 | 1 |  |  | 7 | Main control room staff (e.g.,control/instrumentation failures), Plant employee,Failed Equipment A | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Hose stream or hose reel,Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
51188 | 5/20/2013 | Undetermined (PC-CH) |  | 3:50 | 1 |  |  | 27 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Multiple portable fire extinguishers | Initial Suppression Method Successful
51190 | 4/2/2012 | Potentially Challenging |  | 6:24 | 1 |  |  | 9 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Initial Suppression Method Successful
51191 | 4/27/2013 | Potentially Challenging |  | 10:10 | 1 |  |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51193 | 5/21/2013 | Potentially Challenging |  | 21:59 | 1 |  |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51194 | 7/2/2013 | Challenging |  | 20:26 | 1 |  |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51196 | 7/11/2013 | Potentially Challenging |  | 10:29 | 2 | 2 | <5 minutes | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51199 | 7/26/2013 | Challenging |  | 23:35 | 1 |  |  | 33 | Smoke detector, Other plant personnel (in vicinity or passerby), Failed Equipment Alarm (Tripped pum | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher | Initial Suppression Method Successful
51201 | : 8/8/2013 | Challenging |  | 3:00 | 2 | 2 | <5 minutes | 2 | Plant employee, Very early smoke detection system,(incipient detection), Main control room staff (e. | Plant area had installed detection which did not actuate, fire was detected visually or by other means – system failure indicated | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51207 | 9/2/2013 | Potentially Challenging |  | 19:22 | 2 | 25 | 20 to <30 minu | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Initial Suppression Method Successful
51209 | 7/31/2013 | Undetermined (NC-PC) |  | 13:02 | 1 |  |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Unknown,Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51216 | 1/3/2010 | Potentially Challenging |  |  | 3 |  |  |  | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51219 | 2/12/2010 | Potentially Challenging |  | 2:30 | 1 |  |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) | Initial Suppression Method Successful
51220 | 3/26/2010 | Undetermined (NC-PC) |  | 22:45 | 1 |  |  | 25 | Dedicated Fire Watch | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51221 | 7/20/2011 | Potentially Challenging |  | 13:19 | 1 |  |  | 17 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Other (specify in comments)Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51222 | 10/12/2011 | Challenging |  | 5:30 | 1 |  |  | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Initial Suppression Method Successful
51231 | 4/7/2014 | Undetermined (NC-PC) |  | 9:43 | 1 |  |  | 4 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51254 | 10/13/2012 | Potentially Challenging |  | 14:15 | 1 |  |  | 10 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51256 | 6/13/2013 | Undetermined (NC-PC) |  | 14:31 | 1 |  |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51257 | 5/16/2011 | Potentially Challenging |  | 10:00 | 3 |  |  |  |  | Unknown |  | Initial Suppression Method Successful
51258 | 7/10/2013 | Challenging |  | 1:00 | 1 |  |  | 60 | Plant employee | Plant area had installed detection which actuated | Single Portable fire extinguisher | Initial Suppression Method Successful
51265 | 8/24/2012 | Potentially Challenging |  | 4:50 | 1 |  |  | 1 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) | Initial Suppression Method Successful
51273 | 4/2/2013 | Undetermined (NC-PC) |  | 17:07 | 1 |  |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51274 | 12/9/2012 | Potentially Challenging |  | 5:00 | 3 |  |  |  | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51276 | 8/14/2013 | Potentially Challenging |  | 16:15 | 1 |  |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) | Initial Suppression Method Successful
51278 | 11/5/2013 | Challenging |  | 17:48 | 1 |  |  | 42 | Sprinkler or fire-water system flow alarm | Plant area did not have installed detection capability | Automatic fixed - thermally actuated | Initial Suppression Method Successful
51280 | 12/21/2014 | Potentially Challenging |  | 9:15 | 3 |  |  |  | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51287 | 10/6/2013 | Potentially Challenging |  | 16:00 | 1 |  |  | 3 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51289 | 10/26/2013 | Potentially Challenging |  | 8:15 | 1 |  |  | 6 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51291 | 12/9/2013 | Challenging |  | 7:48 | 1 |  |  | 89 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic),Hose stream or hose reel | Initial Suppression Method Successful
51293 | 11/6/2013 | Potentially Challenging |  | 20:10 | 1 |  |  | 10 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51295 | 11/1/2013 | Potentially Challenging |  | 20:56 | 1 |  |  | 134 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure |  | Initial Suppression Method Successful
51296 | 11/30/2013 | Potentially Challenging |  | 13:50 | 1 |  |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51304 | 1/18/2014 | Potentially Challenging |  | 3:45 | 1 |  |  | 26 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
51308 | 4/7/2012 | Potentially Challenging |  | 8:00 | 1 |  |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51309 | 3/7/2014 | Potentially Challenging |  | 4:55 | 1 |  |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher | Initial Suppression Method Successful
51310 | 4/17/2014 | Potentially Challenging |  | 11:00 | 1 |  |  | 2 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51315 | 3/20/2014 | Potentially Challenging |  | 14:01 | 1 |  |  | 5 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51316 | 4/12/2014 | Potentially Challenging |  | 22:00 | 1 |  |  | 1 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51317 | 4/2/2014 | Challenging |  | 12:47 | 1 |  |  | 91 | Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Automatic fixed - thermally actuated | Initial Suppression Method Successful
51318 | 4/3/2014 | Potentially Challenging |  | 13:55 | 1 |  |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51322 | 6/19/2014 | Undetermined (NC-PC) |  | 15:26 | 1 |  |  | 0 | Plant employee | Plant area did not have installed detection capability |  | Initial Suppression Method Successful
51324 | 5/23/2014 | Potentially Challenging |  | 19:41 | 1 |  |  | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Initial Suppression Method Successful
51328 | 7/27/2014 | Potentially Challenging |  | 12:44 | 1 |  |  | 15 | Smoke detector | Plant area had installed detection which actuated |  | Initial Suppression Method Successful
51331 | 9/4/2014 | Potentially Challenging |  | 10:10 | 1 |  |  | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51332 | 10/6/2014 | Challenging |  | 13:26 | 1 |  |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51335 | 9/15/2014 | Potentially Challenging |  | 19:36 | 1 |  |  | 3 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher | Initial Suppression Method Successful
51339 | 9/28/2014 | Potentially Challenging |  | 15:45 | 1 |  |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51354 | 3/28/2010 | Potentially Challenging |  | 23:30 | 1 |  |  | 3 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Initial Suppression Method Successful
51366 | 4/21/2010 | Potentially Challenging |  | 13:47 | 1 |  |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51374 | 3/1/2014 | Undetermined (NC-PC) |  |  | 3 |  |  |  | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) | Initial Suppression Method Successful
51377 | 12/12/2013 | Potentially Challenging |  | 14:16 | 1 |  |  | 2 | Plant employee | Plant area did not have installed detection capability | Portable manual system(e_g_ CO2 cart) | Initial Suppression Method Successful

## Plant Response
FireID | Event Date_PR | Disposition_PR | Mode Prior | Mode After | Power Level Prior | Power Level After | Power Effect | EAL Declaration
50907 | 1/9/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event
50908 | 1/20/2010 | Challenging | Power Operation | Power Operation | 100 | 100 | None
50909 | 3/7/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram | Unusual Event
50910 | 3/28/2010 | Challenging | Unknown | Unknown | 0 | 0 | Scram | Alert
50911 | 4/18/2010 | Potentially Challenging | Power Operation | Cold Shutdown | 11 | 0 | Reduced Power
50912 | 5/5/2010 | Challenging | Unknown | Unknown | 0 | 0 | None
50913 | 5/12/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50914 | 6/8/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50916 | 7/13/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50917 | 7/13/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 77 | Reduced Power
50919 | 8/22/2010 | Undetermined (PC-CH) | Unknown | Unknown | 0 | 0
50921 | 10/11/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50922 | 11/7/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram
50923 | 12/19/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 |  | Unusual Event
50925 | 2/8/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50926 | 2/12/2011 | Challenging | Startup | Unknown | 20 | 0
50928 | 3/23/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50930 | 3/29/2011 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
50931 | 5/1/2011 | Potentially Challenging | Cold Shutdown | Unknown | 0 | 0
50935 | 6/7/2011 | Challenging | Cold Shutdown | Unknown | 0 | 0 |  | Unusual Event
50936 | 6/25/2011 | Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event
50939 | 10/4/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50942 | 11/1/2011 | Potentially Challenging | Power Operation | Power Operation | 100 | 90 | Reduced Power
50944 | 11/16/2011 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Alert
50945 | 12/21/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0
50946 | 1/23/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  | Unusual Event
50949 | 4/2/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event
50950 | 5/21/2012 | Undetermined (PC-CH) | Power Operation | Hot Shutdown | 100 | 0 | Turbine Trip
50951 | 5/24/2012 | Undetermined (NC-PC) | Startup | Cold Shutdown | 33 | 0 | Scram
50952 | 6/21/2012 | Potentially Challenging | Power Operation | Power Operation | 87 | 62 | Reduced Power | Unusual Event
50956 | 10/22/2012 | Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event
50968 | 4/18/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50969 | 11/11/2012 | Challenging | Power Operation | Hot Shutdown | 100 | 0 | Turbine Trip | Unusual Event
50977 | 1/8/2013 | Challenging | Power Operation | Unknown | 100 | 0 | Scram | Unusual Event
50982 | 12/20/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram
50983 | 9/22/2010 | Challenging | Unknown | Unknown | 0 | 0 | None | Unusual Event
50985 | 3/26/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50986 | 3/28/2010 | Challenging | Power Operation | Unknown | 100 | 68 | Reduced Power
50992 | 11/17/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
50994 | 2/13/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51002 | 11/10/2010 | Not Challenging/Undeter | Refueling | Refueling | 0 | 0 | None
51005 | 4/30/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51007 | 1/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51013 | 11/29/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51014 | 3/27/2012 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0
51026 | 3/30/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None
51027 | 5/24/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None
51032 | 5/2/2010 | Undetermined (NC-PC) | Power Operation | Power Operation |  |  | None
51040 | 4/11/2012 | Challenging | Unknown | Unknown | 0 | 0 | None
51044 | 3/11/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51048 | 3/24/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51051 | 4/6/2011 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0
51057 | 5/2/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51081 | 12/14/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0
51082 | 4/4/2011 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51085 | 4/27/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51088 | 4/5/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51090 | 2/15/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51092 | 3/20/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51093 | 1/17/2013 | Challenging | Power Operation | Power Operation | 0 | 0 | None
51109 | 10/15/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51111 | 11/2/2010 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51113 | 10/5/2010 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51117 | 3/11/2013 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51118 | 4/12/2011 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51125 | 12/31/2011 | Potentially Challenging | Power Operation | Power Operation |  |  | None
51132 | 4/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51135 | 3/12/2013 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51136 | 1/19/2011 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None
51140 | 11/4/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51146 | 4/3/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51152 | 4/11/2013 | Challenging | Unknown | Unknown | 0 | 0 | None
51153 | 1/28/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51154 | 8/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51157 | 9/20/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51158 | 10/4/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51160 | 9/25/2010 | Challenging | Unknown | Unknown | 0 | 0 | None
51162 | 10/10/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51164 | 9/19/2011 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51166 | 6/10/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51168 | 12/3/2012 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51171 | 7/13/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51172 | 3/21/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51176 | 5/4/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51180 | 5/16/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51181 | 9/14/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51184 | 12/2/2011 | 12/2/2011 | Unknown | Unknown | 0 | 0 | None
51186 | 4/20/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51187 | 4/17/2013 | Challenging | Refueling | Refueling | 0 | 0 | None
51188 | 5/20/2013 | Undetermined (PC-CH) | Startup | Hot Shutdown |  | 0 | Reduced Power
51190 | 4/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51191 | 4/27/2013 | Potentially Challenging | Power Operation | Hot Shutdown |  | 0 | Scram
51193 | 5/21/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51194 | 7/2/2013 | Challenging | Power Operation | Unknown | 100 | 60 | Reduced Power
51196 | 7/11/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51199 | 7/26/2013 | Challenging | Power Operation | Unknown | 100 | 0 | Turbine Trip
51201 | : 8/8/2013 | Challenging | Power Operation | Power Operation | 100 | 92 | Reduced Power
51207 | 9/2/2013 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None
51209 | 7/31/2013 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51216 | 1/3/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51219 | 2/12/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51220 | 3/26/2010 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51221 | 7/20/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51222 | 10/12/2011 | Challenging | Power Operation | Power Operation | 100 | 100 | None
51231 | 4/7/2014 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0
51254 | 10/13/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0
51256 | 6/13/2013 | Undetermined (NC-PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | LOOP
51257 | 5/16/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51258 | 7/10/2013 | Challenging | Unknown | Unknown | 0 | 0
51265 | 8/24/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51273 | 4/2/2013 | Undetermined (NC-PC) | Power Operation | Power Operation | 100 | 100 | None
51274 | 12/9/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51276 | 8/14/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51278 | 11/5/2013 | Challenging | Power Operation | Unknown | 0 | 0 | Turbine Trip | Unusual Event
51280 | 12/21/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51287 | 10/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51289 | 10/26/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51291 | 12/9/2013 | Challenging | Power Operation | Unknown | 0 | 0 | Scram | Unusual Event
51293 | 11/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51295 | 11/1/2013 | Potentially Challenging | Power Operation | Unknown | 50 | 0 | Reduced Power
51296 | 11/30/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51304 | 1/18/2014 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | Entered an LCO | Unusual Event
51308 | 4/7/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51309 | 3/7/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51310 | 4/17/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51315 | 3/20/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Alert
51316 | 4/12/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0
51317 | 4/2/2014 | Challenging | Startup | Hot Shutdown | 0 | 0 | Scram | Alert
51318 | 4/3/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51322 | 6/19/2014 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None
51324 | 5/23/2014 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None
51328 | 7/27/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51331 | 9/4/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51332 | 10/6/2014 | Challenging | Power Operation | Power Operation | 100 | 100 | Entered an LCO | Alert
51335 | 9/15/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51339 | 9/28/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None
51354 | 3/28/2010 | Potentially Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None
51366 | 4/21/2010 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None
51374 | 3/1/2014 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None
51377 | 12/12/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None