## Sheet1
| FireID | Event Date_FES | Disposition_FES | Outside PA | Plant Area | Building | System | Component Group | Component | Voltage | Current Type | HP or kVA | ICES Component | Event Date_FEA | Disposition_FEA | Fire Cause | Combustible Group | Type | Form | Fire Type | Smoke | Temperature | Damage Extent | Collateral Damage | Collateral Damage.1 | Feet Above | Feet Laterally | Collateral Description | Suppression Effects | Evidence of secondary ignition | Smoke.1 | Heat Damage | Event Date_FSE | Disposition_FSE | Review Status: | Automatic Determination | Unnamed: 5 | Unnamed: 6 | Override | Comment on Disposition | Automatic Determination Basis | Event Date_FTS | Disposition_FTS | Ignition | Discovery | Duration Certainty | Duration | Suppression Time | Detection Method | Detection Performance | Suppression Method | Suppression Agent | Unnamed: 12 | Unnamed: 13 | Estimated Duration | Suppression Agent Portable | Suppression Agent Other | Unnamed: 14 | Event Date_PR | Disposition_PR | Mode Prior | Mode After | Power Level Prior | Power Level After | Power Effect | EAL Declaration | Disposition_new
0 | 1 | 12/12/2006 |  | No |  | Main Transformer or Switch Yard | Switchyard System | Generator | Electric Bus Bar or Bus Duct | 13 KV or greater | AC |  |  | 12/12/2006 | Undetermined | High Energy Arc Fault (HEAF) | Transient |  |  | Arc/electric discharge | Unknow | Unknow | Confined to the objective of origin | Yes | [8 empty] | 12/12/2006 | Undetermined | Preliminary | Challenging | [5 empty] | 12/12/2006 | Undetermined | 13:22:00 | 13:22:00 | Known | 34 | 34 | Failed Equipment Alarm | Unknown | Unknow | Portable | [6 empty] | 12/12/2006 | Undetermined | Operate | Hot Standby | 25 | 0 | scram | Unusual Event
1 | 2 | 1/5/1999 | Not Challenging | Yes |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 1/5/1999 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | Yes | [8 empty] | 1/5/1999 | Not Challenging | Preliminary | Challenging | [5 empty] | 1/5/1999 | Not Challenging | 13:11:00 | 13:11:00 | Known | 14 | 14 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Hose stream or hose reel | Portable | [6 empty] | 1/5/1999 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Not Challenging
2 | 3 | 1/14/1999 | Challenging | No |  | Other (Specify in comments) | Hydrogen Supply System | Other | [5 empty] | 1/14/1999 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No | [8 empty] | 1/14/1999 | Challenging | Preliminary | Challenging | [5 empty] | 1/14/1999 | Challenging | 12:56:00 | 12:56:00 | Known | 409 | 409 | Other plant personnel (in vicinity or passerby） | Plant area did not have installed detection capability | Hose stream or hose reel | Portable | [6 empty] | 1/14/1999 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
3 | 4
4 | 5 | 5/18/1999 | Not Evaluated | Yes |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) |  | Transformers | Oil‐filled Transformer | AC |  |  | 5/18/1999 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the objective of origin | No | [8 empty] | 5/18/1999 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 5/18/1999 | Not Evaluated | 18:32:00 | 18:32:00 | Known | 173 | 173 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 5/18/1999 | Not Evaluated | Refueling | Refueling | 0 | 0 | None | Unusual Event | Not Evaluated
5 | 6 | 7/13/1999 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 7/13/1999 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No | [8 empty] | 7/13/1999 | Potentially Challenging | Final | Challenging | [5 empty] | 7/13/1999 | Potentially Challenging | 13:00:00 |  | Known | 40 | 40 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water | [6 empty] | 7/13/1999 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
6 | 7 | 10/9/1999 | Undetermined (NC‐PC) | No |  | Main Transformer or Switch Yard | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 4KV | AC |  |  | 10/9/1999 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | Insulation | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/9/1999 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 10/9/1999 | Undetermined (NC‐PC) | 23:25:00 | 23:25:00 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable | [6 empty] | 10/9/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 96 | Reduced Power |  | Not Challenging
7 | 8 | 5/7/2000 | Potentially Challenging | No |  | Turbine Building | Main Generator Output Power System | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 5/7/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/7/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/7/2000 | Potentially Challenging | 07:50:00 | 07:57:00 | Known | 37 | 37 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | Portable | [6 empty] | 5/7/2000 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
8 | 9 | 1/3/1990 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) |  | Transformers | Dry transformer | 110V | AC |  |  | 1/3/1990 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Not available | Yes | [8 empty] | 1/3/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 1/3/1990 | Undetermined (PC‐CH) | 07:45:00 |  | Known | 13 | 13 | Unknown | Unknown | Unknown | Portable | [6 empty] | 1/3/1990 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
9 | 10
10 | 11 | 3/15/1990 | Not Challenging | Yes |  | Main Transformer or Switch Yard | Main Generator Output Power System | Cable/Wiring | Cable/Wiring | 13 KV or greater | AC |  |  | 3/15/1990 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 3/15/1990 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/15/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable | [6 empty] | 3/15/1990 | Unusual Event | Operate | Operate | 50 | 50 | None |  | Not Challenging
11 | 12 | 3/30/1990 | Not Challenging | No |  | Control building | Low Voltage Power System, Class 1E | Transformers | Other (Capacitor Voltage, Poten | 480V | AC |  |  | 3/30/1990 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/30/1990 | Not Challenging | Final | Not Challenging | [5 empty] | 3/30/1990 | Not Challenging | 03:41:00 | 03:41:00 | Known | 3 | 3 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher Other (specify in comments) | Portable: CO2 | [6 empty] | 3/30/1990 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
12 | 13 | 4/10/1990 | Potentially Challenging | No |  | Turbine Building | Low Voltage Power System (600V and less) |  | Dry transformer | 4KV | AC |  |  | 4/10/1990 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/10/1990 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/10/1990 | Potentially Challenging | 05:41:00 |  | Known | 9 | 9 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 4/10/1990 | Potentially Challenging | Unknown | Unknown |  |  | None |  | Challenging
13 | 14 | 5/24/1990 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 5/24/1990 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No | [8 empty] | 5/24/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/24/1990 | Potentially Challenging | 03:15:00 | 03:23:00 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable | [6 empty] | 5/24/1990 | Potentially Challenging | Operate | Operate | 70 | 70 | None | Alert | Challenging
14 | 15 | 5/27/1990 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 5/27/1990 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/27/1990 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/27/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 5/27/1990 | Cold Shutdown | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Not Challenging
15 | 16 | 6/10/1990 | Not Challenging | No |  | Radwaste Building | Offgas System (BWR) | Other |  |  | AC |  |  | 6/10/1990 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No | [8 empty] | 6/10/1990 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/10/1990 | Not Challenging | 13:31:00 |  | Known | 8624 | 8624 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable | [6 empty] | 6/10/1990 | Not Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None | Unusual Event | Not Challenging
16 | 17 | 6/28/1990 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 6/28/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Not available | No | [8 empty] | 6/28/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/28/1990 | Potentially Challenging | 03:01:00 | 03:01:00 | Known | 29 | 29 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable | [6 empty] | 6/28/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
17 | 18 | 7/13/1990 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 7/13/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/13/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/13/1990 | Potentially Challenging | 13:10:00 | 13:25:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable | [6 empty] | 7/13/1990 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
18 | 19 | 8/4/1990 | Challenging | No |  | Radwaste Building |  | Dryers | [5 empty] | 8/4/1990 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Interior finish |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/4/1990 | Challenging | Preliminary | Challenging | [5 empty] | 8/4/1990 | Challenging | 17:09:00 | 17:09:00 | Known | 19 | 19 | Unknown | Unknown | Fixed suppression system ‐ deluge (automatic) | Portable | [6 empty] | 8/4/1990 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
19 | 20 | 8/25/1990 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 8/25/1990 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No | [8 empty] | 8/25/1990 | Challenging | Preliminary | Potentially Challenging | [5 empty] | 8/25/1990 | Challenging | 18:02:00 |  | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable | [6 empty] | 8/25/1990 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
20 | 21 | 9/22/1990 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 9/22/1990 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes | [8 empty] | 9/22/1990 | Challenging | Preliminary | Challenging | [5 empty] | 9/22/1990 | Challenging | 21:51:00 |  | Known | 29 | 29 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Portable,Other: Water | [6 empty] | 9/22/1990 | Challenging | Operate | Hot Standby | 40 | 0 | Scram | Unusual Event | Challenging
21 | 22 | 12/3/1990 | Challenging | No | Containment/Drywell | Drywell (BWR) |  |  |  |  | AC |  |  | 12/3/1990 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No | [8 empty] | 12/3/1990 | Challenging | Preliminary | Challenging | [5 empty] | 12/3/1990 | Challenging | 04:29:00 |  | Known | 76 | 76 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel Multiple portable fire extinguishers | Portable: Dry Chemical,Other: Water | [6 empty] | 12/3/1990 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
22 | 23 | 12/19/1990 | Undetermined (PC‐CH) | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  | AC |  |  | 12/19/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/19/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 12/19/1990 | Undetermined (PC‐CH) | 12:20:00 |  | Known | 40 | 40 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher Other (specify in comments) | Portable: Dry Chemical | [6 empty] | 12/19/1990 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
23 | 24 | 12/22/1990 | Undetermined (PC‐CH) | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 12/22/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/22/1990 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 12/22/1990 | Undetermined (PC‐CH) | 07:45:00 |  | Known | 120 | 120 | Dedicated Fire Watch | Unknown | Unknown | Portable | [6 empty] | 12/22/1990 | Undetermined (PC‐CH) | Operate | Operate | 90 | 80 | Reduced Power | Unusual Event | Challenging
24 | 25 | 1/11/1991 | Undetermined (NC‐PC) | No |  | Turbine Building | General Ventillation Systems |  |  |  | AC |  |  | 1/11/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/11/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/11/1991 | Undetermined (PC‐CH) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable | [6 empty] | 1/11/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 65 | Reduced Power | Unusual Event | Not Challenging
25 | 26 | 2/14/1991 | Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Cable/Wiring |  | 110V | AC |  |  | 2/14/1991 | Challenging | Personnel error: Misuse of heating devices | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/14/1991 | Challenging | Preliminary | Challenging | [5 empty] | 2/14/1991 | Challenging | 21:45:00 | 21:45:00 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Single Portable fire extinguisher | Portable: Halon，Other: Water | [6 empty] | 2/14/1991 | Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
26 | 27 | 1/16/1991 | Not Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 1/16/1991 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume |  | Confined to the object of origin | No | [8 empty] | 1/16/1991 | Not Challenging | Final | Not Challenging | [5 empty] | 1/16/1991 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 1/16/1991 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram |  | Not Challenging
27 | 28 | 1/23/1991 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 1/23/1991 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/23/1991 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/23/1991 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable | [6 empty] | 1/23/1991 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
28 | 29 | 2/23/1991 | Potentially Challenging | No |  | Turbine Building | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC |  |  | 2/23/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of originn (broad/extensive damage) | No | [8 empty] | 2/23/1991 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/23/1991 | Potentially Challenging | 00:50:00 | 00:52:00 | Known | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/23/1991 | Potentially Challenging | Hot Standby | Hot Standby | 0 | 0 | None | Unusual Event | Challenging
29 | 30 | 4/29/1991 | Challenging | No |  | Turbine Building | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 4/29/1991 | Challenging | Electrical arcing or sparks (non-HEAF) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | Yes | [8 empty] | 4/29/1991 | Challenging | Preliminary | Challenging | [5 empty] | 4/29/1991 | Challenging | 18:42:00 |  | Known | 200 | 200 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression ‐ manually actuated,Fixed suppression system ‐ deluge (automatic),Fuel supply removed,Supervised burn out | Other: Water | [6 empty] | 4/29/1991 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
30 | 31 | 6/15/1991 | Undetermined (NC‐PC) | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/15/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 6/15/1991 | Undetermined (PC‐CH) | Preliminary | Undetermined (PC‐CH) | [5 empty] | 6/15/1991 | Undetermined (NC‐PC) | 23:50:00 |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable | [6 empty] | 6/15/1991 | Undetermined (NC‐PC) | Operate | Hot Standby | 75 | 0 | Scram | Alert | Not Challenging
31 | 32 | 6/27/1991 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 6/27/1991 | Potentially Challenging | Personnel error during test and maintenance activity | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/27/1991 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/27/1991 | Potentially Challenging | 21:15:00 | 21:15:00 | Known | 28 | 28 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable | [6 empty] | 6/27/1991 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram |  | Challenging
32 | 33 | 8/1/1991 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 8/1/1991 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/1/1991 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/1/1991 | Potentially Challenging | 19:31:00 | 19:31:00 | Known | 183 | 183 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable | [6 empty] | 8/1/1991 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
33 | 34 | 8/11/1991 | Potentially Challenging | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 8/11/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/11/1991 | Potentially Challenging | Final | Challenging | [5 empty] | 8/11/1991 | Potentially Challenging | 08:55:00 | 08:55:00 | Known | 11 | 11 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel Multiple portable fire extinguishers | Portable: CO2,Other: Water | [6 empty] | 8/11/1991 | Potentially Challenging | Operate | Operate | 91 | 87 | Reduced Power | Unusual Event | Challenging
34 | 35 | 11/2/1991 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 11/2/1991 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/2/1991 | Not Challenging | Final | Challenging | [5 empty] | 11/2/1991 | Not Challenging |  | 21:39:00 | Estimated | 46 | 46 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Portable | [6 empty] | 11/2/1991 | Not Challenging | Operate | Operate | 0 | 0 | None | Unusual Event | Not Challenging
35 | 36 | 11/9/1991 | Not Challenging | Yes |  | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC |  |  | 11/9/1991 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | Yes | [8 empty] | 11/9/1991 | Not Challenging | Preliminary | Challenging | [5 empty] | 11/9/1991 | Not Challenging | 11:22:00 | 11:22:00 | Known | 15 | 15 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated, Hose stream or hose reel, Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water | [6 empty] | 11/9/1991 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram | Alert | Not Challenging
36 | 37 | 11/15/1991 | Not Challenging | Yes |  | Other (Specify in comments) |  | Crane |  | 13 KV or greater | AC |  |  | 11/15/1991 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 11/15/1991 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/15/1991 | Not Challenging | 09:28:00 |  | Known | 34 | 34 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable | [6 empty] | 11/15/1991 | Not Challenging | Hot Standby | Hot Standby | 0 |  | None | Unusual Event | Not Challenging
37 | 38 | 3/21/1992 | Challenging | No | Switchgear Room | Reactor Building (BWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 3/21/1992 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes | [8 empty] | 3/21/1992 | Challenging | Final | Challenging | [5 empty] | 3/21/1992 | Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable | [6 empty] | 3/21/1992 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
38 | 39 | 5/3/1992 | Not Challenging | No |  | Main Transformer or Switch Yard |  | Air Compressors |  |  | N/A |  |  | 5/3/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 5/3/1992 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/3/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable | [6 empty] | 5/3/1992 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Alert | Not Challenging
39 | 40 | 5/22/1992 | Not Challenging | No |  | Radwaste Building | Offgas System (BWR) | Other |  |  | N/A |  |  | 5/22/1992 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/22/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 5/22/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Other (specify in comments) | Portable | [6 empty] | 5/22/1992 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Alert | Not Challenging
40 | 41 | 6/17/1992 | Potentially Challenging | No | Switchgear Room | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 4KV | AC |  |  | 6/17/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/17/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/17/1992 | Potentially Challenging | 15:26:00 | 15:26:00 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 6/17/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
41 | 42 | 7/3/1992 | Potentially Challenging | No |  | Other (Specify in comments) |  | Air Compressors | [5 empty] | 7/3/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 7/3/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/3/1992 | Potentially Challenging | 10:29:00 |  | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable | [6 empty] | 7/3/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
42 | 43 | 7/4/1992 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 7/4/1992 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 7/4/1992 | Challenging | Final | Challenging | [5 empty] | 7/4/1992 | Challenging |  | 01:50:00 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable | [6 empty] | 7/4/1992 | Challenging | Operate | Hot Shutdown | 95 | 0 | Scram | Alert | Challenging
43 | 44 | 7/13/1992 | Challenging | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 7/13/1992 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/13/1992 | Challenging | Final | Challenging | [5 empty] | 7/13/1992 | Challenging | 19:10:00 | 19:10:00 | Estimated | 13 | 13 | Unknown | Unknown | Hose stream or hose reel, Multiple portable fire extinguishers,Other (specify in comments) | Portable: CO2,Other: Water | [6 empty] | 7/13/1992 | Challenging | Operate | Operate | 93 | 73 | Reduced Power | Unusual Event | Challenging
44 | 45 | 7/29/1992 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 4KV | AC |  |  | 7/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 7/29/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/29/1992 | Potentially Challenging | 04:15:00 |  | Known | 16 | 16 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 7/29/1992 | Potentially Challenging | Operate | Operate | 95 | 95 | None | Unusual Event | Challenging
45 | 46 | 8/4/1992 | Potentially Challenging | No | Battery Room | Control building | DC Power System, class 1E | Electrical panel |  | Other (specify) | DC |  |  | 8/4/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 8/4/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/4/1992 | Potentially Challenging | 05:52:00 | 05:52:00 | Known | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable | [6 empty] | 8/4/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert | Challenging
46 | 47 | 8/10/1992 | Not Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 8/10/1992 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/10/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 8/10/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable | [6 empty] | 8/10/1992 | Not Challenging | Operate | Hot Standby | 73 | 0 | Scram |  | Not Challenging
47 | 48 | 9/4/1992 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 9/4/1992 | Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/4/1992 | Challenging | Final | Challenging | [5 empty] | 9/4/1992 | Challenging | 02:14:00 | 02:14:00 | Known | 27 | 27 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers,Power Supply Removed | Portable: Dry Chemical,Other: Water | [6 empty] | 9/4/1992 | Challenging | Operate |  | 100 | 1 | Turbine Trip | Unusual Event | Challenging
48 | 49 | 9/15/1992 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 9/15/1992 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/15/1992 | Challenging | Preliminary | Challenging | [5 empty] | 9/15/1992 | Challenging | 02:43:00 | 02:43:00 | Known | 77 | 77 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers | Portable: CO2,Other: AFFF foam | [6 empty] | 9/15/1992 | Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
49 | 50 | 11/24/1992 | Potentially Challenging | No |  | Turbine Building | Main Generator Output Power System | Bus Duct | IsoPhase Bus Duct | 13 KV or greater | AC |  |  | 11/24/1992 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Structural component |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/24/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/24/1992 | Potentially Challenging | 02:18:00 | 02:18:00 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable | [6 empty] | 11/24/1992 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
50 | 51 | 2/5/1993 | Not Challenging | No | Cable Spreading Room |  | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC |  |  | 2/5/1993 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/5/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 2/5/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed | Portable | [6 empty] | 2/5/1993 | Not Challenging | Operate | Operate | 100 | 46 | Reduced Power | Unusual Event | Not Challenging
51 | 52 | 6/19/1993 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/19/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 6/19/1993 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/19/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown | Portable | [6 empty] | 6/19/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
52 | 53 | 7/27/1993 | Not Challenging | No |  | Radwaste Building | Offgas System (BWR) | Other | [5 empty] | 7/27/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/27/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 7/27/1993 | Not Challenging |  |  | Known | 0 | 0 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Other (specify in comments) | Portable | [6 empty] | 7/27/1993 | Not Challenging | Operate | Operate | 100 | 45 | Reduced Power |  | Not Challenging
53 | 54 | 8/16/1993 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System |  | Class 1A emergency generator | 4KV | AC |  |  | 8/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/16/1993 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/16/1993 | Not Challenging | 15:09:00 | 15:09:00 | Known | 1 | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 8/16/1993 | Not Challenging | Operate | Operate | 100 | 100 | None | Alert | Not Challenging
54 | 55 | 10/13/1993 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Essential Service Water System | Other | [5 empty] | 10/13/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No | [8 empty] | 10/13/1993 | Potentially Challenging | Final | Challenging | [5 empty] | 10/13/1993 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemica | [6 empty] | 10/13/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
55 | 56 | 10/21/1993 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator | 13 KV or greater | AC |  |  | 10/21/1993 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/21/1993 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/21/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable | [6 empty] | 10/21/1993 | Potentially Challenging | Operate | Operate | 40 | 29 | Reduced Power | Unusual Event | Challenging
56 | 57 | 11/2/1993 | Not Challenging | Yes |  | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  | 220V | AC |  |  | 11/2/1993 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/2/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/1993 | Not Challenging | 13:00:00 | 13:00:00 | Known | 14 | 14 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 11/2/1993 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
57 | 58 | 12/25/1993 | Challenging | No |  | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator | 13 KV or greater | AC |  |  | 12/25/1993 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to part of room or area of origin | Yes | [8 empty] | 12/25/1993 | Challenging | Preliminary | Challenging | [5 empty] | 12/25/1993 | Challenging | 13:52:00 | 13:52:00 | Known | 210 | 210 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified, Multiple portable fire extinguishers | Portable: CO2,Other: Water | [6 empty] | 12/25/1993 | Challenging | Operate | Hot Shutdown | 93 | 0 | Scram | Alert | Challenging
58 | 59 | 1/29/1994 | Challenging | No |  | Turbine Building | [7 empty] | 1/29/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 1/29/1994 | Challenging | Preliminary | Challenging | [5 empty] | 1/29/1994 | Challenging | 06:54:00 |  | Known | 20 | 20 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 1/29/1994 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
59 | 60 | 2/3/1994 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other | [5 empty] | 2/3/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Ambient pressure, within a component | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/3/1994 | Not Challenging | Final | Not Challenging | [5 empty] | 2/3/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable | [6 empty] | 2/3/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
60 | 61 | 4/3/1994 | Challenging | No |  | Turbine Building | Main Generator System | Other |  | 13 KV or greater | AC |  |  | 4/3/1994 | Challenging | Electrical arcing or sparks (non-HEAF) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes | [8 empty] | 4/3/1994 | Challenging | Preliminary | Challenging | [5 empty] | 4/3/1994 | Challenging | 06:18:00 | 06:18:00 | Known | 167 | 167 | ailed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression ‐ manually actuated, Hose stream or hose reel | Other: Water | [6 empty] | 4/3/1994 | Challenging | Operate | Hot Standby | 25 | 0 | Scram | Unusual Event | Challenging
61 | 62 | 6/6/1994 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 6/6/1994 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/6/1994 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/6/1994 | Not Challenging | 11:41:00 | 11:41:00 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention | Portable | [6 empty] | 6/6/1994 | Not Challenging | Operate | Operate | 100 | 100 | None | Alert | Not Challenging
62 | 63 | 6/15/1994 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 6/15/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/15/1994 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/15/1994 | Potentially Challenging |  | 01:40:00 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 6/15/1994 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
63 | 64 | 6/1/1994 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/1/1994 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/1/1994 | Challenging | Preliminary | Challenging | [5 empty] | 6/1/1994 | Challenging | 14:55:00 |  | Known | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water | [6 empty] | 6/1/1994 | Challenging | Operate | Operate | 100 | 0 | Scram |  | Challenging
64 | 65 | 7/2/1994 | Challenging | No |  | Turbine Building | Main Generator Output Power System | Other |  | 13 KV or greater | AC |  |  | 7/2/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/2/1994 | Challenging | Preliminary | Challenging | [5 empty] | 7/2/1994 | Challenging | 11:44:00 | 11:44:00 | Known | 31 | 31 | Fire Watch | Unknown | Hose stream or hose reel,Portable manual system (e.g. CO2 cart),Multiple portable fire extinguishers | Portable: Dry Chemical,Other: CO2 | [6 empty] | 7/2/1994 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
65 | 66 | 7/11/1994 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps |  |  |  |  | 7/11/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/11/1994 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/11/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable | [6 empty] | 7/11/1994 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
66 | 67 | 7/29/1994 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Other | [5 empty] | 7/29/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/29/1994 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/29/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable | [6 empty] | 7/29/1994 | Potentially Challenging | Operate | Operate | 87 | 87 | None | Unusual Event | Challenging
67 | 68 | 8/10/1994 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/10/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/10/1994 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 8/10/1994 | Undetermined (PC‐CH) | 13:30:00 |  | Known | 30 | 30 | Fire Watch | Unknown | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water | [6 empty] | 8/10/1994 | Undetermined (PC‐CH) | Operate | Operate | 80 | 80 | None | Unusual Event | Challenging
68 | 69 | 8/29/1994 | Undetermined (NC‐PC) | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 8/29/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 8/29/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 8/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable | [6 empty] | 8/29/1994 | Undetermined (NC‐PC) | Operate | Hot Shutdown | 100 | 0 | Scram |  | Not Challenging
69 | 70 | 10/26/1994 | Not Challenging | Yes |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 10/26/1994 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/26/1994 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/26/1994 | Not Challenging | 14:26:00 |  | Known | 569 | 569 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable | [6 empty] | 10/26/1994 | Not Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Not Challenging
70 | 71 | 3/1/1995 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 3/1/1995 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/1/1995 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 3/1/1995 | Undetermined (PC‐CH) |  | 03:35:00 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable | [6 empty] | 3/1/1995 | Undetermined (PC‐CH) | Operate | Operate | 75 | 75 | None | Unusual Event | Not Challenging
71 | 72 | 4/14/1995 | Challenging | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Other | [5 empty] | 4/14/1995 | Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/14/1995 | Challenging | Preliminary | Challenging | [5 empty] | 4/14/1995 | Challenging | 05:10:00 | 05:10:00 | Known | 19 | 19 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water | [6 empty] | 4/14/1995 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
72 | 73 | 6/1/1995 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | [6 empty] | 6/1/1995 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/1/1995 | Not Challenging | Final | Not Challenging | [5 empty] | 6/1/1995 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable | [6 empty] | 6/1/1995 | Not Challenging | Hot Standby | Hot Standby | 0 | 0 | None | Unusual Event | Not Challenging
73 | 74 | 6/10/1995 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear | 4KV | AC |  |  | 6/10/1995 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | Yes | [8 empty] | 6/10/1995 | Challenging | Preliminary | Challenging | [5 empty] | 6/10/1995 | Challenging | 08:57:00 | 08:57:00 | Known | 136 | 136 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify],Other: Water | [6 empty] | 6/10/1995 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
74 | 75 | 8/22/1995 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 8/22/1995 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No | [8 empty] | 8/22/1995 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/22/1995 | Potentially Challenging | 11:25:00 |  | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable | [6 empty] | 8/22/1995 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
75 | 76 | 10/21/1995 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 10/21/1995 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes | [8 empty] | 10/21/1995 | Challenging | Preliminary | Challenging | [5 empty] | 10/21/1995 | Challenging | 09:38:00 |  | Known | 30 | 30 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other:AFFF foam | [6 empty] | 10/21/1995 | Challenging | Refueling | Refueling | 0 | 0 | LOOP | Unusual Event | Challenging
76 | 77 | 12/10/1995 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Other | [5 empty] | 12/10/1995 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/10/1995 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/10/1995 | Not Challenging |  |  | Estimated | 13 | 13 | Unknown | Unknown | Unknown | Portable: | [6 empty] | 12/10/1995 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
77 | 78 | 1/24/1996 | Challenging | No |  | Auxiliary Building (PWR) | Essential Service Water System | Other | [5 empty] | 1/24/1996 | Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Interior finish |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | No | [8 empty] | 1/24/1996 | Challenging | Preliminary | Challenging | [5 empty] | 1/24/1996 | Challenging | 06:15:00 |  | Known | 13 | 13 | Fire Watch | Plant area had installed detection which actuated | Hose stream or hose reel | Portable: Water | [6 empty] | 1/24/1996 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
78 | 79 | 2/5/1996 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 2/5/1996 | Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 2/5/1996 | Challenging | Preliminary | Potentially Challenging | [5 empty] | 2/5/1996 | Challenging | 15:45:00 |  | Known | 37 | 37 | Unknown | Unknown | Unknown | Portable: | [6 empty] | 2/5/1996 | Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
79 | 80 | 2/29/1996 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 2/29/1996 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/29/1996 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 2/29/1996 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/29/1996 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
80 | 81 | 3/25/1996 | Undetermined (NC‐PC) | No |  | Radwaste Building | Offgas System (BWR) | Other | [5 empty] | 3/25/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/25/1996 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 3/25/1996 | Undetermined (NC‐PC) |  | 20:10:00 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable: | [6 empty] | 3/25/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
81 | 82 | 3/27/1996 | Potentially Challenging | No |  | Turbine Building | Condensate System | Other | [5 empty] | 3/27/1996 | Potentially Challenging | Unknown | Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/27/1996 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/27/1996 | Potentially Challenging |  | 20:00:00 | Known | 14 | 14 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off) | Portable: | [6 empty] | 3/27/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
82 | 83 | 4/4/1996 | Potentially Challenging | No | Main Control Room | Control building | Low Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 110V | AC |  |  | 4/4/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/4/1996 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/4/1996 | Potentially Challenging | 17:00:00 | 17:00:00 | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: | [6 empty] | 4/4/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Alert | Challenging
83 | 84 | 4/19/1996 | Potentially Challenging | No | Main Control Room | Radwaste Building |  | Electrical panel | Main control board (i.e., the ma | 110V | AC |  |  | 4/19/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/19/1996 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/19/1996 | Potentially Challenging | 10:19:00 |  | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/19/1996 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram |  | Challenging
84 | 85 | 5/13/1996 | Not Challenging | Yes |  | Other (Specify in comments) |  | Air Compressors | [5 empty] | 5/13/1996 | Not Challenging | Unknown | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 5/13/1996 | Not Challenging | Final | Challenging | [5 empty] | 5/13/1996 | Not Challenging | 18:48:00 | 18:48:00 | Known | 13 | 13 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 5/13/1996 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
85 | 86 | 6/23/1996 | Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 6/23/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | Yes | [8 empty] | 6/23/1996 | Challenging | Preliminary | Challenging | [5 empty] | 6/23/1996 | Challenging | 17:14:00 |  | Known | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable: | [6 empty] | 6/23/1996 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
86 | 87 | 8/19/1996 | Potentially Challenging | No |  | Reactor Building (BWR) | Reactor Core Isolation Cooling System (BWR) | Pumps | Turbine‐driven pump |  |  |  |  | 8/19/1996 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/19/1996 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/19/1996 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable: | [6 empty] | 8/19/1996 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert | Challenging
87 | 88 | 10/5/1996 | Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 10/5/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes | [8 empty] | 10/5/1996 | Challenging | Preliminary | Challenging | [5 empty] | 10/5/1996 | Challenging | 13:13:00 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable: | [6 empty] | 10/5/1996 | Challenging | Operate | Operate | 0 | 0 | None | Unusual Event | Challenging
88 | 89 | 10/15/1996 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Motor control center | 480V | AC |  |  | 10/15/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/15/1996 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/15/1996 | Potentially Challenging | 13:15:00 |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g.open circuit breaker) | Portable: | [6 empty] | 10/15/1996 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Challenging
89 | 90 | 10/17/1996 | Challenging | No | Containment/Drywell | Containment (PWR) | Feedwater System | Other | [5 empty] | 10/17/1996 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/17/1996 | Challenging | Preliminary | Challenging | [5 empty] | 10/17/1996 | Challenging | 16:07:00 |  | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: CO2，Other: Water | [6 empty] | 10/17/1996 | Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None | Unusual Event | Challenging
90 | 91 | 11/19/1996 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Instrument and Uninterruptible Power System | [6 empty] | 11/19/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 11/19/1996 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/19/1996 | Undetermined (NC‐PC) | 14:59:00 |  | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable: | [6 empty] | 11/19/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
91 | 92 | 11/22/1996 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 11/22/1996 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 11/22/1996 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/22/1996 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable: | [6 empty] | 11/22/1996 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
92 | 93 | 3/4/1997 | Potentially Challenging | No | Switchgear Room | Control building | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC |  |  | 3/4/1997 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/4/1997 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/4/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 3/4/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
93 | 94 | 8/1/1997 | Potentially Challenging | No |  | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC |  |  | 8/1/1997 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Mixed | Other (Specify) | Flaming combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to the object of origin | No | [8 empty] | 8/1/1997 | Potentially Challenging | Final | Challenging | [5 empty] | 8/1/1997 | Potentially Challenging |  | 00:02:00 | Estimated | 18 | 18 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: CO2 | [6 empty] | 8/1/1997 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram |  | Challenging
94 | 95 | 10/9/1997 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 10/9/1997 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/9/1997 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/9/1997 | Potentially Challenging | 23:02:00 |  | Known | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher，Other (specify in comments | Portable: CO2 | [6 empty] | 10/9/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert | Challenging
95 | 96 | 10/28/1997 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 10/28/1997 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Interior finish |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/28/1997 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/28/1997 | Not Challenging | 08:45:00 | 08:45:00 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)，Fuel supply removed (simple manual action e.g. valve turn off) | Portable: | [6 empty] | 10/28/1997 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Not Challenging
96 | 97 | 6/10/1998 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC |  |  | 6/10/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/10/1998 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/10/1998 | Potentially Challenging | 02:00:00 | 02:10:00 | Known | 39 | 39 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: | [6 empty] | 6/10/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
97 | 98 | 10/8/1998 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin |  |  |  |  | 10/8/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/1998 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/8/1998 | Potentially Challenging |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | Portable: | [6 empty] | 10/8/1998 | Potentially Challenging | Refueling | Refueling | 0 | 0 | Entered an LCO | Alert | Challenging
98 | 99 | 10/10/1998 | Not Challenging | No |  | Radwaste Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  |  | 10/10/1998 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/10/1998 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/10/1998 | Not Challenging | 13:12:00 | 13:12:00 | Known | 18 | 18 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable: | [6 empty] | 10/10/1998 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Not Challenging
99 | 100 | 5/15/2000 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Bus Duct | Segmented Bus Duct | 13 KV or greater | AC |  |  | 5/15/2000 | Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | Yes | [8 empty] | 5/15/2000 | Challenging | Preliminary | Challenging | [5 empty] | 5/15/2000 | Challenging | 00:25:00 | 00:25:00 | Known | 78 | 78 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2，Other: CO2 | [6 empty] | 5/15/2000 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
100 | 101 | 9/3/2000 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 9/3/2000 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/3/2000 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 9/3/2000 | Undetermined (PC‐CH) | 14:40:00 | 14:40:00 | Known | 29 | 29 | Dedicated Fire Watch | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water | [6 empty] | 9/3/2000 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
101 | 102 | 9/4/2000 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 9/4/2000 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/4/2000 | Challenging | Preliminary | Challenging | [5 empty] | 9/4/2000 | Challenging | 11:32:00 |  | Known | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 9/4/2000 | Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
102 | 103 | 9/22/2000 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 9/22/2000 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/22/2000 | Challenging | Preliminary | Challenging | [5 empty] | 9/22/2000 | Challenging | 03:46:00 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water | [6 empty] | 9/22/2000 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
103 | 104 | 10/14/2000 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 480V | AC |  |  | 10/14/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/14/2000 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/14/2000 | Potentially Challenging |  | 18:15:00 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/14/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
104 | 105 | 11/10/2000 | Potentially Challenging | No |  | Radwaste Building | [7 empty] | 11/10/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/10/2000 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/10/2000 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable: | [6 empty] | 11/10/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
105 | 106 | 2/3/2001 | Challenging | No |  | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 2/3/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No | [8 empty] | 2/3/2001 | Challenging | Preliminary | Challenging | [5 empty] | 2/3/2001 | Challenging | 15:14:00 |  | Known | 156 | 156 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable: | [6 empty] | 2/3/2001 | Challenging | Operate | Hot Standby | 39 | 0 | Scram | Unusual Event | Challenging
106 | 107 | 3/21/2001 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 3/21/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Cleaning solvents or paint | Contained within component | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/21/2001 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/21/2001 | Potentially Challenging | 22:11:00 |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 3/21/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert | Challenging
107 | 108 | 4/6/2001 | Not Challenging | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Other | [5 empty] | 4/6/2001 | Not Challenging | Unknown |  | Unknown |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 4/6/2001 | Not Challenging | Final | Challenging | [5 empty] | 4/6/2001 | Not Challenging | 00:00:00 | 00:00:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable: | [6 empty] | 4/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
108 | 109 | 4/24/2001 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/24/2001 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No | [8 empty] | 4/24/2001 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 4/24/2001 | Undetermined (PC‐CH) | 01:48:00 | 01:48:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 4/24/2001 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
109 | 110 | 6/25/2001 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/25/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/25/2001 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/25/2001 | Potentially Challenging | 04:33:00 |  | Known | 16 | 16 | Unknown | Unknown | Unknown | Portable: | [6 empty] | 6/25/2001 | Potentially Challenging | Operate | Operate | 100 | 60 | Reduced Power | Alert | Challenging
110 | 111 | 8/2/2001 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 8/2/2001 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/2/2001 | Challenging | Final | Challenging | [5 empty] | 8/2/2001 | Challenging | 08:23:00 |  | Known | 22 | 22 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water | [6 empty] | 8/2/2001 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
111 | 112 | 8/3/2001 | Undetermined (PC‐CH) | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 8/3/2001 | Undetermined (PC‐CH) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 8/3/2001 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 8/3/2001 | Undetermined (PC‐CH) | 08:40:00 | 08:40:00 | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown | Portable: | [6 empty] | 8/3/2001 | Undetermined (PC‐CH) | Operate | Hot Standby | 20 | 0 | Scram | Unusual Event | Challenging
112 | 113 | 6/12/2002 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 13 KV or greater | AC |  |  | 6/12/2002 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/12/2002 | Challenging | Final | Challenging | [5 empty] | 6/12/2002 | Challenging | 13:45:00 | 13:45:00 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable: | [6 empty] | 6/12/2002 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert | Challenging
113 | 114 | 8/21/2002 | Challenging | No |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 8/21/2002 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/21/2002 | Challenging | Final | Challenging | [5 empty] | 8/21/2002 | Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 8/21/2002 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Unusual Event | Challenging
114 | 115 | 8/22/2002 | Challenging | No |  | Turbine Building | Hydrogen Supply System | Other | [5 empty] | 8/22/2002 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/22/2002 | Challenging | Final | Challenging | [5 empty] | 8/22/2002 | Challenging | 16:32:00 | 16:32:00 | Known | 18 | 18 | Ultraviolet flame detector | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified，Multiple portable fire extinguishers，Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water，Other: Water | [6 empty] | 8/22/2002 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
115 | 116 | 10/3/2002 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 10/3/2002 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/3/2002 | Challenging | Final | Challenging | [5 empty] | 3/18/2003 | Not Challenging | 20:37:00 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: | [6 empty] | 10/3/2002 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
116 | 117 | 10/9/2002 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC |  |  | 10/9/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/9/2002 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/9/2002 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable: | [6 empty] | 10/9/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
117 | 118 | 1/15/2003 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 1/15/2003 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/15/2003 | Challenging | Final | Challenging | [5 empty] | 1/15/2003 | Challenging | 20:10:00 | 20:10:00 | Known | 35 | 35 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water | [6 empty] | 1/15/2003 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
118 | 119 | 3/18/2003 | Not Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Electric motor driven pumps | 480V | AC |  |  | 3/18/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No | [8 empty] | 3/18/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/18/2003 | Not Challenging | 20:37:00 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: | [6 empty] | 3/18/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Alert | Not Challenging
119 | 120 | 4/7/2003 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 4/7/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | No damage | No | [8 empty] | 4/7/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/7/2003 | Potentially Challenging | 22:01:00 |  | Known | 33 | 33 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other (specify in comments) | Portable: | [6 empty] | 4/7/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
120 | 121 | 4/26/2003 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 7KV | AC |  |  | 4/26/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/26/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 4/26/2003 | Undetermined (NC‐PC) | 17:46:00 | 17:46:00 | Known | 37 | 37 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart)，Single Portable fire extinguisher | Portable: | [6 empty] | 4/26/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
121 | 122 | 4/29/2003 | Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 4/29/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 4/29/2003 | Challenging | Final | Challenging | [5 empty] | 4/29/2003 | Challenging | 02:58:00 |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated，Hose stream or hose reel | Portable: Other [specify]，Other: CO2 | [6 empty] | 4/29/2003 | Challenging | Operate | Hot Standby | 60 | 0 | Scram | Unusual Event | Challenging
122 | 123 | 10/16/2003 | Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 10/16/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Not available | No | [8 empty] | 10/16/2003 | Challenging | Preliminary | Challenging | [5 empty] | 10/16/2003 | Challenging |  |  | Estimated | 23 | 23 | Unknown | Unknown | Hose stream or hose reel，Single Portable fire extinguisher | Portable: Dry Chemical，Other: AFFF foam | [6 empty] | 10/16/2003 | Challenging | Operate | Operate | 100 | 65 | Reduced Power | Unusual Event | Challenging
123 | 124 | 10/28/2003 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Other |  | 13 KV or greater | AC |  |  | 10/28/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/28/2003 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/28/2003 | Potentially Challenging | 01:30:00 | 01:30:00 | Known | 317 | 317 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable: | [6 empty] | 10/28/2003 | Potentially Challenging | Operate | Operate | 100 | 0 | Scram |  | Challenging
124 | 125 | 1/6/2004 | Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Cable/Wiring |  | 110KV | AC |  |  | 1/6/2004 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | Yes | [8 empty] | 1/6/2004 | Challenging | Final | Challenging | [5 empty] | 1/6/2004 | Challenging | 12:40:00 | 12:40:00 | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 1/6/2004 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
125 | 126 | 5/21/2004 | Undetermined (PC‐CH) | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 5/21/2004 | Undetermined (PC‐CH) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/21/2004 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 5/21/2004 | Undetermined (PC‐CH) | 21:09:00 | 21:09:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown | Portable: | [6 empty] | 5/21/2004 | Undetermined (PC‐CH) | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
126 | 127 | 6/18/2004 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/18/2004 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/18/2004 | Challenging | Preliminary | Challenging | [5 empty] | 6/18/2004 | Challenging | 06:40:00 | 06:40:00 | Known | 71 | 71 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water | [6 empty] | 6/18/2004 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
127 | 128 | 8/31/2004 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 8/31/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 8/31/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/31/2004 | Potentially Challenging | 07:15:00 | 07:15:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)Power supply removed (simple manual action e.g. open circuit breaker) | Portable: | [6 empty] | 8/31/2004 | Potentially Challenging | Operate | Hot Standby | 95 | 0 | Scram |  | Challenging
128 | 129 | 11/6/2004 | Potentially Challenging | No |  | Turbine Building | Heat Rejection System (Circulating Water) | Other | [5 empty] | 11/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Interior finish |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 11/6/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/6/2004 | Potentially Challenging | 02:52:00 |  | Known | 18 | 18 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: | [6 empty] | 11/6/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
129 | 130 | 12/14/2004 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 12/14/2004 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 12/14/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/14/2004 | Potentially Challenging | 11:40:00 |  | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: | [6 empty] | 12/14/2004 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
130 | 131 | 1/14/2005 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 1/14/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No | [8 empty] | 1/14/2005 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 1/14/2005 | Undetermined (PC‐CH) | 09:53:00 | 09:53:00 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Water | [6 empty] | 1/14/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None | Unusual Event | Not Challenging
131 | 132 | 3/4/2005 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 3/4/2005 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/4/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/4/2005 | Undetermined (NC‐PC) | 14:47:00 | 14:47:00 | Estimated | 64 | 64 | Other plant personnel (in vicinity or passerby) |  | Unknown | Portable: | [6 empty] | 3/4/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None | Unusual Event | Not Challenging
132 | 133 | 5/4/2005 | Potentially Challenging | No | Fuel handling area | Containment (PWR) | Reactor Coolant System | Cable/Wiring |  | 110KV | AC |  |  | 5/4/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 5/4/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/4/2005 | Potentially Challenging | 14:10:00 | 14:10:00 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable: | [6 empty] | 5/4/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
133 | 134 | 6/27/2005 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/27/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes | [8 empty] | 6/27/2005 | Challenging | Final | Challenging | [5 empty] | 6/27/2005 | Challenging | 03:16:00 |  | Known | 27 | 27 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water | [6 empty] | 6/27/2005 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
134 | 135 | 8/25/2005 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 7KV | AC |  |  | 8/25/2005 | otentially Challenging |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light – visibility reduced, but all areas of the space can be seen | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 8/25/2005 | Potentially Challenging | Final | Challenging | [5 empty] | 8/25/2005 | Potentially Challenging | 11:25:00 | 11:25:00 | Known | 112 | 112 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel，Multiple portable fire extinguishers | [7 empty] | 8/25/2005 | Potentially Challenging |  | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
135 | 136 | 10/25/2005 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 10/25/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/25/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/25/2005 | Potentially Challenging | 21:40:00 | 21:40:00 | Known | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable: | [6 empty] | 10/25/2005 | Potentially Challenging |  | Hot Standby | 0 | 0 | None | Unusual Event | Challenging
136 | 137 | 10/29/2005 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 10/29/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No | [8 empty] | 10/29/2005 | Challenging | Final | Challenging | [5 empty] | 10/29/2005 | Challenging | 13:30:00 | 13:30:00 | Known | 28 | 28 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water | [6 empty] | 10/29/2005 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
137 | 138 | 2/11/2006 | Potentially Challenging | No |  | Reactor Building (BWR) | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 2/11/2006 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Interior finish |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/11/2006 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 2/11/2006 | Potentially Challenging | 15:06:00 |  | Known | 154 | 154 | Other plant personnel (in vicinity or passerby | Unknown | Unknown | Portable: | [6 empty] | 2/11/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert | Challenging
138 | 139 | 2/24/2006 | Potentially Challenging | No | Cable vault/tunnel area | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 480V | AC |  |  | 2/24/2006 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Other (Specify) | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 2/24/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/24/2006 | Potentially Challenging | 08:36:00 | 08:36:00 | Known | 153 | 153 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: | [6 empty] | 2/24/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
139 | 140 | 3/20/2006 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC |  |  | 3/20/2006 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 3/20/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 3/20/2006 | Undetermined (NC‐PC) |  | 07:56:00 | Known | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed | [7 empty] | 3/20/2006 | Undetermined (NC‐PC) | Operate | Operate | 82 | 82 | None | Unusual Event | Not Challenging
140 | 141 | 5/1/2006 | Undetermined (PC‐CH) | No |  | Turbine Building | Main Generator Output Power System | Bus Duct | IsoPhase Bus Duct | 13 KV or greater | AC |  |  | 5/1/2006 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 5/1/2006 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 5/1/2006 | Undetermined (PC‐CH) | 04:39:00 | 04:39:00 | Estimated | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 5/1/2006 | Undetermined (PC‐CH) | Operate | Operate | 100 | 60 | Reduced Power | Unusual Event | Challenging
141 | 142 | 5/24/2006 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 5/24/2006 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 5/24/2006 | Challenging | Preliminary | Challenging | [5 empty] | 5/24/2006 | Challenging |  |  | Estimated | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: CO2 | [6 empty] | 5/24/2006 | Challenging | Operate | Operate | 100 | 56 | Reduced Power | Unusual Event | Challenging
142 | 143 | 8/15/2006 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4 KV | AC |  |  | 8/15/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to room of origin | No | [8 empty] | 8/15/2006 | Potentially Challenging | Final | Challenging | [5 empty] | 8/15/2006 | Potentially Challenging | 17:59:00 | 17:59:00 | Known | 36 | 36 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel | [7 empty] | 8/15/2006 | Potentially Challenging | Operate | Operate | 98 | 98 | Entered an LCO | Unusual Event | Challenging
143 | 144 | 10/30/2006 | Potentially Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  |  | 10/30/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/30/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/30/2006 | Potentially Challenging | 12:38:00 | 12:44:00 | Known | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 10/30/2006 | Potentially Challenging | Operate | Operate | 67 | 67 | Entered an LCO | Alert | Challenging
144 | 145 | 11/11/2006 | Not Challenging | No | Fuel handling area | Auxiliary Building (PWR) |  | Cable/Wiring |  | 110V | AC |  |  | 11/11/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/11/2006 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/11/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/11/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Not Challenging
145 | 146 | 2/27/2007 | Undetermined (PC‐CH) | No |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Load center | 480V | AC |  |  | 2/27/2007 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Not available | No | [8 empty] | 2/27/2007 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 2/27/2007 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 2/27/2007 | Undetermined (PC‐CH) | Operate | Operate | 100 | 50 | Reduced Power | Unusual Event | Challenging
146 | 147 | 4/5/2007 | Not Challenging | No |  | Control building | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 4 KV | AC |  |  | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/5/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/5/2007 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable: None | [6 empty] | 4/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None | Alert | Not Challenging
147 | 148 | 4/6/2007 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 4/6/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No | [8 empty] | 4/6/2007 | Challenging | Final | Challenging | [5 empty] | 4/6/2007 | Challenging | 11:09:00 | 11:09:00 | Known | 12 | 12 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water | [6 empty] | 4/6/2007 | Challenging | Operate | Hot Standby | 93 | 0 | Scram | Unusual Event | Challenging
148 | 149 | 4/8/2007 | Potentially Challenging | No | Switchgear Room | Radwaste Building | Low Voltage Power System, Class 1E | Transformers | Dry transformer | 110V | AC |  |  | 4/8/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/8/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/8/2007 | Potentially Challenging | 13:30:00 | 13:30:00 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/8/2007 | Potentially Challenging | Operate | Operate | 95 | 65 | Entered an LCO | Alert | Challenging
149 | 150 | 4/25/2007 | Challenging | No |  | Other (Specify in comments) | Hydrogen Supply System | [6 empty] | 4/25/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No | [8 empty] | 4/25/2007 | Challenging | Final | Challenging | [5 empty] | 4/25/2007 | Challenging | 16:33:00 |  | Known | 28 | 28 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 4/25/2007 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
150 | 151 | 8/1/2007 | Not Challenging | Yes |  | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 4 KV | AC |  |  | 8/1/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No | [8 empty] | 8/1/2007 | Not Challenging | Final | Challenging | [5 empty] | 8/1/2007 | Not Challenging | 01:52:00 | 01:52:00 | Known | 21 | 21 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 8/1/2007 | Not Challenging | Operate | Operate | 100 | 91 | Reduced Power | Unusual Event | Not Challenging
151 | 152 | 10/23/2007 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electrical panel | Motor control center |  |  |  |  | 10/23/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No | [8 empty] | 10/23/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/23/2007 | Potentially Challenging | 22:58:00 | 22:58:00 | Known | 6 | 6 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/23/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Alert | Challenging
152 | 153 | 8/16/2008 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 8/16/2008 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | Yes | [8 empty] | 8/16/2008 | Challenging | Preliminary | Challenging | [5 empty] | 8/16/2008 | Challenging | 23:57:00 |  | Known | 125 | 125 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | [7 empty] | 8/16/2008 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
153 | 154 | 9/20/2008 | Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 9/20/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | [9 empty] | 9/20/2008 | Challenging | Final | Challenging | [5 empty] | 9/20/2008 | Challenging | 20:05:00 | 20:05:00 | Known | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: Water | [6 empty] | 9/20/2008 | Challenging | Operate | Hot Standby | 100 | 0 | Scram | Unusual Event | Challenging
154 | 155 | 11/17/2008 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 11/17/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | No damage | No | [8 empty] | 11/17/2008 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 11/17/2008 | Undetermined (NC‐PC) | 09:11:00 | 09:11:00 | Known | 24 | 24 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/17/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 48 | Reduced Power | Unusual Event | Not Challenging
155 | 156
156 | 157 | 2/1/2009 | Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 2/1/2009 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 2/1/2009 | Challenging | Final | Challenging | [5 empty] | 2/1/2009 | Challenging | 21:56:00 | 21:56:00 | Known | 31 | 31 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water | [6 empty] | 2/1/2009 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
157 | 158 | 6/26/2009 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  |  | 6/26/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/26/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/26/2009 | Potentially Challenging | 19:49:00 | 19:49:00 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 6/26/2009 | Potentially Challenging | Operate | Hot Shutdown | 73 | 0 | Scram | Unusual Event | Challenging
158 | 159 | 1/16/1990 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4 KV | AC |  |  | 1/16/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | Yes | [8 empty] | 1/16/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/16/1990 | Potentially Challenging | 17:24:00 | 17:30:00 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown | [7 empty] | 1/16/1990 | Potentially Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Challenging
159 | 160 | 2/7/2009 | Challenging | No |  | Turbine Building | Main Generator Output Power System | Other | [5 empty] | 2/7/2009 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to fire rated compartment of origin | No | [8 empty] | 2/7/2009 | Challenging | Final | Challenging | [5 empty] | 2/7/2009 | Challenging | 10:46:00 | 10:46:00 | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Hose stream or hose reel | Other: Water | [6 empty] | 2/7/2009 | Challenging | Operate | Hot Standby | 90 | 0 | Scram |  | Challenging
160 | 161 | 4/22/2009 | Potentially Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 4/22/2009 | Potentially Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/22/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/22/2009 | Potentially Challenging | 04:30:00 | 05:00:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/22/2009 | Potentially Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
161 | 162 | 8/5/2009 | Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 7 KV | AC |  |  | 8/5/2009 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Single Cable Tray | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to floor of origin | No | [8 empty] | 8/5/2009 | Challenging | Preliminary | Challenging | [5 empty] | 8/5/2009 | Challenging | 07:50:00 | 07:50:00 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/5/2009 | Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Alert | Challenging
162 | 163 | 10/12/2009 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 10/12/2009 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/12/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/12/2009 | Potentially Challenging | 15:51:00 | 15:51:00 | Known | 22 | 22 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 10/12/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
163 | 164 | 3/28/1990 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 3/28/1990 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 3/28/1990 | Not Challenging | Final | Challenging | [5 empty] | 3/28/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water | [6 empty] | 3/28/1990 | Not Challenging | Operate | Hot Shutdown | 100 | 0 | Scram | Unusual Event | Not Challenging
164 | 165
165 | 166
166 | 167
167 | 168 | 11/13/2003 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | [7 empty] | 11/13/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Mixed | Unknown | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/13/2003 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 11/13/2003 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 11/13/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
168 | 169 | 11/13/2003 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 7 KV | AC |  |  | 11/13/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No | [8 empty] | 11/13/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/13/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 11/13/2003 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
169 | 170 | 11/21/2003 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 11/21/2003 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes | [8 empty] | 11/21/2003 | Not Challenging | Final | Challenging | [5 empty] | 11/21/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 11/21/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
170 | 171
171 | 172 | 12/7/2003 | Challenging | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump | 480V | AC |  |  | 12/7/2003 | Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to room of origin | No | [8 empty] | 12/7/2003 | Challenging | Final | Challenging | [5 empty] | 12/7/2003 | Not Challenging |  | 01:50:00 | Known | 130 | 130 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | [7 empty] | 12/7/2003 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
172 | 173 | 12/13/2003 | Not Challenging | No |  | Control building |  | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 12/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Overheating – no smoldering or flaming combustion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/13/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 12/13/2003 | Not Challenging | 23:16:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | [7 empty] | 12/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
173 | 174 | 12/30/2003 | Not Challenging | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 12/30/2003 | Not Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/30/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 12/30/2003 | Not Challenging | 18:00:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 12/30/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
174 | 175 | 11/22/2009 | Challenging | No | Switchgear Room | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear | 7 KV | AC |  |  | 11/22/2009 | Challenging |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to part of room or area of origin | No | [8 empty] | 11/22/2009 | Challenging | Final | Challenging | [5 empty] | 11/22/2009 | Challenging | 15:41:00 | 15:41:00 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | [7 empty] | 11/22/2009 | Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Unusual Event | Challenging
175 | 176 | 12/12/2009 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/12/2009 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No | [8 empty] | 12/12/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/12/2009 | Potentially Challenging |  |  | Estimated | 23 | 23 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | Other: Water | [6 empty] | 12/12/2009 | Potentially Challenging | Operate | Operate | 100 | 97 |  | Unusual Event | Challenging
176 | 177
177 | 178
178 | 179
179 | 180
180 | 181 | 2/13/1997 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC |  |  | 2/13/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage） | No | [8 empty] | 2/13/1997 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/13/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Gas Ionization | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 2/13/1997 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
181 | 182
182 | 183
183 | 184 | 6/27/1997 | Challenging | No | Battery Room | Control building | DC Power System | Electrical panel | Battery charger | 125VDC | DC |  |  | 6/27/1997 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No | [8 empty] | 6/27/1997 | Challenging | Final | Challenging | [5 empty] | 6/27/1997 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify] | [6 empty] | 6/27/1997 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
184 | 185 | 3/23/1998 | Not Challenging | No | Main Control Room | Control building | General Ventillation Systems | Transformers | Other (Capacitor Voltage, Poten | 110V | AC |  |  | 3/23/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/23/1998 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/23/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/23/1998 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
185 | 186 | 5/14/1998 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Electrical panel | Other instrument/control cabin | 110V | AC |  |  | 5/14/1998 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/14/1998 | Not Challenging | Final | Not Challenging | [5 empty] | 5/14/1998 | Not Challenging | 14:40:00 |  | Known | 14 | 14 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/14/1998 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
186 | 187 | 8/16/1999 | Potentially Challenging | No |  | Turbine Building | Condensate System | Electrical panel | Other instrument/control cabin | 110V | AC |  |  | 8/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 8/16/1999 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/16/1999 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/16/1999 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
187 | 188 | 8/24/1999 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Electrical panel | Motor control center | 480V | AC |  |  | 8/24/1999 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/24/1999 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/24/1999 | Potentially Challenging |  |  | Estimated | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown,Power supply removed (simple manual action e.g. open circuit,breaker) | [7 empty] | 8/24/1999 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
188 | 189 | 10/14/1996 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 10/14/1996 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to part of room or area of origin | No | [8 empty] | 10/14/1996 | Not Challenging | Final | Challenging | [5 empty] | 10/14/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/14/1996 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
189 | 190 | 3/18/1998 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 3/18/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/18/1998 | Not Challenging | Final | Not Challenging | [5 empty] | 3/18/1998 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/18/1998 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
190 | 191 | 11/11/1998 | Not Challenging | No | Switchgear Room | Auxiliary Building (PWR) |  | Electrical panel | Motor control center |  |  |  |  | 11/11/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/11/1998 | Not Challenging | Final | Not Challenging | [5 empty] | 11/11/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/11/1998 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
191 | 192 | 5/15/1999 | Not Challenging | No | Main Control Room | Control building | Main Turbine System | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 5/15/1999 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/15/1999 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/15/1999 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
192 | 193 | 7/31/1991 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 7/31/1991 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/31/1991 | Not Challenging | Final | Not Challenging | [5 empty] | 7/31/1991 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/31/1991 | Not Challenging | Operate | Operate | 97 | 97 | None |  | Not Challenging
193 | 194 | 5/22/1990 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 5/22/1990 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Contained within reservoir | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes | [8 empty] | 5/22/1990 | Potentially Challenging | Final | Challenging | [5 empty] | 5/22/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/22/1990 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
194 | 195 | 3/21/1992 | Not Challenging | No |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 3/21/1992 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/21/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 3/21/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/21/1992 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
195 | 196
196 | 197
197 | 198
198 | 199 | 1/22/1990 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Pumps | Electric motor driven pumps |  |  |  |  | 1/22/1990 | Potentially Challenging |  | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/22/1990 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 1/22/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 1/22/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
199 | 200 | 2/6/1990 | Not Challenging | Yes |  | Other (Specify in comments) | Other | [6 empty] | 2/6/1990 | Not Challenging | Personnel error: Misuse of heating devices | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 2/6/1990 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/6/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/6/1990 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
200 | 201 | 3/8/1990 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps |  |  |  |  | 3/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/8/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/8/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/8/1990 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
201 | 202 | 3/23/1990 | Potentially Challenging | No | Main Control Room | Radwaste Building | Low Voltage Power System, Class 1E | Electrical panel | Main control board (i.e., the ma | 110V | AC |  |  | 3/23/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/23/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/23/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 3/23/1990 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
202 | 203 | 4/6/1990 | Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 4/6/1990 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes | [8 empty] | 4/6/1990 | Challenging | Preliminary | Challenging | [5 empty] | 4/6/1990 | Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/6/1990 | Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
203 | 204 | 4/9/1990 | Not Challenging | No |  | Radwaste Building |  | Other |  | 480V | AC |  |  | 4/9/1990 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/9/1990 | Not Challenging | Final | Not Challenging | [5 empty] | 4/9/1990 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/9/1990 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
204 | 205
205 | 206 | 6/11/1990 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 6/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 6/11/1990 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 6/11/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/11/1990 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
206 | 207 | 7/15/1990 | Undetermined (PC‐CH) | No | Cable vault/tunnel area | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring | [5 empty] | 7/15/1990 | Undetermined (PC-CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/15/1990 | Undetermined (PC‐CH) | Preliminary | Challenging | [5 empty] | 7/15/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon | [6 empty] | 7/15/1990 | Undetermined (PC‐CH) | Unknown | Unknown |  |  | None |  | Challenging
207 | 208 | 8/8/1990 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 8/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/8/1990 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/8/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/8/1990 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
208 | 209 | 8/22/1990 | Not Challenging | Yes | Switchgear Room | Control building | Medium Voltage Power System (601V to 35kV) |  | Motor control center |  |  |  |  | 8/22/1990 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/22/1990 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/22/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 8/22/1990 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
209 | 210 | 10/16/1990 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring | [5 empty] | 10/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/16/1990 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 10/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Dry Chemical | [6 empty] | 10/16/1990 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
210 | 211 | 11/2/1990 | Potentially Challenging | No |  | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 480V | AC |  |  | 11/2/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/2/1990 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/2/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/2/1990 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
211 | 212 | 12/5/1990 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 12/5/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/5/1990 | Not Challenging | Final | Not Challenging | [5 empty] | 12/5/1990 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/5/1990 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
212 | 213
213 | 214 | 3/8/1991 | Potentially Challenging | No |  | Other (Specify in comments) |  | Boilers | [5 empty] | 3/8/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/8/1991 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/8/1991 | Potentially Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Multiple portable fire extinguishers | [7 empty] | 3/8/1991 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
214 | 215 | 3/11/1991 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 3/11/1991 | Not Challenging |  | In_Situ | Other (Specify) |  | Flaming combustion – external to component |  |  | Confined to part of room or area of origin | [9 empty] | 3/11/1991 | Not Challenging | Final | Challenging | [5 empty] | 3/11/1991 | Not Challenging |  |  | Unknown | 0 | 0 |  |  | Unknown | [7 empty] | 3/11/1991 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
215 | 216 | 7/12/1991 | Potentially Challenging | No |  |  | General Ventillation Systems | Cable/Wiring | [5 empty] | 7/12/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 7/12/1991 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/12/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 7/12/1991 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
216 | 217 | 7/19/1991 | Potentially Challenging | No |  | Other (Specify in comments) |  | Pumps | Diesel driven pumps |  |  |  |  | 7/19/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/19/1991 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/19/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/19/1991 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
217 | 218 | 9/12/1991 | Undetermined (NC‐PC) | No |  | Turbine Building | Turbine Lube Oil System | Lube Oil |  | 480V | AC |  |  | 9/12/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/12/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 9/12/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/12/1991 | Undetermined (NC‐PC) | Operate | Operate |  |  | None |  | Not Challenging
218 | 219 | 9/27/1991 | Undetermined (PC‐CH) | No |  | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 9/27/1991 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/27/1991 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 9/27/1991 | Undetermined (PC‐CH) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/27/1991 | Undetermined (PC‐CH) | Unknown | Unknown |  |  |  |  | Challenging
219 | 220 | 10/20/1991 | Potentially Challenging | No | Battery Room | Other (Specify in comments) | DC Power System | Transformers | Other (Capacitor Voltage, Poten | 480V | AC |  |  | 10/20/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/20/1991 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/20/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/20/1991 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
220 | 221 | 10/23/1991 | Not Challenging | No |  | Control building | Medium Voltage Power System, Class 1E | Transformers | Other (Capacitor Voltage, Poten | 480V | AC |  |  | 10/23/1991 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/23/1991 | Not Challenging | Final | Not Challenging | [5 empty] | 10/23/1991 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/23/1991 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
221 | 222 | 2/1/1992 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | Low Voltage Power System (600V and less) | Other |  | 110V | AC |  |  | 2/1/1992 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No | [8 empty] | 2/1/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 2/1/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/1/1992 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
222 | 223 | 3/3/1992 | Not Challenging | No | Switchgear Room |  | Instrument and Uninterruptible Power System | Electrical panel | Inverter |  |  |  |  | 3/3/1992 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/3/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 3/3/1992 | Not Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/3/1992 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
223 | 224 | 3/8/1992 | Undetermined (NC‐PC) | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  |  | 3/8/1992 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/8/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/8/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | [7 empty] | 3/8/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
224 | 225 | 3/23/1992 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 3/23/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/23/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/1992 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/23/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
225 | 226 | 4/17/1992 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/17/1992 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 4/17/1992 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 4/17/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/17/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
226 | 227 | 6/9/1992 | Not Challenging | No |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/9/1992 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/9/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 6/9/1992 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed | [7 empty] | 6/9/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
227 | 228 | 8/14/1992 | Potentially Challenging | No |  | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps | 250VDC | DC |  |  | 8/14/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 8/14/1992 | Potentially Challenging | Final | Challenging | [5 empty] | 8/14/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 8/14/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
228 | 229 | 8/21/1992 | Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 8/21/1992 | Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable Tray | Other (specify) | Unknown | Unknown | Confined to the object of origin | Yes | [8 empty] | 8/21/1992 | Challenging | Preliminary | Challenging | [5 empty] | 8/21/1992 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | [9 empty] | 8/21/1992 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
229 | 230 | 8/31/1992 | Potentially Challenging | No |  | Reactor Building (BWR) | Offgas System (BWR) | Other | [5 empty] | 8/31/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/31/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/31/1992 | Potentially Challenging |  |  | Estimated | 85 | 85 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Supervised burn out,Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 8/31/1992 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
230 | 231 | 10/22/1992 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 10/22/1992 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/22/1992 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 10/22/1992 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/22/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
231 | 232 | 10/27/1992 | Not Challenging | Yes |  | Main Transformer or Switch Yard | [7 empty] | 10/27/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 10/27/1992 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/27/1992 | Not Challenging |  |  | Estimated | 46 | 46 | Unknown | Unknown | Unknown | [7 empty] | 10/27/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
232 | 233 | 11/29/1992 | Potentially Challenging | No |  | Control building | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 11/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/29/1992 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/29/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/29/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
233 | 234 | 12/16/1992 | Not Challenging | No | Fuel handling area | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 12/16/1992 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/16/1992 | Not Challenging | Final | Not Challenging | [5 empty] | 12/16/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/16/1992 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
234 | 235 | 12/30/1992 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor | Fans | 480V | AC |  |  | 12/30/1992 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/30/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/30/1992 | Potentially Challenging |  |  | Estimated | 25 | 25 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/30/1992 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
235 | 236 | 1/6/1993 | Undetermined (NC‐PC) | No | Main Control Room | Control building |  | Other | [5 empty] | 1/6/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 1/6/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/6/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | [7 empty] | 1/6/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
236 | 237 | 3/19/1993 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 3/19/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/19/1993 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/19/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Other: Water | [6 empty] | 3/19/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
237 | 238 | 4/1/1993 | Potentially Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 4/1/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 4/1/1993 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/1/1993 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
238 | 239 | 7/14/1993 | Potentially Challenging | No |  | Turbine Building | General Ventillation Systems | Other | [5 empty] | 7/14/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/14/1993 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/14/1993 | Potentially Challenging |  |  | Estimated | 25 | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/14/1993 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
239 | 240 | 7/19/1993 | Undetermined (PC‐CH) | No | Containment/Drywell | Containment (PWR) | [7 empty] | 7/19/1993 | Undetermined (PC‐CH） | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/19/1993 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 7/19/1993 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel | Other: Water | [6 empty] | 7/19/1993 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None |  | Challenging
240 | 241 | 11/3/1993 | Potentially Challenging | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 11/3/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 11/3/1993 | Potentially Challenging | Final | Challenging | [5 empty] | 11/3/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/3/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
241 | 242 | 11/13/1993 | Undetermined (NC‐PC) | No |  | Turbine Building | Diesel Fuel Oil System | Boilers | Auxiliary or Heating Boiler |  |  |  |  | 11/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 11/13/1993 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 11/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 11/13/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
242 | 243 | 12/1/1993 | Potentially Challenging | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 12/1/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 12/1/1993 | Potentially Challenging | Final | Challenging | [5 empty] | 12/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 12/1/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
243 | 244 | 12/7/1993 | Undetermined (PC‐CH) | No |  | Turbine Building | [7 empty] | 12/7/1993 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 12/7/1993 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 12/7/1993 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart) | [7 empty] | 12/7/1993 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None |  | Challenging
244 | 245 | 12/16/1993 | Not Challenging | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 12/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/16/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 12/16/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 12/16/1993 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
245 | 246 | 1/12/1994 | Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 1/12/1994 | Challenging | Personnel error: Misuse of material ignited | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to room of origin | No | [8 empty] | 1/12/1994 | Challenging | Preliminary | Challenging | [5 empty] | 1/12/1994 | Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Hose stream or hose reel | Other: Water | [6 empty] | 1/12/1994 | Challenging | Unknown | Unknown |  |  | None |  | Challenging
246 | 247 | 1/12/1994 | Undetermined (PC‐CH) | No |  | Turbine Building | Auxiliary/Emergency Feedwater System (PWR) | Pumps | Electric motor driven pumps |  |  |  |  | 1/12/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No | [8 empty] | 1/12/1994 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 1/12/1994 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable: Other [specify] | [6 empty] | 1/12/1994 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
247 | 248 | 3/5/1994 | Undetermined (PC‐CH) | No |  | Turbine Building | [7 empty] | 3/5/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No | [8 empty] | 3/5/1994 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 3/5/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/5/1994 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None |  | Challenging
248 | 249 | 3/7/1994 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) |  | Electric Motor | Fans |  |  |  |  | 3/7/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 3/7/1994 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 3/7/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed | [7 empty] | 3/7/1994 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None |  | Challenging
249 | 250 | 7/19/1994 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 7/19/1994 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/19/1994 | Potentially Challenging | Final | Challenging | [5 empty] | 7/19/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated | Other: Water | [6 empty] | 7/19/1994 | Potentially Challenging | Operate | Operate | 0 | 0 | Scram |  | Challenging
250 | 251 | 10/11/1994 | Potentially Challenging | No | Switchgear Room |  | Medium Voltage Power System (601V to 35kV) | Transformers | Dry transformer | 4 KV | AC |  |  | 10/11/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/11/1994 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/11/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/11/1994 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
251 | 252 | 3/18/1995 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | Cable/Wiring | [6 empty] | 3/18/1995 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 3/18/1995 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 3/18/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Automatic fixed ‐ thermally actuated | [7 empty] | 3/18/1995 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
252 | 253 | 7/6/1995 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear |  |  |  |  | 7/6/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/6/1995 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/6/1995 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 7/6/1995 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
253 | 254 | 9/25/1995 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 9/25/1995 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/25/1995 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC) | [5 empty] | 9/25/1995 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/25/1995 | Undetermined (PC‐CH) | Unknown | Unknown |  |  | None |  | Challenging
254 | 255 | 11/19/1995 | Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Transformers | Dry transformer |  |  |  |  | 11/19/1995 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | No | [8 empty] | 11/19/1995 | Challenging | Preliminary | Challenging | [5 empty] | 11/19/1995 | Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 11/19/1995 | Challenging | Unknown | Unknown |  |  |  |  | Challenging
255 | 256 | 7/22/1996 | Undetermined (NC‐PC) | No |  |  |  | Cable/Wiring | [5 empty] | 7/22/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/22/1996 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/22/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 7/22/1996 | Undetermined (NC‐PC) | Unknown | Unknown |  |  | Scram |  | Not Challenging
256 | 257 | 10/22/1997 | Not Challenging | No |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Inverter |  |  |  |  | 10/22/1997 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/22/1997 | Not Challenging | Final | Not Challenging | [5 empty] | 10/22/1997 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/22/1997 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
257 | 258 | 11/3/1997 | Undetermined (PC‐CH) | No |  | Turbine Building | Turbine Lube Oil System | Lube Oil | [5 empty] | 11/3/1997 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 11/3/1997 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 11/3/1997 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 11/3/1997 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 | None |  | Challenging
258 | 259 | 12/26/1997 | Potentially Challenging | No |  | Control building |  | Other | [5 empty] | 11/26/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 12/26/1997 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/26/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify] | [6 empty] | 12/26/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
259 | 260 | 2/3/1998 | Potentially Challenging | No |  | Other (Specify in comments) |  | Pumps | Diesel driven pumps |  |  |  |  | 2/3/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/3/1998 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 2/3/1998 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/3/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
260 | 261 | 5/11/1998 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4 KV | AC |  |  | 5/11/1998 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/11/1998 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/11/1998 | Not Challenging | 19:50:00 | 19:50:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/11/1998 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
261 | 262 | 2/19/1999 | Undetermined (PC‐CH) | No |  | Turbine Building |  | Air Compressors | [5 empty] | 2/19/1999 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/19/1999 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC) | [5 empty] | 2/19/1999 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 2/19/1999 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
262 | 263 | 4/25/1999 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps |  |  |  |  | 4/25/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/25/1999 | Not Challenging | Final | Not Challenging | [5 empty] | 4/25/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/25/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
263 | 264 | 10/20/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 10/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 10/20/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/20/2001 | Not Challenging | 11:01:00 | 11:01:00 | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 10/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
264 | 265 | 9/23/2006 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other | [5 empty] | 9/23/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/23/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 9/23/2006 | Not Challenging | 09:40:00 | 09:40:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/23/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
265 | 266 | 11/9/2006 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 11/9/2006 | Potentially Challenging | Unknown | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/9/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/9/2006 | Potentially Challenging |  | 11:30:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 11/9/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
266 | 267 | 6/1/2000 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | [7 empty] | 6/1/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (Specify) | Jet from a pressurized source | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/1/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 6/1/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 6/1/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
267 | 268 | 4/7/2000 | Not Challenging | No |  | Turbine Building | [7 empty] | 4/7/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/7/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/7/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Single Portable fire extinguisher | [7 empty] | 4/7/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
268 | 269 | 12/12/2000 | Potentially Challenging | No | Fuel handling area | Other (Specify in comments) |  | Other | [5 empty] | 12/12/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/12/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/12/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 12/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
269 | 270 | 11/18/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 11/18/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/18/2005 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 11/18/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
270 | 271 | 10/5/2007 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/5/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/5/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/5/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
271 | 272 | 4/17/2004 | Not Challenging | No |  |  |  | Other | [5 empty] | 4/17/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Contained within reservoir | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes | [8 empty] | 4/17/2004 | Not Challenging | Final | Challenging | [5 empty] | 4/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/17/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
272 | 273 | 5/10/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 5/10/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/10/2002 | Not Challenging |  |  | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 5/10/2002 | Not Challenging | Operate | Operate | 97 | 97 | None |  | Not Challenging
273 | 274 | 5/7/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/7/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No | [8 empty] | 5/7/2003 | Not Challenging | Final | Challenging | [5 empty] | 5/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Water,Other: Water | [6 empty] | 5/7/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
274 | 275 | 10/14/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/14/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/14/2003 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/14/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Unknown | Portable: Water | [6 empty] | 10/14/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
275 | 276 | 11/2/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/2/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify] | [6 empty] | 11/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
276 | 277 | 11/2/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/2/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify] | [6 empty] | 11/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
277 | 278 | 1/5/2004 | Not Challenging | No | Battery Room |  | DC Power System | Electrical panel | Battery charger | 125VDC | DC |  |  | 1/5/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/5/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
278 | 279
279 | 280 | 11/19/2005 | Not Challenging | No | Containment/Drywell |  |  | Other | [5 empty] | 11/19/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/19/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/19/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
280 | 281
281 | 282 | 4/23/2001 | Not Challenging | Yes | N/A |  |  | Other | [5 empty] | 4/23/2001 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 4/23/2001 | Not Challenging | Final | Challenging | [5 empty] | 4/23/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Other: Water | [6 empty] | 4/23/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
282 | 283 | 11/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
283 | 284 | 11/29/2005 | Not Challenging | No | Containment/Drywell |  |  | Other | [5 empty] | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/29/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Water | [6 empty] | 11/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
284 | 285 | 12/9/2005 | Not Challenging | No |  | Turbine Building |  | Crane | [5 empty] | 11/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/9/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered) | [7 empty] | 12/9/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
285 | 286 | 4/20/2006 | Not Challenging | No | [9 empty] | 4/20/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/20/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 4/20/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/20/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
286 | 287 | 8/10/2006 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 8/10/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/10/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 8/10/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
287 | 288 | 10/10/2006 | Potentially Challenging | No |  |  |  | Pumps | Other instrument/control cabin | 110V | AC |  |  | 10/10/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/10/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/10/2006 | Potentially Challenging |  |  | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 10/10/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
288 | 289 | 5/28/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/28/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 5/28/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
289 | 290 | 8/22/2007 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 8/22/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/22/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | Portable: Water | [6 empty] | 8/22/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
290 | 291
291 | 292 | 10/8/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/8/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/8/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 10/8/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
292 | 293 | 10/14/2007 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/14/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/14/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/14/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
293 | 294 | 10/13/2007 | Not Challenging | No | N/A | Containment (PWR) |  | Other | [5 empty] | 10/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/13/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water | [6 empty] | 10/13/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
294 | 295 | 10/22/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/22/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/22/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/22/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
295 | 296 | 10/30/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/30/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/30/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
296 | 297 | 11/30/2007 | Not Challenging | No | [9 empty] | 11/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/30/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 11/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 11/30/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
297 | 298 | 12/16/2007 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 12/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/16/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 12/16/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 12/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
298 | 299 | 3/4/2008 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 3/4/2008 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/4/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/4/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable: Water | [6 empty] | 3/4/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
299 | 300 |  | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 3/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/16/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 3/16/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
300 | 301
301 | 302 | 12/21/1999 | Not Challenging | No |  |  |  | Crane | [5 empty] | 12/21/1999 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/21/1999 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/21/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 12/21/1999 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
302 | 303 | 3/1/2000 | Potentially Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 480V | AC |  |  | 3/1/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 3/1/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/1/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 3/1/2000 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Challenging
303 | 304
304 | 305 | 6/21/2001 | Not Challenging | No | [9 empty] | 6/21/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/21/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments) | [7 empty] | 6/21/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
305 | 306 | 1/24/2002 | Not Challenging | No |  |  |  | Cable/Wiring | [5 empty] | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/24/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/24/2002 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/24/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
306 | 307 | 10/17/2002 | Not Challenging | No |  |  | Hydrogen Supply System | Other | [5 empty] | 10/17/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Other (Specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/17/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 10/17/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/17/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
307 | 308 | 10/14/2005 | Potentially Challenging | No |  | Turbine Building | Condensate System | [6 empty] | 10/14/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/14/2005 | Potentially Challenging | Final with disagreement | Potentially Challenging | [5 empty] | 10/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/14/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
308 | 309 | 10/23/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other | [5 empty] | 10/23/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/23/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/23/2005 | Not Challenging | 07:30:00 | 07:30:00 | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 10/23/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
309 | 310 | 11/18/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/18/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/18/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 11/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
310 | 311 | 12/1/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 12/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/1/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 12/1/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
311 | 312 | 10/29/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/29/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 10/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
312 | 313 | 11/9/2008 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 11/9/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/9/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/9/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
313 | 314 | 2/10/2000 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 2/10/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/10/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/10/2000 | Not Challenging |  | 07:58:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/10/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
314 | 315
315 | 316 | 8/17/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 8/17/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 8/17/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/17/2000 | Not Challenging | 16:47:00 | 16:47:00 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 8/17/2000 | Not Challenging | Operate | Operate | 55 | 55 |  |  | Not Challenging
316 | 317 | 9/27/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 9/27/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/27/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/27/2003 | Not Challenging | 14:18:00 | 14:18:00 | Known | 3 | 3 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: None | [6 empty] | 9/27/2003 | Not Challenging |  |  | 0 | 0 |  |  | Not Challenging
317 | 318 | 10/5/2000 | Potentially Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/5/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Unknown | [7 empty] | 10/5/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
318 | 319 | 10/5/2000 | Potentially Challenging | No |  |  |  | Other | [5 empty] | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/5/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | [7 empty] | 10/5/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
319 | 320 | 10/24/2000 | Potentially Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 10/24/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/24/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/24/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/24/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
320 | 321 | 10/31/2000 | Not Challenging | No |  | Radwaste Building |  | Batteries |  | Other (specify) | AC |  |  | 10/31/2000 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | In_Situ | Other electrical or electronic equipment |  | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/31/2000 | Not Challenging | Final | Challenging | [5 empty] | 10/31/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/31/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
321 | 322 | 3/8/2001 | Not Challenging | No | [9 empty] | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/8/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 3/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
322 | 323
323 | 324 | 1/12/2005 | Not Challenging | No |  | Turbine Building | Main Turbine System | [6 empty] | 1/12/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/12/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/12/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
324 | 325 | 3/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 3/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
325 | 326 | 3/25/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 3/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/25/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/25/2005 | Not Challenging | 03:55:00 | 03:55:00 | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/25/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
326 | 327 | 1/1/2006 | Not Challenging | No |  |  | High Pressure Safety Injection System (PWR) | Pumps | [5 empty] | 1/1/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/1/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 1/1/2006 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 1/1/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
327 | 328 | 9/24/2006 | Not Challenging | No | [9 empty] | 9/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/24/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 9/24/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
328 | 329 | 9/25/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 9/25/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/25/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/25/2006 | Not Challenging |  | 16:29:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Air supply cut off (smothered, covered) | [7 empty] | 9/25/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
329 | 330 | 9/27/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 9/27/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/27/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 9/27/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 9/27/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
330 | 331 | [57 empty] | 4/15/2007 | Not Challenging | Operate | Operate | 100 | 100
331 | 332 | 4/15/2007 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 4/15/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/15/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/15/2007 |  |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
332 | 333 | 5/11/2007 | Potentially Challenging | No |  | Diesel Generator Building | Diesel Fuel Oil System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 5/11/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/11/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/11/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 5/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
333 | 334
334 | 335 | 8/3/2007 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 8/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/3/2007 | Potentially Challenging | Final | Challenging | [5 empty] | 8/3/2007 | Potentially Challenging | 11:04:00 |  | Known | 6 | 6 | Ultraviolet flame detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 8/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
335 | 336
336 | 337 | 8/18/2005 | Not Challenging | No |  | Diesel Generator Building |  | Other | [5 empty] | 8/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/18/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 8/18/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 8/18/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
337 | 338 | 7/25/2007 | Not Challenging | No | Fuel handling area | Other (Specify in comments) | [7 empty] | 7/25/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/25/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments) | [7 empty] | 7/25/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
338 | 339
339 | 340 | 8/7/2009 | Not Challenging | No |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 8/7/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/7/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/7/2009 | Not Challenging |  | 22:40:00 | Known | 22 | 22 | Installed Fire detector ‐ Type not specified | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/7/2009 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
340 | 341 | 2/18/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Electrical panel |  | 480V | AC |  |  | 2/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/18/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/18/2008 | Not Challenging | 21:24:00 | 21:25:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/18/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
341 | 342 | 11/4/2006 | Not Challenging | No | [9 empty] | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 11/4/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
342 | 343 | 11/4/2006 | Not Challenging | No | Containment/Drywell |  |  | Other | [5 empty] | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 11/4/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
343 | 344 | 10/26/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/26/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/26/2006 | Not Challenging | 13:27:00 | 13:27:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 10/26/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
344 | 345 | 4/25/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 4/25/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/25/2005 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/25/2005 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
345 | 346 | 3/1/2002 | Potentially Challenging | No |  | Turbine Building |  | Electric Motor | Other (specify in comments) | 480V | AC |  |  | 3/1/2002 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/1/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/1/2002 | Potentially Challenging |  | 20:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguishe | [7 empty] | 3/1/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
346 | 347
347 | 348
348 | 349 | 4/5/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | Other (specify) | AC |  |  | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/5/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/5/2007 | Not Challenging |  | 05:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
349 | 350 | 7/11/2002 | Potentially Challenging | No |  | Turbine Building |  | Other |  | Other (specify) | stea |  |  | 7/11/2002 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/11/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/11/2002 | Potentially Challenging |  | 08:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/11/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
350 | 351 | 9/26/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 9/26/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/26/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 9/26/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 9/26/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
351 | 352 | 2/28/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 2/28/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/28/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 2/28/2003 | Not Challenging |  | 09:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 2/28/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
352 | 353 | 1/21/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 1/21/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/21/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 1/21/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
353 | 354 | 10/1/2005 | Not Challenging | No |  |  |  | Electric Motor | [5 empty] | 10/1/2005 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/1/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/1/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/1/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
354 | 355 | 3/7/2006 | Not Challenging | No |  |  | Closed/Component Cooling Water | Electrical panel | [5 empty] | 3/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/7/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 3/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/7/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
355 | 356 | 4/19/2006 | Potentially Challenging | No |  | Turbine Building | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 4/19/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/19/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/19/2006 | Potentially Challenging |  | 19:15:00 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | [7 empty] | 4/19/2006 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
356 | 357 | 1/10/2007 | Not Challenging | No |  | Other (Specify in comments) |  |  | Other |  |  |  |  | 1/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 1/10/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
357 | 358 | 5/2/2007 | Not Challenging | No |  |  | General Ventillation Systems | Pumps |  | 480V | AC |  |  | 5/2/2007 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/2/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 5/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
358 | 359 | 3/6/2001 | Not Challenging | No |  |  |  | Electrical panel | Inverter |  |  |  |  | 3/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/6/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/6/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
359 | 360 | 7/25/2001 | Not Challenging | No | [9 empty] | 7/25/2001 | Not Challenging | Mechanical equipment malfunction/failure |  |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/25/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 7/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
360 | 361 | 2/4/2002 | Not Challenging | No | [9 empty] | 2/4/2002 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/4/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 2/4/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/4/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
361 | 362 | 4/16/2002 | Not Challenging | Yes |  | Other (Specify in comments) |  | Air Compressors | [5 empty] | 4/16/2002 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 4/16/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/16/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown | [7 empty] | 4/16/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
362 | 363 | 5/27/2003 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor | Elevator motor |  |  |  |  | 5/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/27/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 5/27/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/27/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
363 | 364 | 10/3/2003 | Not Challenging | No |  |  |  | Cable/Wiring | [5 empty] | 10/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed | [7 empty] | 10/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
364 | 365 | 8/7/2004 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 8/7/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/7/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 8/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
365 | 366 | 1/25/2006 | Not Challenging | No | [9 empty] | 1/25/2006 | Not Challenging | Personnel error: Misuse of heating devices | Liquid | Lube Oil or Grease |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/25/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 1/25/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
366 | 367 | 10/12/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/12/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/12/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
367 | 368 | 10/24/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/24/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/24/2006 | Not Challenging | 05:19:00 | 05:19:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown | [7 empty] | 10/24/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
368 | 369
369 | 370
370 | 371
371 | 372 | 9/8/2009 | Not Challenging | No | [9 empty] | 9/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/8/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 9/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Unknown | Power Supply Removed | [7 empty] | 9/8/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
372 | 373 | 10/5/2009 | Not Challenging | No | [9 empty] | 10/5/2009 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/5/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/5/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
373 | 374 | 10/13/2009 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 10/13/2009 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/13/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 10/13/2009 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
374 | 375 | 10/16/2009 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Non Essential Service Water System | Pumps | Electric motor driven pumps | 480V | AC |  |  | 10/15/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/16/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/16/2009 | Potentially Challenging | 20:52:00 | 20:52:00 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/16/2009 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
375 | 376 | 6/5/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/5/2004 | Not Challenging |  | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/5/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 6/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
376 | 377 | 8/27/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 8/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/27/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/27/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
377 | 378 | 6/24/2002 | Not Challenging | No |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps |  |  |  |  | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/24/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 6/24/2002 | Not Challenging |  | 12:00:00 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/24/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
378 | 379 | 10/2/2009 | Not Challenging | No | Containment/Drywell | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps |  |  |  |  | 10/2/2009 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/2/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
379 | 380 | 10/29/2004 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu | 600V | AC |  |  | 10/29/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/29/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 10/29/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/29/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
380 | 381 | 3/6/2005 | Potentially Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 3/6/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/6/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/6/2005 | Potentially Challenging |  |  | Estimated | 13 | 13 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/6/2005 | Potentially Challenging | Operate | Operate | 100 | 0 | None |  | Challenging
381 | 382
382 | 383
383 | 384 | 3/23/2007 | Not Challenging | No |  | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 3/23/2007 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/23/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2007 | Not Challenging | 00:20:00 | 00:20:00 | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 3/23/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
384 | 385 | 4/14/2006 | Not Challenging | Yes |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers |  | 13 KV or greater | AC |  |  | 4/14/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | Yes | [8 empty] | 4/14/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/14/2006 | Not Challenging |  | 02:00:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/14/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
385 | 386 | 6/3/2008 | Not Challenging | No |  | Turbine Building | General Ventillation Systems | Other | [5 empty] | 6/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 6/3/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 6/3/2008 | Not Challenging |  | 11:01:00 | Known | 685 | 685 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon | [6 empty] | 6/3/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
386 | 387 | 7/24/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Diesel driven pumps |  |  |  |  | 7/24/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/24/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/24/2008 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 7/24/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
387 | 388 | 7/25/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers |  | 13 KV or greater | AC |  |  | 7/25/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 7/25/2005 | Not Challenging | Final | Challenging | [5 empty] | 7/25/2005 | Not Challenging |  | 14:22:00 | Known | 1025 | 1025 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart) | Other: AFFF foam | [6 empty] | 7/25/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
388 | 389 | 10/17/2004 | Not Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 110V | AC |  |  | 10/17/2004 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/17/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: CO2 | [6 empty] | 10/17/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
389 | 390 | 10/29/2007 | Not Challenging | No |  | Radwaste Building | Reactor Recirculation System (BWR) | Cable/Wiring |  | Other (specify) | DC |  |  | 10/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/29/2007 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/29/2007 | Not Challenging |  | 07:40:00 | Known | 462 | 462 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed by maintenance staff (craft activity required) | Portable: CO2 | [6 empty] | 10/29/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
390 | 391
391 | 392 | 10/30/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/30/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/30/2002 | Not Challenging | Final | Challenging | [5 empty] | 10/30/2002 | Not Challenging | 14:45:00 | 14:53:00 | Known | 11 | 11 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel,Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/30/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
392 | 393 | 10/30/2004 | Not Challenging | No |  | Turbine Building |  | Crane | [5 empty] | 10/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/30/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/30/2004 | Not Challenging |  | 05:00:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: Dry Chemical | [6 empty] | 10/30/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
393 | 394 | 2/11/2000 | Not Challenging | No | Containment/Drywell | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 2/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/11/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/11/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
394 | 395
395 | 396
396 | 397 | 5/2/2000 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 5/2/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/2/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 5/2/2000 | Not Challenging |  | 07:30:00 | Estimated | 13 | 13 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/2/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
397 | 398 | 7/7/2000 | Not Challenging | No |  | Turbine Building | [7 empty] | 7/7/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/7/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 7/7/2000 | Not Challenging |  |  | Known | 0 | 0 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 7/7/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
398 | 399 | 12/24/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/24/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/24/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/24/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/24/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
399 | 400 | 3/28/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 3/28/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | [10 empty] | 3/28/2001 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 3/28/2001 | Not Challenging | Unknown |  |  |  | None |  | Not Challenging
400 | 401 | 6/13/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Elevator motor |  |  |  |  | 6/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/13/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/13/2001 | Not Challenging |  | 12:32:00 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/13/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
401 | 402
402 | 403
403 | 404 | 6/12/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) | 480V | AC |  |  | 6/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/12/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/12/2001 | Not Challenging |  | 05:45:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 6/12/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
404 | 405 | 8/13/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 8/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | [10 empty] | 8/13/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/13/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 8/13/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
405 | 406 | 6/12/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 6/12/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/12/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/12/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 6/12/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
406 | 407 | 12/1/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/1/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/1/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 12/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 12/1/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
407 | 408 | 6/1/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 6/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/1/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/1/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 6/1/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
408 | 409 | 9/21/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 9/21/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) | Other (Specify) | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/21/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/21/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 9/21/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
409 | 410 | 7/25/2005 | Not Challenging | Yes |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC |  |  | 7/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/25/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/25/2005 | Not Challenging |  |  | Known | 533 | 533 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/25/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
410 | 411 | 3/8/2001 | Potentially Challenging | No | Cable vault/tunnel area | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 3/8/2001 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 3/8/2001 | Potentially Challenging | Final | Not Challenging | [5 empty] | 3/8/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/8/2001 | Potentially Challenging | Operate | Operate |  |  | None |  | Challenging
411 | 412 | 7/15/2009 | Not Challenging | No |  | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  |  | 7/15/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/15/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 7/15/2009 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/15/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
412 | 413
413 | 414
414 | 415
415 | 416 | 10/11/2000 | Not Challenging | No |  | Turbine Building | Other | [6 empty] | 10/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/11/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 10/11/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
416 | 417
417 | 418 | 10/8/2000 | Not Challenging | No | [9 empty] | 10/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/8/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
418 | 419 | 4/5/2005 | Not Challenging | No | [9 empty] | 4/5/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/5/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/5/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
419 | 420 | 6/24/2001 | Undetermined (NC‐PC) | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/24/2001 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/24/2001 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 6/24/2001 | Undetermined (NC‐PC) |  | 08:05:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Unknown | Portable: Water | [6 empty] | 6/24/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
420 | 421 | 7/1/2002 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 7/1/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/1/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 7/1/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 7/1/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
421 | 422 | 3/7/2003 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other |  | 480V | AC |  |  | 3/7/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/7/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 3/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
422 | 423 | 6/23/2003 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 6/23/2003 | Undetermined (PC‐CH) | Unknown | In_Situ | Structural component |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 6/23/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 6/23/2003 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 6/23/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
423 | 424 | 3/10/2005 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 3/10/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 3/10/2005 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 3/10/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel | [7 empty] | 3/10/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
424 | 425
425 | 426 | 9/17/2007 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 9/17/2007 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/17/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical | [6 empty] | 9/17/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
426 | 427 | 2/3/2003 | Not Challenging | No | [9 empty] | 2/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/3/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/3/2003 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
427 | 428 | 9/14/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 9/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/14/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | [7 empty] | 9/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
428 | 429 | 3/12/2007 | Not Challenging | No |  |  |  | Other | [5 empty] | 3/12/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/12/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/12/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
429 | 430 | 10/10/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 10/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
430 | 431 | 4/3/2000 | Not Challenging | No | [9 empty] | 4/3/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/3/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/3/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
431 | 432
432 | 433
433 | 434
434 | 435
435 | 436 | 11/21/2000 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 11/21/2000 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | [7 empty] | 11/21/2000 | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
436 | 437 | 2/3/2001 | Challenging | No | Switchgear Room | Auxiliary Building (PWR) | Medium Voltage Power System, Class 1E | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 2/3/2001 | Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | High – protective clothing needed for room entry | Confined to room of origin | Yes | [8 empty] | 2/3/2001 | Challenging | Preliminary | Challenging | [5 empty] | 2/3/2001 | Challenging | 15:14:00 | 15:14:00 | Known | 177 | 177 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify] | [6 empty] | 2/3/2001 | Challenging | Operate | Hot Standby | 39 | 0 | Turbine Trip | Unusual Event | Challenging
437 | 438 | 6/24/2001 | Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 6/24/2001 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | Yes | [8 empty] | 6/24/2001 | Challenging | Preliminary | Challenging | [5 empty] | 6/24/2001 | Challenging |  | 11:02:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 6/24/2001 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
438 | 439 | 10/2/2002 | Not Challenging | Yes |  | Turbine Building |  | Batteries | [5 empty] | 10/2/2002 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a component | Explosion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/2/2002 | Not Challenging | Preliminary | Challenging | [5 empty] | 10/2/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/2/2002 | Not Challenging | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
439 | 440 | 1/2/2003 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/2/2003 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/2/2003 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 1/2/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 1/2/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
440 | 441 | 11/23/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 11/23/2003 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/23/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 11/23/2003 | Not Challenging |  | 15:16:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/23/2003 | Not Challenging | Operate | Operate |  |  | Reduced Power |  | Not Challenging
441 | 442 | 2/4/2004 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/4/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/4/2004 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 2/4/2004 | Potentially Challenging |  | 07:35:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/4/2004 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
442 | 443 | 3/3/2004 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 3/3/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/3/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 3/3/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/3/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
443 | 444 | 6/28/2004 | Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/28/2004 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes | [8 empty] | 6/28/2004 | Challenging | Preliminary | Challenging | [5 empty] | 6/28/2004 | Challenging |  |  | Unknown |  |  |  | Unknown | Multiple portable fire extinguishers | Portable: Halon | [6 empty] | 6/28/2004 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
444 | 445 | 8/30/2004 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 8/30/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/30/2004 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 8/30/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 8/30/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
445 | 446 | 10/5/2004 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/5/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/5/2004 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/5/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/5/2004 | Potentially Challenging | Refueling | Refueling |  |  | None |  | Challenging
446 | 447 | 10/8/2004 | Not Challenging | No |  |  |  | Other |  | 110V | AC |  |  | 10/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/8/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
447 | 448 | 11/17/2004 | Not Challenging | No |  |  |  | Other | [5 empty] | 11/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/17/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 11/17/2004 | Not Challenging |  | 11:58:00 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments) | [7 empty] | 11/17/2004 | Not Challenging | Refueling | Refueling |  |  |  |  | Not Challenging
448 | 449 | 12/8/2004 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 12/8/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/8/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 12/8/2004 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
449 | 450 | 12/13/2004 | Not Challenging | No |  |  |  | Other | [5 empty] | 12/13/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/13/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 12/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/13/2004 | Not Challenging | Refueling | Refueling |  |  |  |  | Not Challenging
450 | 451 | 12/13/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/13/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/13/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/13/2004 | Not Challenging |  | 19:45:00 | Unknown | 0 | 0 | Fire Watch | Unknown | Unknown | [7 empty] | 12/13/2004 | Not Challenging | Refueling | Refueling |  |  | None |  | Not Challenging
451 | 452 | 12/18/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 12/18/2004 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/18/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 12/18/2004 | Not Challenging |  | 11:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/18/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
452 | 453 | 6/3/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention),Unknown | [7 empty] | 6/3/2005 | Not Challenging | Operate | Operate | 100 | 10 |  |  | Not Challenging
453 | 454 | 6/4/2005 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 6/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/4/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/4/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
454 | 455 | 6/6/2005 | Not Challenging | No |  |  |  | Other | [5 empty] | 6/6/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/6/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/6/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 6/6/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
455 | 456 | 7/7/2005 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 7/7/2005 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/7/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/7/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
456 | 457 | 2/17/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/17/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/17/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 2/17/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown | [7 empty] | 2/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
457 | 458 | 5/4/2006 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 5/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 5/4/2006 | Not Challenging | 16:00:00 | 16:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water | [6 empty] | 5/4/2006 | Not Challenging | Unknown | Unknown | 0 |  |  |  | Not Challenging
458 | 459 | 5/10/2006 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/10/2006 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/10/2006 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 5/10/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/10/2006 | Potentially Challenging | Refueling | Refueling |  |  | None |  | Challenging
459 | 460 | 9/7/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Crane motor |  |  |  |  | 9/7/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/7/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 9/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/7/2006 | 9/7/2006 | Operate | Operate | 100 | 100 |  |  | Not Challenging
460 | 461 | 10/12/2006 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/12/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 10/12/2006 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
461 | 462 | 10/18/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/18/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/18/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Other (specify in comments) | [7 empty] | 10/18/2006 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
462 | 463 | 11/1/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 11/1/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/1/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/1/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 11/1/2006 | Not Challenging | Refueling | Refueling |  |  | None |  | Not Challenging
463 | 464 | 12/8/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 12/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/8/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 12/8/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
464 | 465 | 1/31/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/31/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/31/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments) | [7 empty] | 1/31/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
465 | 466 | 2/2/2007 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 2/2/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/2/2007 | Not Challenging | Preliminary | Challenging | [5 empty] | 2/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Hose stream or hose reel | Other: Water | [6 empty] | 2/2/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
466 | 467 | 2/13/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/13/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 2/13/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
467 | 468 | 2/20/2007 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 2/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/20/2007 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 2/20/2007 | Undetermined (NC‐PC) |  | 15:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/20/2007 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
468 | 469 | 3/19/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | Other (specify) | AC |  |  | 3/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/19/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/19/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed | [7 empty] | 3/19/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
469 | 470 | 6/29/2007 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 6/29/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/29/2007 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 6/29/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
470 | 471 | 7/10/2007 | Not Challenging | No |  |  |  | Electric Motor | Elevator motor |  |  |  |  | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/10/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
471 | 472 | 7/17/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/17/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/17/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed | [7 empty] | 7/17/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
472 | 473 | 8/4/2007 | Potentially Challenging | No | Battery Room |  | Low Voltage Power System (600V and less) | Other |  | 250VDC | DC |  |  | 8/4/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/4/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 8/4/2007 | Potentially Challenging | 10:03:00 | 10:04:00 | Known | 147 | 147 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/4/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
473 | 474 | 8/21/2007 | Potentially Challenging | No | Switchgear Room |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 8/21/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | [9 empty] | 8/21/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 8/21/2007 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/21/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
474 | 475 | 9/27/2007 | Potentially Challenging | No |  |  |  | Air Compressors | [5 empty] | 9/27/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/27/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 9/27/2007 | Potentially Challenging |  |  | Estimated | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments) | [7 empty] | 9/27/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
475 | 476 | 12/6/2007 | Not Challenging | No |  |  |  | Other | [5 empty] | 12/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/6/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/6/2007 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 12/6/2007 | Not Challenging | Refueling | Refueling |  |  |  |  | Not Challenging
476 | 477 | 2/23/2008 | Not Challenging | No |  |  |  | Electrical panel | Inverter |  |  |  |  | 2/23/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/23/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/23/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
477 | 478 | 3/30/2008 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 3/30/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 3/30/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/30/2008 | Not Challenging |  | 18:31:00 | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/30/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
478 | 479 | 3/17/2000 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 3/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/17/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/17/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/17/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
479 | 480 | 4/7/2000 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/7/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/7/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/7/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/7/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
480 | 481 | 6/29/2000 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 6/29/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/29/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 6/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/29/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
481 | 482 | 2/8/2000 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/8/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/8/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 2/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/8/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
482 | 483 | 11/9/2000 | Not Challenging | No |  | Control building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 11/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/9/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 11/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed | [7 empty] | 11/9/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
483 | 484 | 11/8/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 11/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/8/2001 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 11/8/2001 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
484 | 485 | 9/14/2001 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/14/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed | [7 empty] | 9/14/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
485 | 486 | 8/27/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/27/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/27/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/27/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 8/27/2001 | Not Challenging | Operate |  | 39 |  |  |  | Not Challenging
486 | 487 | 1/13/2001 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 1/13/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 1/13/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 1/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/13/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
487 | 488 | 10/16/2000 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/16/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/16/2000 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/16/2000 | Not Challenging | Refueling | Refueling |  |  | None |  | Not Challenging
488 | 489
489 | 490
490 | 491 | 4/12/2000 | Undetermined (NC‐PC) | No | [9 empty] | 4/12/2000 | Undetermined (NC‐PC) | Unknown | In_Situ | Structural component |  |  | Unknown | Unknown | Unknown | [9 empty] | 4/12/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/12/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 4/12/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
491 | 492 | 10/19/2000 | Undetermined (NC‐PC) | No | [9 empty] | 10/19/2000 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 10/19/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 10/19/2000 | Undetermined (NC‐PC) | [15 empty] | 10/19/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
492 | 493
493 | 494 | 3/8/2000 | Undetermined (NC‐PC) | No |  |  |  | Air Compressors | [5 empty] | 3/8/2000 | Undetermined(NC‐PC) | Unknown | In_Situ | Structural component |  |  | Unknown | Unknown | Unknown | No | [8 empty] | 3/8/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 3/8/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
494 | 495 | 3/20/2003 | Undetermined (NC‐PC) | No | Main Control Room | Control building | [7 empty] | 3/20/2003 | Undetermined(NC‐PC) | Unknown | In_Situ | Other electrical or electronic equipment |  |  | Unknown | Unknown | Unknown | No | [8 empty] | 3/20/2003 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/20/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 3/20/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
495 | 496 | 5/19/2002 | Undetermined (NC‐PC) | No |  |  |  | Boilers | [5 empty] | 5/19/2002 | Undetermined(NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 5/19/2002 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 5/19/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Unknown | [7 empty] | 5/19/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
496 | 497 | 8/14/2003 | Not Challenging | No | [9 empty] | 8/14/2003 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 8/14/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 8/14/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/14/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
497 | 498 | 12/19/2000 | Undetermined (PC‐CH) | No |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 12/19/2000 | Undetermined(PC‐CH) | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 12/19/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 12/19/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 12/19/2000 | Undetermined (PC‐CH) | Unknown | Unknown |  |  |  |  | Challenging
498 | 499 | 12/17/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/17/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 12/17/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/17/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
499 | 500 | 3/12/2001 | Undetermined (PC‐CH) | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 3/12/2001 | Undetermined(PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Unknown | [9 empty] | 3/12/2001 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC) | [5 empty] | 3/12/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 3/12/2001 | Undetermined (PC‐CH) | Operate | Hot Standby | 0 | 0 | Scram |  | Challenging
500 | 501 | 1/24/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 1/24/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component |  | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 1/24/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 1/24/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
501 | 502 | 11/18/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 11/18/2003 | NotChallenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 11/18/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 11/18/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 11/18/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
502 | 503 | 5/14/2002 | Not Challenging | No |  | Containment (PWR) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 5/14/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 5/14/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/14/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 5/14/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
503 | 504 | 10/9/2002 | Undetermined (PC‐CH) | No |  | Turbine Building | [7 empty] | 10/9/2002 | Undetermined(PC‐CH) | Unknown | Unknown | Unknown |  | Unknown | Unknown | Unknown | Unknown | [9 empty] | 10/9/2002 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC) | [5 empty] | 10/9/2002 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 10/9/2002 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 |  |  | Challenging
504 | 505 | 9/13/2003 | Not Challenging | No |  | Turbine Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 9/13/2003 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 9/13/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/13/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
505 | 506 | 9/12/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 9/12/2003 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | No | [8 empty] | 9/12/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/12/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/12/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
506 | 507
507 | 508 | 3/14/2005 | Not Challenging | No |  | Containment (PWR) |  | Cable/Wiring | [5 empty] | 3/14/2005 | NotChallenging |  |  |  |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 3/14/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/14/2005 | Not Challenging | 19:17:00 | 19:17:00 | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/14/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
508 | 509 | 1/19/2005 | Potentially Challenging | No |  | Other (Specify in comments) | [7 empty] | 1/19/2005 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 1/19/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 1/19/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/19/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
509 | 510 | 7/16/2005
510 | 511 | 7/16/2005 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 7/16/2005 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 7/16/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed | [7 empty] | 7/16/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
511 | 512 | 7/20/2005 | Not Challenging | No |  | Other (Specify in comments) |  |  |  | 24‐48VDC | DC |  |  | 7/20/2005 | NotChallenging |  | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 7/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Power Supply Removed | [7 empty] | 7/20/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
512 | 513 | 11/18/2005 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 11/18/2005 | Undetermined(NC‐PC) |  | In_Situ | Thermal insulation materials |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 11/18/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/18/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/18/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
513 | 514 | 4/27/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | [5 empty] | 4/27/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | [12 empty] | 4/27/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/27/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
514 | 515 | 10/5/2005 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) |  | Air Compressors | [5 empty] | 10/5/2005 | Undetermined(PC‐CH) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown | [9 empty] | 10/5/2005 | Undetermined (PC‐CH) | Final | Undetermined (NC‐PC) | [5 empty] | 10/5/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 10/5/2005 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 |  |  | Challenging
515 | 516 | 10/25/2005 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Transformers | Dry transformer | 4KV | AC |  |  | 10/25/2005 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 10/25/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/25/2005 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 10/25/2005 | Potentially Challenging | Operate | Operate | 0 | 0 |  |  | Challenging
516 | 517 | 3/23/2006 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) |  | Electrical panel | Inverter |  |  |  |  | 3/23/2006 | Undetermined(PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 3/23/2006 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 3/23/2006 | Undetermined (PC‐CH) | 00:34:00 | 00:39:00 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers,Power Supply Removed,Other (specify in comments) | [7 empty] | 3/23/2006 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
517 | 518 | 3/30/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | MG set |  |  |  |  | 3/30/2006 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 3/30/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 3/30/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 3/30/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
518 | 519 | 5/4/2007 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 5/4/2007 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Unknown | Unknown | Confinedtotheobjectoforigin | No | [8 empty] | 5/4/2007 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 5/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 5/4/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
519 | 520 | 6/6/2006 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electrical panel | Inverter |  |  |  |  | 6/6/2006 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 6/6/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/6/2006 | Potentially Challenging | 01:16:00 | 01:19:00 | Known | 11 | 11 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 6/6/2006 | : Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
520 | 521 | 12/17/2007 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 12/17/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 12/17/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 12/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/17/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
521 | 522 | 9/19/2006 | Not Challenging | No |  | Turbine Building |  | Crane | [5 empty] | 9/19/2006 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 9/19/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/19/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 9/19/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
522 | 523 | 9/27/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 9/27/2006 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 9/27/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/27/2006 | Not Challenging |  |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/27/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
523 | 524 | 10/11/2006 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/11/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 10/11/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 10/11/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
524 | 525
525 | 526 | 1/30/2009 | Undetermined (NC‐PC) | No |  |  |  | Pumps | [5 empty] | 1/30/2009 | Undetermined(NC‐PC) | Unknown | In_Situ | Other (specify) |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 1/30/2009 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/30/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/30/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
526 | 527 | 11/10/2009 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 11/10/2009 | Undetermined(NC‐PC) | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 11/10/2009 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/10/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 11/10/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
527 | 528
528 | 529 | 11/28/2008 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Other instrument/control cabin | 125VDC | DC |  |  | 11/28/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | No | [8 empty] | 11/28/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/28/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/28/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
529 | 530 | 3/5/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/5/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 3/5/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/5/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/5/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
530 | 531 | 8/24/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 8/24/2009 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No | [8 empty] | 8/24/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/24/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
531 | 532
532 | 533 | 1/27/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/27/2000 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/27/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 1/27/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/27/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
533 | 534 | 4/10/2000 | Not Challenging | No |  |  |  | Electrical panel | Motor control center |  |  |  |  | 4/10/2000 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/10/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/10/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/10/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
534 | 535 | 6/16/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/16/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/16/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 6/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/16/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
535 | 536 | 8/24/2000 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Pumps | [5 empty] | 8/24/2000 | Undetermined(NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | [13 empty] | 8/24/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 8/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | [7 empty] | 8/24/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | Reduced Power |  | Not Challenging
536 | 537 | 10/13/2000 | Not Challenging | No |  |  | Feedwater System | Other | [5 empty] | 10/13/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/13/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/13/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
537 | 538 | 10/20/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/20/2000 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/20/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/20/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/20/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
538 | 539 | 10/23/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Diesel driven pumps |  |  |  |  | 10/23/2000 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/23/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/23/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
539 | 540 | 10/23/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Air Compressors | [5 empty] | 10/23/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/23/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/23/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments) | [7 empty] | 10/23/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
540 | 541 | 10/24/2000 | Not Challenging | No |  |  |  | Pumps | Diesel driven pumps |  |  |  |  | 10/24/2000 | Undetermined(NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/24/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 10/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown | [7 empty] | 10/24/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
541 | 542 | 3/4/2000 | Not Challenging | No |  | Turbine Building | Main Generator System | Electric Motor |  | 480V | AC |  |  | 3/4/2000 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Thermal insulation materials |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/4/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/4/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None,Other: None | [6 empty] | 3/4/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
542 | 543 | 8/27/2001 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 8/27/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/27/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/27/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/27/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
543 | 544 | 12/13/2001 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments) |  |  |  |  | 12/13/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/13/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/13/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
544 | 545 | 6/5/2002 | Not Challenging | No |  |  |  | Other | [5 empty] | 6/5/2002 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/5/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 6/5/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 6/5/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
545 | 546 | 10/9/2002 | Not Challenging | No |  |  | DC Power System | Electrical panel | Battery charger |  |  |  |  | 10/9/2002 | NotChallenging |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/9/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/9/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
546 | 547 | 11/5/2002 | Not Challenging | No |  |  | Feedwater System | Pumps | [5 empty] | 11/5/2002 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/5/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 11/5/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/5/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
547 | 548 | 11/13/2002 | Not Challenging | No |  |  | Feedwater System | Pumps | [5 empty] | 11/13/2002 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 11/13/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 11/13/2002 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/13/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
548 | 549 | 7/16/2004 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 7/16/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/16/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/16/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
549 | 550 | 2/2/2005 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) |  | Cable/Wiring | [5 empty] | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 2/2/2005 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 2/2/2005 | Undetermined (NC‐PC) | 05:58:00 | 05:58:00 | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
550 | 551 | 2/2/2005 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown | [9 empty] | 2/2/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 2/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 2/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
551 | 552 | 7/31/2003 | Not Challenging | No |  |  | General Ventillation Systems | Pumps | Electric motor driven pumps |  |  |  |  | 7/31/2003 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/31/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 7/31/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/31/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
552 | 553 | 6/24/2004 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 6/24/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 6/24/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/24/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | [7 empty] | 6/24/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
553 | 554 | 6/2/2005 | Undetermined (NC‐PC) | No | [9 empty] | 6/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown | [9 empty] | 6/2/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 6/2/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
554 | 555 | 7/27/2005 | Not Challenging | No |  | Turbine Building |  | Other |  | Other (specify) | AC |  |  | 7/27/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/27/2005 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 7/27/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
555 | 556 | 10/14/2005 | Not Challenging | No |  | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 10/14/2005 | NotChallenging |  | Unknown |  |  | Overheating – no smoldering or flaming combustion | Nosmokepresent | : Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/14/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/14/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | [7 empty] | 10/14/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
556 | 557 | 11/2/2005 | Not Challenging | No |  |  |  | Other | [5 empty] | 11/2/2005 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/2/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/2005 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/2/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
557 | 558 | 12/13/2005 | Potentially Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 12/13/2005 | PotentiallyChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/13/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 12/13/2005 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | [7 empty] | 12/13/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
558 | 559 | 9/12/2006 | Undetermined (NC‐PC) | No |  |  |  | Electric Motor | [5 empty] | 9/12/2006 | Undetermined(NC‐PC | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown | [9 empty] | 9/12/2006 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 9/12/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 9/12/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
559 | 560 | 5/20/2006 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/20/2006 | Undetermined(NC‐PC) | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplumt | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 5/20/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 5/20/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 5/20/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
560 | 561 | 1/3/2005 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 1/3/2005 | NotChallenging | Unknown | In_Situ | Other (specify) |  | No Fire ‐ False actuation of detection device | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 1/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown | [7 empty] | 1/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
561 | 562 | 10/9/2006 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Other | Other (specify in comments) |  |  |  |  | 10/9/2006 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 10/9/2006 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 10/9/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/9/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
562 | 563 | 10/18/2006 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other | [5 empty] | 10/18/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/18/2006 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
563 | 564 | 3/13/2007 | Not Challenging | No |  | Radwaste Building |  | Electrical panel | Other (specify in comments) |  |  |  |  | 3/13/2007 | NotChallenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/13/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/13/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
564 | 565 | 4/25/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/25/2007 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 4/25/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/25/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/25/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
565 | 566 | 7/2/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/2/2007 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 7/2/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 7/2/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
566 | 567 | 7/31/2007 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/31/2007 | Undetermined(NC‐PC) |  | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/31/2007 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/31/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/31/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
567 | 568 | 1/12/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 1/12/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/12/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 1/12/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
568 | 569 | 5/15/2008 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments) |  |  |  |  | 5/15/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/15/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/15/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/15/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
569 | 570 | 6/3/2008 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other |  | 13 KV or greater | AC |  |  | 6/3/2008 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Structural component |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 6/3/2008 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/3/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed | [7 empty] | 6/3/2008 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
570 | 571 | 9/29/2008 | Not Challenging | No |  | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 9/29/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/29/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
571 | 572 | 12/23/2008 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 12/23/2008 | Undetermined(NC‐PC) | Unknown | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/23/2008 | Undetermined (NC‐PC) | Preliminary | Not Challenging | [5 empty] | 12/23/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 12/23/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
572 | 573 | 1/29/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 1/29/2009 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/29/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 1/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/29/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
573 | 574
574 | 575 | 5/18/2009 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 5/18/2009 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/18/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 5/18/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/18/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
575 | 576 | 8/31/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 8/31/2009 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/31/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 8/31/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
576 | 577 | 9/16/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 9/16/2002 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/16/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/16/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
577 | 578 | 11/8/2003 | Not Challenging | No |  |  | General Ventillation Systems | Other | [5 empty] | 11/8/2003 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/8/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/8/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
578 | 579 | 3/23/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/23/2004 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 3/23/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/23/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
579 | 580 | 1/6/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 1/6/2003 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/6/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/6/2003 | Not Challenging | 06:30:00 | 06:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/6/2003 | : Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
580 | 581 | 4/17/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/17/2002 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 4/17/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/17/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
581 | 582 | 9/3/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring |  | 480V | AC |  |  | 9/3/2004 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 9/3/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 9/3/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
582 | 583
583 | 584 | 10/8/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/8/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Nodamage | [9 empty] | 10/8/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 10/8/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
584 | 585 | 12/10/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 220V | AC |  |  | 12/10/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 12/10/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 12/10/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/10/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
585 | 586 | 5/5/2003 | Not Challenging | No |  | Reactor Building (BWR) |  | Outlets |  | 110V | AC |  |  | 5/5/2003 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 5/5/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 5/5/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/5/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
586 | 587 | 5/13/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 5/13/2003 | NotChallenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 5/13/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 5/13/2003 | Not Challenging | 00:00:00 |  | Known | 30 | 30 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 5/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
587 | 588 | 11/30/2006 | Challenging | No |  | Control building | Low Voltage Power System (600V and less) | Electrical panel | Switchgear | 480V | AC |  |  | 11/30/2006 | Challenging | Electrical failure resulting in overheating materials | Insulation | Thermoset | Single Cable | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 11/30/2006 | Challenging | Final | Challenging | [5 empty] | 11/30/2006 | Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water | [6 empty] | 11/30/2006 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
588 | 589
589 | 590 | 2/20/2005 | Not Challenging | No | Switchgear Room | Other (Specify in comments) |  | Electrical panel | Switchgear | 4KV | AC |  |  | 2/20/2005 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 2/20/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 2/20/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
590 | 591 | 7/19/2006 | Potentially Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 7/19/2006 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/19/2006 | Potentially Challenging | Final | Not Challenging | [5 empty] | 7/19/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) |  | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 7/19/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
591 | 592 | 6/11/2009 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 6/11/2009 | Undetermined(NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/11/2009 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 6/11/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Fuel supply removed | [7 empty] | 6/11/2009 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
592 | 593 | 10/16/2008 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/16/2008 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/16/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 10/16/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/16/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
593 | 594 | 1/28/2000 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 1/28/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/28/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 1/28/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
594 | 595 | 2/13/2000 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 2/13/2000 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/13/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 2/13/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 2/13/2000 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
595 | 596 | 6/13/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/13/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/13/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 6/13/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
596 | 597 | 7/22/2000 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 7/22/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/22/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 7/22/2000 | Not Challenging | 17:30:00 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 7/22/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
597 | 598 | 10/12/2000 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 10/12/2000 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/12/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/12/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown | [7 empty] | 10/12/2000 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
598 | 599 |  | Not Challenging | No |  |  |  | Other | [6 empty] | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [10 empty] | Not Challenging | Final | Potentially Challenging | [6 empty] | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [8 empty] | Not Challenging | Unknown | Unknown | 0 |  |  |  | Not Challenging
599 | 600 | 1/17/2004 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 1/17/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/17/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 1/17/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 1/17/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
600 | 601 | 10/28/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/28/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/28/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/28/2004 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 10/28/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
601 | 602 | 9/29/2006 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/29/2006 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/29/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 9/29/2006 | Potentially Challenging |  | 22:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/29/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
602 | 603 | 11/14/2007 | Potentially Challenging | No |  | Turbine Building | General Ventillation Systems | Electric Motor | Other (specify in comments) |  |  |  |  | 11/14/2007 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/14/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/14/2007 | Potentially Challenging | 16:18:00 | 16:18:00 | Known | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 11/14/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
603 | 604 | 9/8/2000 | Not Challenging | No |  |  |  | Electric Motor | Other (specify in comments) |  |  |  |  | 9/8/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/8/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/8/2000 | Not Challenging |  | 17:40:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/8/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
604 | 605 | 9/14/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 9/14/2001 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/14/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/14/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
605 | 606 | 10/31/2006 | Potentially Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 10/31/2006 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/31/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/31/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2 | [6 empty] | 10/31/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
606 | 607 | 11/13/2008 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 11/13/2008 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/13/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/13/2008 | Undetermined (NC‐PC) | 09:50:00 | 09:52:00 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/13/2008 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
607 | 608
608 | 609 |  | Not Challenging | No |  | Other (Specify in comments) |  | Other | [6 empty] | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [10 empty] | Not Challenging | Final | Not Challenging | [6 empty] | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [8 empty] | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
609 | 609 |  | Not Challenging | No |  | Other (Specify in comments) |  | Other | [6 empty] | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [10 empty] | Not Challenging | Final | Not Challenging | [6 empty] | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [8 empty] | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
610 | 10273 | 10/18/2000 | Not Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 125VDC | DC |  |  | 10/18/2000 | NotChallenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 10/18/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/18/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
611 | 10274 | 10/21/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/21/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Overheating – no smoldering or flaming combustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/21/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/21/2000 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed | [7 empty] | 10/21/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
612 | 10275
613 | 10276 | 12/15/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring |  | 480V | AC |  |  | 12/15/2000 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/15/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/15/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/15/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
614 | 10277 | 12/22/2000 | Not Challenging | No |  | Service Water Pump house | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 12/22/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/22/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/22/2000 | Not Challenging | 17:24:00 | 18:35:00 |  |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/22/2000 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Not Challenging
615 | 10278 | 4/4/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/4/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/4/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/4/2001 | Not Challenging | 08:45:00 | 08:45:00 | Known | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/4/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
616 | 10279 | 4/14/2001 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 4/14/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/14/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/14/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
617 | 10280 | 4/17/2001 | Not Challenging | No | Fuel handling area | Containment (PWR) |  | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 4/17/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/17/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
618 | 10281
619 | 10282 | 8/12/2001 | Not Challenging | No |  | Turbine Building | Main Turbine System | Other | [5 empty] | 8/12/2001 | NotChallenging | Electrical failure resulting in overheating materials | Unknown |  |  | No Fire ‐ False actuation of detection device | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 8/12/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/12/2001 |  | 15:00:00 | 16:30:00 | Known | 150 | 150 | Thermal detector (e.g., temperature or rate of rise) | Unknown | Other (specify in comments) | [7 empty] | 8/12/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
620 | 10283 | 2/10/2004 | Not Challenging | No |  |  |  | Electric Motor | Motor operated valve |  |  |  |  | 2/10/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/10/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 2/10/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/10/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
621 | 10284 | 3/10/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/10/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/10/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/10/2004 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 3/10/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
622 | 10285 | 4/7/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/7/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/7/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 4/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
623 | 10286 | 5/10/2004 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/10/2004 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/10/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/10/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 5/10/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
624 | 10287 | 5/19/2004 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 5/19/2004 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/19/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 5/19/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 5/19/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
625 | 10288 | 5/22/2004 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/22/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 5/22/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 5/22/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water | [6 empty] | 5/22/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
626 | 10289 | 5/28/2004 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/28/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/28/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 5/28/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments),Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 5/28/2004 | Not Challenging | Refueling | Unknown |  |  | None |  | Not Challenging
627 | 10290 | 6/3/2004 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 6/3/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/3/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 6/3/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
628 | 10291 | 9/18/2004 | Undetermined (PC‐CH) | No |  | Control building | Low Voltage Power System (600V and less) | Other | [5 empty] | 9/18/2004 | Undetermined(PC‐CH) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin | [9 empty] | 9/18/2004 | Undetermined (PC‐CH) | Final | Challenging | [5 empty] | 9/18/2004 | Undetermined (PC‐CH) |  | 17:35:00 | Known | 104 | 104 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel,Multiple portable fire extinguishers | ortable: Dry Chemical,Other: None | [6 empty] | 9/18/2004 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
629 | 10292 | 1/13/2005 | Not Challenging | No |  | Turbine Building |  | Other | Other instrument/control cabin |  |  |  |  | 1/13/2005 | NotChallenging | Mechanical equipment malfunction/failure | Insulation | Other electrical or electronic equipment | Other (Specify) | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 1/13/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/13/2005 | Not Challenging | 10:32:00 | 10:32:00 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None | [6 empty] | 1/13/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
630 | 10293 | 8/16/2005 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 8/16/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/16/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 8/16/2005 | Undetermined (PC‐CH) | 22:28:00 | 22:28:00 | Known | 5 | 5 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 8/16/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
631 | 10294 | 10/9/2005 | Not Challenging | No |  | Turbine Building | Main Turbine System | Other | [5 empty] | 10/9/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/9/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/9/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
632 | 10295 | 10/18/2005 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/18/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 10/18/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/18/2005 | Not Challenging | 22:52:00 | 22:52:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Single Portable fire extinguisher | [6 empty] | 10/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
633 | 10296 | 8/21/2008 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 8/21/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | Unknown |  |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/21/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
634 | 10297 | 12/14/2008 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 12/14/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/14/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 12/14/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/14/2008 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
635 | 10298 | 2/12/2009 | Not Challenging | No |  | Service Water Pump house |  | Electric Motor | Other (specify in comments) |  |  |  |  | 2/12/2009 | NotChallenging | Unknown | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 2/12/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 2/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/12/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
636 | 10299 | 2/19/2009 | Not Challenging | No |  | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator |  |  |  |  | 2/19/2009 | NotChallenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | No Fire ‐ False actuation of detection device | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown | [9 empty] | 2/19/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 2/19/2009 | Not Challenging |  | 10:21:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 2/19/2009 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
637 | 10300 | 6/25/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 6/25/2009 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Other (Specify) | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/25/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/25/2009 | Not Challenging | 10:40:00 | 10:40:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 6/25/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
638 | 10301
639 | 10302 | 3/10/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 3/10/2000 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/10/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/10/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
640 | 10303 | 5/18/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 5/18/2001 | NotChallenging | Suspicious | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/18/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/18/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 5/18/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
641 | 10304 | 4/8/2001 | Not Challenging | Yes |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other | [5 empty] | 4/8/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/8/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
642 | 10305 | 10/25/2001 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments) |  |  |  |  | 10/25/2001 | NotChallenging | Electrical arcing or sparks (non-HEAF) |  |  |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/25/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/25/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
643 | 10306
644 | 10307 | 10/3/2003 | Not Challenging | No |  | Turbine Building | Main Turbine System | Lube Oil | [5 empty] | 10/3/2003 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/3/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed | [7 empty] | 10/3/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
645 | 10308 | 9/19/2004 | Not Challenging | Yes |  | Containment (PWR) |  | Crane | [5 empty] | 9/19/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 9/19/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/19/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/19/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
646 | 10309 | 4/18/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/18/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 4/18/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/18/2006 | Not Challenging | 14:25:00 | 14:25:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown | [7 empty] | 4/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
647 | 10310 | 1/29/2007 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin | 110V | AC |  |  | 1/29/2007 | NotChallenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 1/29/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/29/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
648 | 10311 | 1/9/2008 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 1/9/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/9/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 1/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/9/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
649 | 10312 | 2/9/2009 | Not Challenging | No | Fuel handling area | Radwaste Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 2/9/2009 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/9/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 2/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/9/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
650 | 10313 | 4/3/2009 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 4/3/2009 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/3/2009 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 4/3/2009 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
651 | 10314
652 | 10315 | 10/18/2002 | Not Challenging | Yes |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 10/18/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Other (Specify) | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 10/18/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/18/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/18/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
653 | 10316 | 11/22/2002 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 11/22/2002 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/22/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 11/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
654 | 10317 | 9/23/2004 | Not Challenging | No |  | Containment (PWR) | [7 empty] | 9/23/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/23/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 9/23/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
655 | 10318 | 10/16/2004 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/16/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/16/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/16/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 10/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
656 | 10319 | 1/7/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 1/7/2005 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/7/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/7/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
657 | 10320 | 5/25/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/25/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/25/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/25/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | [7 empty] | 5/25/2005 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
658 | 10321 | 6/1/2005 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 6/1/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/1/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/1/2005 | Not Challenging |  |  | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 6/1/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
659 | 10322 | 12/10/2005 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Other | [5 empty] | 12/10/2005 | NotChallenging | Electrical arcing or sparks (non-HEAF) | Unknown |  |  | Arc/electric discharge | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown | [9 empty] | 12/10/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 12/10/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
660 | 10323 | 12/11/2005 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments) |  |  |  |  | 12/11/2005 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/11/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/11/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
661 | 10324 | 12/30/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/30/200 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/30/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/30/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | [7 empty] | 12/30/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
662 | 10325
663 | 10326 | 1/24/2007 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 1/24/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/24/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/24/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
664 | 10327 | 6/21/2007 | Not Challenging | No |  | Turbine Building |  | Other |  | Other (specify) | AC |  |  | 6/21/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/21/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 6/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/21/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
665 | 10328 | 7/17/2007 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 7/17/2007 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Other (specify) | Other (Specify) | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/17/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 7/17/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
666 | 10329 | 9/22/2008 | Not Challenging | Yes |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 9/22/2008 | NotChallenging | Unknown | Unknown |  |  | Other (specify) | Unknown | Unknown | Unknown | [9 empty] | 9/22/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/22/2008 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 9/22/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
667 | 10330 | 9/23/2008 | Not Challenging | No |  | Turbine Building | [7 empty] | 9/23/2008 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/23/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | : 9/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
668 | 10331 | 3/24/2009 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 3/24/2009 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Other (Specify) | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/24/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/24/2009 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 3/24/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
669 | 10332
670 | 10333
671 | 10334 | 3/30/2000 | Undetermined (NC‐PC) | No |  | Containment (PWR) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 3/30/2000 | Undetermined(NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin | [9 empty] | 3/30/2000 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 3/30/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/30/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
672 | 10335
673 | 10336 | 10/2/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 10/2/2000 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/2/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/2/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/2/2000 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
674 | 10337 | 10/11/2000 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Lighting Ballasts | [5 empty] | 10/11/2000 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment | Other (Specify) | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 10/11/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | [7 empty] | 10/11/2000 | : Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
675 | 10338 | 9/13/2001 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 600V | AC |  |  | 9/13/2001 | Undetermined(PC‐CH) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 9/13/2001 | Undetermined (PC‐CH) | Final | Potentially Challenging | [5 empty] | 9/13/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 9/13/2001 | Undetermined (PC‐CH) | Operate | Operate |  |  | None |  | Challenging
676 | 10339 | 8/16/2004 | Not Challenging | No |  | Main Transformer or Switch Yard |  | Transformers |  | Other (specify) | AC |  |  | 8/16/2004 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/16/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/16/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
677 | 10340
678 | 10341 | 5/21/2005 | Not Challenging | No |  |  | Medium Voltage Power System (601V to 35kV) | Cable/Wiring | [5 empty] | 5/21/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 5/21/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 5/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 5/21/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
679 | 10342
680 | 10343 | 8/25/2005 | Not Challenging | No |  | Other (Specify in comments) |  |  |  | 110V | AC |  |  | 8/25/2005 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/25/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 8/25/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/25/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
681 | 10344 | 10/1/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 10/1/2005 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/1/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/1/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
682 | 10345 | 1/25/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 1/25/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/25/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
683 | 10346
684 | 10347
685 | 10348
686 | 10349 | 9/24/2007 | Not Challenging | : No |  | Containment (PWR) |  | Other | [5 empty] | 9/24/2007 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 9/24/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 9/24/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
687 | 10350 | 1/21/2008 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other |  | 110V | : AC |  |  | 1/21/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/21/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
688 | 10351
689 | 10352 | 12/11/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring |  | 480V | : AC |  |  | 12/11/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/11/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 12/11/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/11/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
690 | 10353 | 1/5/2009 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 1/5/2009 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/5/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 1/5/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
691 | 10354 | 7/2/2009 | Not Challenging | : No |  | Diesel Generator Building |  | Other | [5 empty] | 7/2/2009 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 7/2/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 7/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 7/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
692 | 10355 | 4/26/2008 | Potentially Challenging | : No |  | Other (Specify in comments) | Feedwater System | Other | [5 empty] | 4/26/2008 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/26/2008 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/26/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/26/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
693 | 10356 | 10/3/2007 | Potentially Challenging | : No |  | Auxiliary Building (PWR) | General Ventillation Systems | Pumps | Electric motor driven pumps |  |  |  |  | 10/3/2007 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/3/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
694 | 10357 | 7/1/2005 | Potentially Challenging | : No |  | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps |  |  |  |  | 7/1/2005 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/1/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/1/2005 | Potentially Challenging |  | 16:50:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2 | [6 empty] | 7/1/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
695 | 10358 | 7/3/2002 | Potentially Challenging | : No |  |  | Instrument and Uninterruptible Power System | Electrical panel | : Inverter | Other (specify) |  |  |  | 7/3/2002 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/3/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/3/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/3/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
696 | 10359 | 11/16/2000 | Potentially Challenging | : No |  | Other (Specify in comments) |  | Other | [5 empty] | 11/16/2000 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/16/2000 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 11/16/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
697 | 10360 | 10/13/2000 | Undetermined (NC‐PC) | : No |  | Turbine Building |  | Other | [5 empty] | 10/13/2000 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/13/2000 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 10/13/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 10/13/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
698 | 10361 | 5/5/2005 | Potentially Challenging | : No |  | Containment (PWR) |  | Cable/Wiring | [5 empty] | 5/5/2005 | PotentiallyChallenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/5/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 5/5/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/5/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
699 | 10362 | 10/28/2006 | Potentially Challenging | : No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 10/28/2006 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/28/2006 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/28/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed | [7 empty] | 10/28/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
700 | 10363 | 11/5/2009 | Potentially Challenging | : No |  | Containment (PWR) |  | Cable/Wiring |  | Other (specify) | AC |  |  | 11/5/2009 | PotentiallyChallenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/5/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/5/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/5/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
701 | 10364 | 6/30/2005 | Potentially Challenging | : No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps |  |  |  |  | 6/30/2005 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/30/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/30/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2 | [6 empty] | 6/30/2005 | Potentially Challenging | Operate | Operate | 0 | 0 | None |  | Challenging
702 | 10365 | 8/22/2008 | Undetermined (NC‐PC) | : No |  | Other (Specify in comments) | [7 empty] | 8/22/2008 | Undetermined(NC‐PC) | Electrical arcing or sparks (non-HEAF) | Unknown |  |  | Arc/electric discharge | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 8/22/2008 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 8/22/2008 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 8/22/2008 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 |  |  | Not Challenging
703 | 10366
704 | 10367 | 10/22/2000 | Potentially Challenging | : No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 10/22/2000 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/22/2000 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/22/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/22/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
705 | 10368 | 6/28/2004 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 6/28/2004 | Undetermined(NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/28/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 6/28/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 6/28/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
706 | 10369 | 10/4/2002 | Potentially Challenging | No |  |  |  | Electrical panel | Other (specify in comments) |  |  |  |  | 10/4/2002 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/4/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/4/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/4/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
707 | 10370 | 4/11/2008 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/11/2008 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/11/2008 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/11/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/11/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
708 | 10371 | 10/20/2009 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 10/20/2009 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/20/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/20/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/20/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
709 | 10372 | 10/22/2009 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 10/22/2009 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/22/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/22/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
710 | 10373 | 4/14/2005 | Potentially Challenging | No |  | Turbine Building | Non Essential Service Water System | Other | [5 empty] | 4/14/2005 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/14/2005 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/14/2005 | Potentially Challenging |  | 10:58:00 | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/14/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
711 | 10374 | 7/11/2003 | Potentially Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 7/11/2003 | PotentiallyChallenging |  | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/11/2003 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/11/2003 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 7/11/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
712 | 10375
713 | 10376 | 3/23/2004 | Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/23/2004 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 3/23/2004 | Challenging | Preliminary | Challenging | [5 empty] | 3/23/2004 | Challenging |  |  | Estimated | 10 | 10 | Unknown |  | Hose stream or hose reel | [7 empty] | 3/23/2004 | Challenging | Hot Standby | Hot Standby | 0 | 0 |  |  | Challenging
714 | 10377 | 3/10/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/10/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/10/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/10/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 3/10/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
715 | 10378 | 3/18/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Wall Mounted or Sealed |  |  |  |  | 3/18/2000 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/18/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/18/2000 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
716 | 10379 | 3/22/2000 | Not Challenging | No |  | Turbine Building | Condensate System | Other |  | 480V | AC |  |  | 3/22/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/22/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/22/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/22/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
717 | 10380 | 9/23/2000 | Not Challenging | No |  | Control building | DC Power System, class 1E | Other |  | 125VDC | DC |  |  | 9/23/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 9/23/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 9/23/2000 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
718 | 10381 | 10/24/2000 | Not Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel |  | 600V | AC |  |  | 10/24/2000 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 10/24/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/24/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/24/2000 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
719 | 10382 | 3/20/2001 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 220V | AC |  |  | 3/20/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/20/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/20/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
720 | 10383 | 4/3/2001 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 110V | AC |  |  | 4/3/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 4/3/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/3/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
721 | 10384 | 6/26/2001 | Not Challenging | No |  | Control building | General Ventillation Systems | Lube Oil |  | 125VDC | DC |  |  | 6/26/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 6/26/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 6/26/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
722 | 10385 | 2/12/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Circuit breaker or other distribu |  |  |  |  | 2/12/2002 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/12/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 2/12/2002 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/12/2002 | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
723 | 10386 | 3/1/2003 | Undetermined (NC‐PC) | No |  | Radwaste Building |  | Crane | [5 empty] | 3/1/2003 | Undetermined(NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/1/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 3/1/2003 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/1/2003 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 |  |  | Not Challenging
724 | 10387 | 3/4/2003 | Not Challenging | No | Battery Room | Control building | DC Power System, class 1E | Electrical panel |  | 250VDC | DC |  |  | 3/4/2003 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 3/4/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 3/4/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
725 | 10388
726 | 10389 | 9/8/2003 | Potentially Challenging | No | Main Control Room | Diesel Generator Building | Medium Voltage Power System (601V to 35kV) | Electrical panel |  | 4KV | AC |  |  | 9/8/2003 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 9/8/2003 | Potentially Challenging | Final with disagreement | Potentially Challenging | [5 empty] | 9/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/8/2003 | Potentially Challenging | Operate | Operate | 0 | 0 | None |  | Challenging
727 | 10390
728 | 10391
729 | 10392 | 4/5/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 4/5/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/5/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/5/2004 | Not Challenging |  | 13:30:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/5/2004 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
730 | 10393 | 11/7/2004 | Not Challenging | No |  | Radwaste Building |  | Other | Other instrument/control cabin |  |  |  |  | 11/7/2004 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/7/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 11/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/7/2004 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
731 | 10394 | 2/22/2005 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Other (specify in comments) | 110V | AC |  |  | 2/22/2005 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage) | [9 empty] | 2/22/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/22/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/22/2005 | Potentially Challenging | Operate | Operate | 0 | 0 | None |  | Challenging
732 | 10395 | 7/13/2005 | Not Challenging | No | Switchgear Room | Diesel Generator Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 7/13/2005 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 7/13/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/13/2005 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
733 | 10396 | 7/14/2005 | Not Challenging | No |  | Turbine Building | Closed/Component Cooling Water | Pumps | Electric motor driven pumps |  |  |  |  | 7/14/2005 | NotChallenging | Unknown | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/14/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/14/2005 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
734 | 10397 | 10/12/2005 | Potentially Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electric Motor | Fans | 600V | AC |  |  | 10/12/2005 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Flaming combustion – internal to component | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 10/12/2005 | Potentially Challenging | Final | Challenging | [5 empty] | 10/12/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 10/12/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
735 | 10398
736 | 10399 | 1/31/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 1/31/2006 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/31/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 1/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 1/31/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
737 | 10400
738 | 10401 | 5/9/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | Other instrument/control cabin |  |  |  |  | 5/9/2006 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | [10 empty] | 5/9/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 5/9/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 5/9/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
739 | 10402 | 6/27/2006 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 6/27/2006 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Overheating – no smoldering or flaming combustion | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 6/27/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/27/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker),Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 6/27/2006 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
740 | 10403 | 10/31/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 10/31/2006 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/31/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/31/2006 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
741 | 10404 | 12/5/2006 | Not Challenging | No |  | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Generator | Other generator (specify in com |  |  |  |  | 12/5/2006 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/5/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 12/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 12/5/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
742 | 10405 | 1/20/2007 | Not Challenging | No |  | Turbine Building | Main Generator System | Generator | Main turbine generator |  |  |  |  | 1/20/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Unknown | Confinedtotheobjectoforigin | [9 empty] | 1/20/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/20/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/20/2007 | Not Challenging | Operate | Operate | 10 | 10 |  |  | Not Challenging
743 | 10406 | 5/5/2007 | Not Challenging | Yes |  | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) |  | Other | Other (specify) | AC |  |  | 5/5/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 5/5/2007 | Not Challenging | Final | Challenging | [5 empty] | Unknown | Not Challenging |  | Known | Known | 80 | 80 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Plant area did not have installed detection capability,Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/5/2007 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
744 | 10407 | 6/3/2007 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Main control board (i.e., the ma | 110V | AC |  |  | 6/3/2007 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 6/3/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Potentially Challenging | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Potentially Challenging | [7 empty] | 6/3/2007 | Potentially Challenging | Operate | Operate | 0 | 0 |  |  | Challenging
745 | 10408
746 | 10409 | 12/12/2007 | Not Challenging | No |  | Other (Specify in comments) | Offgas System (BWR) | Electrical panel | Circuit breaker or other distribu | 600V | AC |  |  | 12/12/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 12/12/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 12/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 12/12/2007 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
747 | 10410 | 2/13/2008 | Not Challenging | No |  | Control building | DC Power System, class 1E | Batteries | [5 empty] | 2/13/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/13/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/13/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Not Challenging,Self‐extinguished (no plant staff intervention) | [7 empty] | 2/13/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
748 | 10411 | 3/8/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring |  | Other (specify) | AC |  |  | 3/8/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 3/8/2008 | Not Challenging | Final | Challenging | [5 empty] | 3/8/2008 | Not Challenging |  |  | Unknown |  |  | Not Challenging | Plant area did not have installed detection capability | Not Challenging | [7 empty] | 3/8/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
749 | 10412 | 2/17/2009 | Not Challenging | No |  | Reactor Building (BWR) |  |  |  | 250VDC | DC |  |  | 2/17/2009 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 2/17/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | [8 empty] | 2/17/2009 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
750 | 10413 | 5/17/2009 | Not Challenging | No |  | Radwaste Building |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 5/17/2009 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/17/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 5/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/17/2009 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
751 | 10414 | 8/31/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring |  | 110V | AC |  |  | 8/31/2009 | NotChallenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/31/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/31/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
752 | 10415
753 | 10416 | 4/1/2007 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 4/1/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/1/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/1/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/1/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
754 | 10417 | 4/17/2007 | Not Challenging | No |  | Turbine Building | Condensate System | Electrical panel | Wall Mounted or Sealed |  |  |  |  | 4/17/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/17/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed | [7 empty] | 4/17/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
755 | 10418 | 2/15/2008 | Not Challenging | Yes |  | Main Transformer or Switch Yard |  | Other | [5 empty] | 2/15/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 2/15/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/15/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 2/15/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
756 | 10419 | 4/12/2008 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 4/12/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/12/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/12/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
757 | 10420 | 4/17/2008 | Not Challenging | No | Battery Room | Control building |  | Electric Motor | [5 empty] | 4/17/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/17/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/17/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
758 | 10421 | 6/20/2008 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 6/20/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/20/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/20/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/20/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
759 | 10422 | 8/25/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/25/2008 | NotChallenging | Unknown | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/25/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/25/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
760 | 10423 | 9/3/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 9/3/2008 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 9/3/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 9/3/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 9/3/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
761 | 10424 | 10/19/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/19/2009 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Other (Specify) | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/19/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/19/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/19/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
762 | 10425 | 11/6/2009 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 11/6/2009 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/6/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 11/6/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: CO2 | [6 empty] | 11/6/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
763 | 10426 | 4/29/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/29/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/29/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/29/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 4/29/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
764 | 10427 | 5/3/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/3/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/3/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/3/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
765 | 10428 | 6/1/2000 | Not Challenging | No |  |  |  | Other | [5 empty] | 6/1/2000 | NotChallenging | Mechanical equipment malfunction/failure | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/1/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/1/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/1/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
766 | 10429 | 9/21/2002 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 9/21/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/21/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 9/21/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/21/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
767 | 10430 | 12/21/2000 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 12/21/2000 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/21/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/21/2000 | Potentially Challenging |  | 22:22:00 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/21/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
768 | 10431
769 | 10432 | 10/22/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/22/2003 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 10/22/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/22/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/22/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
770 | 10433 | 12/10/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 12/10/2003 | NotChallenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/10/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 12/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/10/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
771 | 10434 | 5/7/2004 | Not Challenging | No |  | Turbine Building |  | Crane | [5 empty] | 5/7/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/7/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 5/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/7/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
772 | 10435 | 7/8/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/8/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/8/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 7/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/8/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
773 | 10436 | 8/11/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/11/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/11/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/11/2004 | Not Challenging |  | 10:20:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/11/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
774 | 10437 | 5/9/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/9/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | No Fire ‐ False actuation of detection device | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/9/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 5/9/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 5/9/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
775 | 10438
776 | 10439
777 | 10440
778 | 10441 | 3/4/2009 | Potentially Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 3/4/2009 | PotentiallyChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/4/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/4/2009 | Potentially Challenging |  | 00:00:00 | Unknown |  |  | Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher | [7 empty] | 3/4/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
779 | 10442 | 3/9/2009 | Potentially Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 3/9/2009 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 3/9/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/9/2009 | Potentially Challenging |  | 07:40:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed | [7 empty] | 3/9/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
780 | 10443 | 7/25/2009 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 7/25/2009 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/25/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/25/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 7/25/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
781 | 10444 | 10/13/2009 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/13/2009 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/13/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power Supply Removed | [7 empty] | 10/13/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
782 | 10445 | 2/7/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/7/2000 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/7/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 2/7/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/7/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
783 | 10446 | 4/11/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 4/11/2000 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/11/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/11/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
784 | 10447 | 3/9/2000 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Generator | Other generator (specify in com |  |  |  |  | 3/9/2000 | Undetermined(NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/9/2000 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 3/9/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/9/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
785 | 10448 | 10/23/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans | 480V | AC |  |  | 10/23/2001 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/23/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/23/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/23/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
786 | 10449 | 5/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/17/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 5/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/17/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
787 | 10450 | 6/19/2001 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 6/19/2001 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Unconfined spill | Flaming combustion – external to component | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/19/2001 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/19/2001 | Potentially Challenging | 20:00:00 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 6/19/2001 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
788 | 10451 | 6/5/2001 | Not Challenging | No |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/5/2001 | NotChallenging | Electrical failure resulting in overheating materials | Unknown |  |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown | [9 empty] | 6/5/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/5/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/5/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
789 | 10452 | 9/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 9/17/2001 | NotChallenging | Electrical failure resulting in overheating materials | Unknown |  |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 9/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/17/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
790 | 10453 | 11/20/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 11/20/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/20/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/20/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
791 | 10454 | 2/17/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 2/17/2003 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/17/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 2/17/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 2/17/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
792 | 10455 | 3/22/2002 | Not Challenging | No |  | Turbine Building |  | Electric Motor | Fans |  |  |  |  | 3/22/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/22/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/22/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
793 | 10456 | 7/19/2002 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/19/2002 | PotentiallyChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/19/2002 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/19/2002 | Potentially Challenging |  | 11:15:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 7/19/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
794 | 10457 | 10/22/2002 | Undetermined (NC‐PC) | No |  | Containment (PWR) |  | Other | [5 empty] | 10/22/2002 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 10/22/2002 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 10/22/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/22/2002 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
795 | 10458 | 1/7/2003 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Cable/Wiring | [5 empty] | 1/7/2003 | PotentiallyChallenging | Mechanical equipment malfunction/failure | Liquid | Other (specify) | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 1/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | [7 empty] | 1/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
796 | 10459 | 2/7/2003 | Potentially Challenging | No |  | Containment (PWR) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 2/7/2003 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | Potentially Challenging | Preliminary | Potentially Challenging | Not Challenging | [5 empty] | 2/7/2003 | Not Challenging |  | 10:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/7/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
797 | 10460 | 4/9/2003 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 4/9/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/9/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/9/2003 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
798 | 10461 | 3/6/2003 | Not Challenging | No |  | Containment (PWR) |  | Electric Motor | Crane motor |  |  |  |  | 3/6/2003 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/6/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/6/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/6/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
799 | 10462 | 2/5/2004 | Undetermined (NC‐PC) | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps |  |  |  |  | 2/5/2004 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/5/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 2/5/2004 | Undetermined (NC‐PC) |  | 22:54:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed,Unknown | [7 empty] | 2/5/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
800 | 10463 | 3/1/2004 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 3/1/2004 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/1/2004 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 3/1/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/1/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
801 | 10464 | 3/30/2005 | Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/30/2005 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Contained within reservoir | Flaming combustion – internal to component | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Unknown | Confinedtotheobjectoforigin | [9 empty] | 3/30/2005 | Challenging | Preliminary | Challenging | [5 empty] | 3/30/2005 | Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression ‐ manually actuated,Single Portable fire extinguisher,Power Supply Removed | Portable: Other [specify],Other: Other [specify] | [6 empty] | 3/30/2005 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
802 | 10465 | 9/30/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 9/30/2004 | NotChallenging | Unknown | Unknown |  |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/30/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/30/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/30/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
803 | 10466 | 8/31/2005 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 8/31/2005 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/31/2005 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 8/31/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed | Portable: CO2 | [6 empty] | 8/31/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
804 | 10467 | 4/7/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 4/7/2005 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/7/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/7/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/7/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
805 | 10468 | 10/27/2005 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 10/27/2005 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/27/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/27/2005 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
806 | 10469 | 3/23/2006 | Not Challenging | No | Cable Spreading Room | Auxiliary Building (PWR) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 3/23/2006 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/23/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2006 | Not Challenging |  | 22:23:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 3/23/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
807 | 10470 | 5/5/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/5/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | re: Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/5/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 5/5/2006 | Not Challenging |  |  | 0 | 0 |  |  | Not Challenging
808 | 10471 | 12/26/2007 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Other (specify in comments) |  |  |  |  | 12/26/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 12/26/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed，Other (specify in comments) | [7 empty] | 12/26/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
809 | 10472 | 9/25/2007 | Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 13 KV or greater | AC |  |  | 9/25/2007 | Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Unknown | Unknown | Confinedtotheobjectoforigin | [9 empty] | 9/25/2007 | Challenging | Preliminary | Challenging | [5 empty] | 9/25/2007 | Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) |  | Power Supply Removed | [7 empty] | 9/25/2007 | Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
810 | 10473 | 1/23/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/23/2007 | NotChallenging | Unknown | In_Situ | Other (specify) |  | Other (specify) | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown | [9 empty] | 1/23/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/23/2007 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 1/23/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
811 | 10474 | 2/23/2007 | Not Challenging | No |  | Main Transformer or Switch Yard |  | Other | [5 empty] | 2/23/2007 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/23/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 2/23/2007 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 2/23/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
812 | 10475 | [47 empty] | Other plant personnel (in vicinity or passerby)
813 | 10476 | 4/10/2007 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Other (specify in comments) |  |  |  |  | 4/10/2007 | PotentiallyChallenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/10/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/10/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/10/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
814 | 10477 | 6/7/2007 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/7/2007 | PotentiallyChallenging | Unknown | In_Situ | Other (specify) |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 6/7/2007 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/7/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments) | [7 empty] | 6/7/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
815 | 10478 | 7/10/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) | 110V | AC |  |  | 7/10/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/10/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/10/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed，Other (specify in comments) | [7 empty] | 7/10/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
816 | 10479 | 7/23/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 7/23/2008 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/23/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/23/2008 | Not Challenging |  | 09:22:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 7/23/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
817 | 10480 | 7/23/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/23/2008 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/23/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 7/23/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
818 | 10481
819 | 10482 | 10/22/2006 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Pumps | Electric motor driven pumps | 480V | AC |  |  | 10/22/2006 | Undetermined(NC‐PC) | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/22/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 10/22/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 10/22/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
820 | 10483 | 4/10/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | Other (specify) | AC |  |  | 4/10/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/10/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
821 | 10484 | 4/16/2007 | Not Challenging | No |  | Turbine Building | Main Generator System | Other | [5 empty] | 4/16/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/16/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/16/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/16/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
822 | 10485 | 4/21/2007 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 4/21/2007 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/21/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/21/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
823 | 10486 | 7/28/2007 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 7/28/2007 | NotChallenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  |  | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/28/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/28/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
824 | 10487 | 9/4/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 9/4/2007 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtopartofroomorareaoforigin | [9 empty] | 9/4/2007 | Not Challenging | Final | Challenging | [5 empty] | 9/4/2007 | Not Challenging |  | 08:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 9/4/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
825 | 10488 | 9/24/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 9/24/2007 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/24/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/24/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
826 | 10489 | 4/6/2008 | Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/6/2008 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/6/2008 | Challenging | Final | Challenging | [5 empty] | 4/6/2008 | Challenging |  | 07:27:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water | [6 empty] | 4/6/2008 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
827 | 10490 | 4/9/2008 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/9/2008 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/9/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/9/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
828 | 10491 | 4/29/2008 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/29/2008 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/29/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/29/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
829 | 10492 | 9/30/2008 | Potentially Challenging | No |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel |  | 480V | AC |  |  | 9/30/2008 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage) | [9 empty] | 9/30/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/30/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/30/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
830 | 10493 | 10/23/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 10/23/2008 | NotChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Arc/electric discharge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 10/23/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
831 | 10494
832 | 10495
833 | 10496 | 5/14/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | [5 empty] | 5/14/2009 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/14/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 5/14/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/14/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
834 | 10497 | 7/31/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/31/2009 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 7/31/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/31/2009 | Not Challenging |  | 06:50:00 | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 7/31/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
835 | 10498 | 9/26/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 9/26/2009 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/26/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 9/26/2009 | Not Challenging |  | 20:42:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/26/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
836 | 10499 | 10/16/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 10/16/2009 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 10/16/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/16/2009 | Not Challenging |  | 17:46:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
837 | 10500
838 | 10501
839 | 10502
840 | 10503
841 | 10504 | 3/15/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/15/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/15/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/15/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
842 | 10505 | 3/16/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/16/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/16/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/16/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 3/16/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
843 | 10506
844 | 10507 | 3/14/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/14/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/14/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/14/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
845 | 10508 | 3/28/2001 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 3/28/2001 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/28/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 3/28/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/28/2001 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 | None |  | Not Challenging
846 | 10509 | 4/1/2001 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/1/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/1/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/1/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 4/1/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
847 | 10510 | 4/10/2001 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 4/10/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/10/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/10/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | : 4/10/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
848 | 10511
849 | 10512 | 6/22/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 110V | AC |  |  | 6/22/2001 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/22/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/22/2001 | Not Challenging |  | 22:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/22/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
850 | 10513 | 8/20/2001 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 8/20/2001 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/20/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/20/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
851 | 10514 | 8/26/2001 | Potentially Challenging | No |  | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator |  |  |  |  | 8/26/2001 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/26/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/26/2001 | Potentially Challenging |  | 23:38:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 8/26/2001 | Potentially Challenging | Operate | Operate | 67 | 67 | None |  | Challenging
852 | 10515 | 9/30/2001 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 9/30/2001 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/30/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 9/30/2001 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | [7 empty] | 9/30/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
853 | 10516 | 11/20/2001 | Potentially Challenging | No |  | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring | [5 empty] | 11/20/2001 | PotentiallyChallenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/20/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/20/2001 | Potentially Challenging |  | 12:43:00 | Estimated | 10 | 10 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/20/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
854 | 10517 | 8/5/2002 | Not Challenging | No |  | Diesel Generator Building | Lube Oil System | Generator | Class 1A emergency generator |  |  |  |  | 8/5/2002 | NotChallenging | Unknown | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/5/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/5/2002 | Not Challenging |  | 11:46:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 8/5/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
855 | 10518 | 8/26/2002 | Not Challenging | Yes |  | Main Transformer or Switch Yard |  | Other | [5 empty] | 8/26/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | [9 empty] | 8/26/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/26/2002 | Not Challenging | 22:15:00 | 22:15:00 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 8/26/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
856 | 10519 | 9/25/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/25/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/25/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/25/2002 | Not Challenging |  | 03:45:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/25/2002 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
857 | 10520 | 11/26/2002 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 11/26/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – external to component | Unknown | Unknown | Confinedtopartofroomorareaoforigin | [9 empty] | 11/26/2002 | Not Challenging | Final | Challenging | [5 empty] | 11/26/2002 | Not Challenging |  | 14:45:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water | [6 empty] | 11/26/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
858 | 10521 | 9/10/2003 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 9/10/2003 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/10/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/10/2003 | Not Challenging |  | 02:15:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | Portable: CO2 | [6 empty] | 9/10/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
859 | 10522 | 11/2/2003 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 11/2/2003 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/2/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/2/2003 | Potentially Challenging |  | 23:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/2/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
860 | 10523 | 11/9/2003 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 11/9/2003 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 11/9/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/9/2003 | Not Challenging |  | 12:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/9/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
861 | 10524 | 1/7/2004 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 1/7/2004 | PotentiallyChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/7/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/7/2004 | Potentially Challenging |  | 18:27:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 1/7/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
862 | 10525 | 5/10/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 5/10/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/10/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/10/2004 | Not Challenging |  | 13:49:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 5/10/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
863 | 10526 | 5/30/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 5/30/2004 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/30/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/30/2004 | Not Challenging |  | 23:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 5/30/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
864 | 10527
865 | 10528 | 9/8/2004 | Not Challenging | No | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 9/8/2004 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/8/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/8/2004 | Not Challenging |  | 12:55:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 9/8/2004 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
866 | 10529 | 1/25/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/25/2006 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/25/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/25/2006 | Not Challenging |  | 17:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 1/25/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
867 | 10530 | 3/15/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/15/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/15/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/15/2006 | Not Challenging |  | 14:30:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 3/15/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
868 | 10531 | 3/31/2006 | Not Challenging | No |  | Turbine Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 3/31/2006 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/31/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 3/31/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/31/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
869 | 10532 | 6/28/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/28/2006 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/28/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/28/2006 | Not Challenging |  | 12:15:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/28/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
870 | 10533 | 2/1/2001 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 2/1/2001 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – internal to component | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 2/1/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 2/1/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
871 | 10534 | 3/21/2001 | Not Challenging | No |  | Turbine Building | [7 empty] | 3/21/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 3/21/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/21/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
872 | 10535 | 3/31/2002 | Not Challenging | No |  | Turbine Building | [7 empty] | 3/31/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/31/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/31/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/31/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
873 | 10536 | 12/12/2002 | Not Challenging | No |  | Drywell (BWR) | [7 empty] | 12/12/2002 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 12/12/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
874 | 10537 | 2/17/2003 | Not Challenging | No |  | Drywell (BWR) | [7 empty] | 2/17/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 2/17/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 2/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 2/17/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
875 | 10538 | 4/1/2003 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 4/1/2003 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/1/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/1/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/1/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
876 | 10539 | 1/19/2004 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 1/19/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/19/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/19/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 1/19/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
877 | 10540 | 2/4/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 2/4/2004 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Extendedbeyondstructureoforigin | [9 empty] | 2/4/2004 | Not Challenging | Final | Challenging | [5 empty] | 2/4/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 2/4/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
878 | 10541 | 3/24/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/24/2001 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/24/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/24/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/24/2001 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
879 | 10542 | 7/9/2003 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 7/9/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/9/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 7/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/9/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
880 | 10543 | 9/3/2003 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/3/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 9/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
881 | 10544 | 1/17/2003 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 1/17/2003 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/17/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water | [6 empty] | 1/17/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
882 | 10545 | 5/9/2002 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 5/9/2002 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin | [9 empty] | 5/9/2002 | Not Challenging | Final | Challenging | [5 empty] | 5/9/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 5/9/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
883 | 10546 | 3/15/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/15/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 3/15/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown | [7 empty] | 3/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
884 | 10547 | 1/22/2004 | Not Challenging | No | [9 empty] | 1/22/2004 | NotChallenging |  | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/22/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/22/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
885 | 10548 | 6/25/2003 | Not Challenging | No |  | Drywell (BWR) |  | Other | [5 empty] | 6/25/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 6/25/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/25/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 6/25/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
886 | 10549 | 10/8/2003 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/8/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 10/8/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered) | [7 empty] | 10/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
887 | 10550 | 9/3/2003 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/3/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 9/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Single Portable fire extinguisher | [6 empty] | 9/3/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
888 | 10551 | 7/14/2003 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 7/14/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/14/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 7/14/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/14/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
889 | 10552 | 7/8/2003 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 7/8/2003 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/8/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 7/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
890 | 10553 | 4/17/2000 | Not Challenging | No |  | Turbine Building | [7 empty] | 4/17/2000 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/17/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/17/2000 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
891 | 10554 | 5/3/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 5/3/2004 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 5/3/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 5/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 5/3/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
892 | 10555 | 5/5/2004 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 5/5/2004 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 5/5/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 5/5/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | [7 empty] | 5/5/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
893 | 10556 | 5/11/2004 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 5/11/2004 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/11/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 5/11/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
894 | 10557 | 1/13/2005 | Not Challenging | No |  | Drywell (BWR) |  | Other | [5 empty] | 1/13/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 1/13/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 1/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 1/13/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
895 | 10558 | 1/19/2005 | Potentially Challenging | No |  | Turbine Building |  | Air Compressors | [5 empty] | 1/19/2005 | PotentiallyChallenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 1/19/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/19/2005 | Potentially Challenging | 16:54:00 | 16:54:00 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/19/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
896 | 10559 | 3/7/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/7/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 3/7/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/7/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
897 | 10560 | 3/29/2005 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/29/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 3/29/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
898 | 10561 | 4/4/2005 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/4/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/4/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 4/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
899 | 10562 | 5/23/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/23/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 5/23/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/23/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 5/23/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
900 | 10563 | 7/11/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/11/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/11/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 7/11/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
901 | 10564 | 8/10/2005 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 8/10/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/10/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 8/10/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
902 | 10565 | 8/15/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 8/15/2005 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 8/15/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/15/2005 | Not Challenging |  | 12:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 8/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
903 | 10566 | 9/15/2005 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 9/15/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 9/15/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 9/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 9/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
904 | 10567 | 12/19/2005 | Not Challenging | No |  | Drywell (BWR) |  | Other | [5 empty] | 12/19/2005 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 12/19/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 12/19/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
905 | 10568 | 1/12/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 1/12/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 1/12/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 1/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher | [7 empty] | 1/12/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
906 | 10569 | 2/8/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 2/8/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Unknown | Other (specify) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 2/8/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 2/8/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
907 | 10570 | 2/13/2006 | Not Challenging | No |  | Turbine Building | [7 empty] | 2/13/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 2/13/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 2/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
908 | 10571 | 3/5/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 3/5/2006 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 3/5/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 3/5/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
909 | 10572 | 4/13/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Outlets | [5 empty] | 4/13/2006 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin | [9 empty] | 4/13/2006 | Not Challenging | Final | Challenging | [5 empty] | 4/13/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
910 | 10573 | 7/5/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 7/5/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/5/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 7/5/2006 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/5/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
911 | 10574 | 7/17/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 7/17/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/17/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 7/17/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
912 | 10575 | 7/18/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 7/18/2006 | NotChallenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 7/18/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/18/2006 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 7/18/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
913 | 10576 | 7/26/2006 | Potentially Challenging | No |  | Main Transformer or Switch Yard | Main Generator Hydrogen Cooling System | Other | [5 empty] | 7/26/2006 | PotentiallyChallenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Other (Specify) | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 7/26/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/26/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered) | [7 empty] | 7/26/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
914 | 10577 | 10/28/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin | Other (specify) | AC |  |  | 10/28/2006 | NotChallenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Overheating – no smoldering or flaming combustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 10/28/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/28/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
915 | 10578
916 | 10579 | 4/4/2008 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 4/4/2008 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 4/4/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/4/2008 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 4/4/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
917 | 10580 | 4/26/2008 | Not Challenging | No |  | Reactor Building (BWR) |  | Other | [5 empty] | 4/26/2008 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 4/26/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/26/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
918 | 10581 | 11/19/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 11/19/2008 | NotChallenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 11/19/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 11/19/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
919 | 10582 | 12/9/2005 | Undetermined (NC‐PC) | No | Containment/Drywell | Reactor Building (BWR) |  | Other | [5 empty] | 12/9/2005 | Undetermined(NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage | [9 empty] | 12/9/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 12/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | [7 empty] | 12/9/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
920 | 10583 | 9/1/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/1/2006 | NotChallenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Smoldering combustion – external to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | [9 empty] | 9/1/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 9/1/2006 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 9/1/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
921 | 10584 | 7/27/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring |  | Other (specify) | AC |  |  | 7/27/2008 | NotChallenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Explosion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 7/27/2008 | Not Challenging | Final | Challenging | [5 empty] | 7/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/27/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
922 | 10585 | 4/24/2003 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electric Motor | Other (specify in comments) |  |  |  |  | 4/24/2003 | Undetermined(NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | [9 empty] | 4/24/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/24/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/24/2003 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
923 | 10586 | 1/19/2000 | Not Challenging | No |  | Reactor Building (BWR) |  | Electric Motor | Fans |  |  |  |  | 1/19/2000 | : Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/19/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 1/19/2000 | Not Challenging |  | 15:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/19/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
924 | 10587 | 8/10/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/10/2000 | Not Challenging |  | Gas | Hydrogen | Pressurized in a container | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 8/10/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fixed suppression ‐ manually actuated | Other: Other [specify] | [6 empty] | 8/10/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
925 | 10588 | 11/21/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 11/21/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 11/21/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
926 | 10589 | 2/3/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient_Liquid | Fuel Oil | Unconfined spill | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/3/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/3/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
927 | 10590 | 10/3/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume |  | No | [8 empty] | 10/3/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/3/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 10/3/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
928 | 10591 | 10/8/2002 | Not Challenging | No |  | Control building | General Ventillation Systems | Transformers | [5 empty] | 10/8/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/8/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2002 | Not Challenging |  | 08:15:00 | Known | 517 | 517 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/8/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
929 | 10592 | 1/7/2003 | Not Challenging | No |  | Reactor Building (BWR) | DC Power System | Cable/Wiring |  | 24‐48VDC | DC |  |  | 1/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/7/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
930 | 10593 | 7/7/2003 | Not Challenging | No |  | Turbine Building | Main Generator System | Electrical panel | Relay rack |  |  |  |  | 7/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/7/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/7/2003 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
931 | 10594 | 1/25/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Motor control center |  |  |  |  | 1/25/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/25/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/25/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/25/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
932 | 10595 | 2/11/2004 | Not Challenging | No |  | Reactor Building (BWR) | Reactor Core Isolation Cooling System (BWR) | Other | [5 empty] | 2/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/11/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 2/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/11/2004 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
933 | 10596 | 11/4/2004 | Not Challenging | No |  | Turbine Building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 11/4/2004 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/4/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/4/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/4/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
934 | 10597
935 | 10598 | 1/3/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 1/3/2006 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/3/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 1/3/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/3/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
936 | 10599 | 3/25/2006 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 125VDC |  |  |  | 3/25/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/25/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/25/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/25/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
937 | 10600 | 2/18/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A |  |  |  | 2/18/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/18/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/18/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/18/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
938 | 10601 | 2/16/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A |  |  |  | 2/16/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/16/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 2/16/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 2/16/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
939 | 10602 | 2/13/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A |  |  |  | 2/13/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (Specify) | Other (Specify) | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/13/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/13/2008 | Not Challenging |  | 02:55:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/13/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
940 | 10603
941 | 10604 | 5/14/2001 | Potentially Challenging | No |  | Turbine Building | Main Turbine System | Lube Oil |  | N/A |  |  |  | 5/14/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/14/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/14/2001 | Potentially Challenging | 08:22:00 | 08:22:00 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | [7 empty] | 5/14/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
942 | 10605 | 1/31/2006 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans | N/A |  |  |  | 1/31/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/31/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/31/2006 | Potentially Challenging | 15:29:00 | 15:29:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/31/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
943 | 10606 | 5/6/2004 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Other |  | N/A |  |  |  | 5/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (Specify) | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/6/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 5/6/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
944 | 10607 | 12/27/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A |  |  |  | 12/27/2004 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | High – protective clothing needed for room entry | Confined to part of room or area of origin | Yes | [8 empty] | 12/27/2004 | Not Challenging | Final | Challenging | [5 empty] | 12/27/2004 | Not Challenging |  | 00:02:00 | Known | 49 | 49 | Installed Fire detector ‐ Type not specified |  | Plant area had installed detection which actuated | Portable: Dry Chemical,Other: Water | [6 empty] | 12/27/2004 | Not Challenging | Operate | Operate | 100 | 100 |  | Unusual Event | Not Challenging
945 | 10608 |  |  | No | [5 empty] | N/A
946 | 10609 | 9/7/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A |  |  |  | 9/7/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/7/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 9/7/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 9/7/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
947 | 10610 | [31 empty] | 8/20/2009 | Potentially Challenging | Final | Potentially Challenging
948 | 10611 | 8/20/2009 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) | High Pressure Safety Injection System (PWR) | Pumps | [5 empty] | 8/20/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [17 empty] | 8/20/2009 | Potentially Challenging |  | 15:49:00 | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 8/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
949 | 10612
950 | 10613
951 | 10614 | 2/25/2004 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/25/2004 | Undetermined (NC‐PC) FireID: 10614 | [5 empty] | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | [11 empty] | 2/25/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 2/25/2004 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown | [7 empty] | 2/25/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
952 | 10615 | 10/15/2005 | Undetermined (NC‐PC) | No | [9 empty] | 10/15/2005 | Undetermined (NC‐PC) | [5 empty] | possible with SCBA | [11 empty] | 10/15/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/15/2005 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown | [7 empty] | 10/15/2005 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
953 | 10616
954 | 10617 | 2/14/2003 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Pumps | Diesel driven pumps | N/A | N/A |  |  | 2/14/2003 | Undetermined (NC‐PC) | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a compartment | Explosion | Unknown | Unknown | Unknown | [9 empty] | 2/14/2003 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 2/14/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/14/2003 | Refueling | Operate | Operate | 100 | 100 |  |  | Not Challenging
955 | 10618 | 2/15/2000 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Dryers |  | 480V | AC |  |  | 2/15/2000 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/15/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/15/2000 | Undetermined (PC‐CH) | 16:17:00 | 16:17:00 | Known | 13 | 13 | Roving Firewatch | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 2/15/2000 | Undetermined (PC‐CH) | Operate | Operate |  |  |  |  | Challenging
956 | 10619 | 5/24/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | 480V | AC |  |  | 5/24/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/24/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 5/24/2000 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 5/24/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
957 | 10620 | 8/9/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | 220V | AC |  |  | 8/9/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/9/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 8/9/2000 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
958 | 10621 | 8/22/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 8/22/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/22/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/22/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 8/22/2000 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
959 | 10622 | 6/25/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/25/2001 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/25/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/25/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown | [7 empty] | 6/25/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
960 | 10623 | 8/8/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring |  | N/A | N/A |  |  | 8/8/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/8/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 8/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
961 | 10624 | 10/26/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | Oil‐filled Transformer | 110V | AC |  |  | 10/26/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No | [8 empty] | 10/26/2001 | Not Challenging | Final | Challenging | [5 empty] | 10/26/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown | [7 empty] | 10/26/2001 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
962 | 10625 | 9/28/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers |  | N/A | N/A |  |  | 9/28/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/28/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 9/28/2002 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
963 | 10626 | 12/11/2002 | Potentially Challenging | No |  | Service Water Pump house |  | Pumps | Electric motor driven pumps | 480V | AC |  |  | 12/11/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/11/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/11/2002 | Potentially Challenging | 03:05:00 | 03:05:00 | Known | 67 | 67 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/11/2002 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
964 | 10627 | 12/12/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/12/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/12/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 12/12/2002 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
965 | 10628 | 12/30/2005 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Low Voltage Power System, Class 1E | Cable/Wiring |  | 110V | AC |  |  | 12/30/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/30/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 12/30/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 12/30/2005 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
966 | 10629
967 | 10630 | 6/6/2007 | Potentially Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Air Compressors |  | N/A | N/A |  |  | 6/6/2007 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Flaming combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/6/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/6/2007 | Potentially Challenging | 15:36:00 | 15:36:00 | Known |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/6/2007 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
968 | 10631 | 11/28/2001 | Not Challenging | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 11/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No | [8 empty] | 11/28/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/28/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 11/28/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
969 | 10632 | 3/3/2000 | Challenging | No |  | Diesel Generator Building | DC Power System, class 1E | Transformers | Dry transformer | 4KV | AC |  |  | 3/3/2000 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/3/2000 | Challenging | Final | Challenging | [5 empty] | 3/3/2000 | Challenging | 11:45:00 | 11:45:00 | Known | 275 | 275 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Halon | [6 empty] | 3/3/2000 | Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
970 | 10633 | 3/7/2000 | Potentially Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 3/7/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/7/2000 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/7/2000 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/7/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
971 | 10634
972 | 10635
973 | 10636 | 9/26/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 9/26/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable Tray | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/26/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 9/26/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | [7 empty] | 9/26/2000 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
974 | 10637
975 | 10638 | 3/5/2001 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/5/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/5/2001 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/5/2001 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 3/5/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
976 | 10639 | 2/16/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  |  |  | N/A | N/A |  |  | 2/16/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No | [8 empty] | 2/16/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 2/16/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
977 | 10640
978 | 10641 | 3/11/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) | Reactor Recirculation System (BWR) | Electrical panel | Relay rack |  |  |  |  | 3/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Flaming combustion – internal to component | Flaming combustion – internal to component | Confined to the object of origin | No | [8 empty] | 3/11/2001 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/11/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
979 | 10642 | 3/14/2002 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/14/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/14/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/14/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water | [6 empty] | 3/14/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
980 | 10643 | 5/22/2002 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Air Compressors |  | Other (specify) | AC |  |  | 5/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/22/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 5/22/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/22/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
981 | 10644 | 11/3/2002 | Potentially Challenging | No |  | Control building | [7 empty] | 11/3/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/3/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/3/2002 | Potentially Challenging |  |  | Known | 7 | 7 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical | [6 empty] | 11/3/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
982 | 10645 | 4/11/2003 | Not Challenging | No | N/A | Turbine Building | Main Turbine System | Electric Motor | Other (specify in comments) | 480V | AC |  |  | 4/11/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/11/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/11/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 4/11/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
983 | 10646 | 7/17/2003 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/17/2003 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/17/2003 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/17/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 7/17/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
984 | 10647 | 8/22/2003 | Potentially Challenging | No | N/A | Reactor Building (BWR) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 8/22/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/22/2003 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 8/22/2003 | Potentially Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 8/22/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
985 | 10648 | 3/12/2004 | Potentially Challenging | No |  | Turbine Building |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 3/12/2004 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/12/2004 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/12/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/12/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
986 | 10649 | 3/15/2004 | Potentially Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 3/15/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/15/2004 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/15/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 3/15/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
987 | 10650 | 3/20/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 480V | AC |  |  | 3/20/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/20/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/20/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | [7 empty] | 3/20/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
988 | 10651
989 | 10652 | 3/10/2005 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/10/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/10/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 3/10/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
990 | 10653 | 4/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Motor control center |  |  |  |  | 4/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/3/2005 | Not Challenging |  | 04:43:00 | Known | 334 | 334 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/3/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
991 | 10654 | 2/5/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 2/5/2007 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/5/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 2/5/2007 | Not Challenging |  | 11:08:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/5/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
992 | 10655
993 | 10656 | 2/22/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 2/22/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/22/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/22/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 2/22/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
994 | 10657 | 6/29/2009 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps | N/A | N/A |  |  | 6/29/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/29/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 6/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2 | [6 empty] | 6/29/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
995 | 10658 | 12/29/2009 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Electrical panel | [5 empty] | 12/29/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/29/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 12/29/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 12/29/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
996 | 10659
997 | 10660 | 11/6/2009 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/6/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/6/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/6/2009 | Not Challenging |  | 22:20:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/6/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
998 | 10661
999 | 10662
1000 | 10663
1001 | 10664 | 10/2/2000 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 10/2/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/2/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 10/2/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/2/2000 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1002 | 10665 | 11/3/2000 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 11/3/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/3/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/3/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 11/3/2000 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1003 | 10666 | 4/18/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/18/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/18/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 4/18/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1004 | 10667 | 4/26/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/26/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/26/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 4/26/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1005 | 10668 | 4/22/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/22/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/22/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/22/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 4/22/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1006 | 10669 | 5/20/2001 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps |  |  |  |  | 5/20/2001 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/20/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 5/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1007 | 10670 | 6/1/2001 | Not Challenging | No |  | Control building |  | Electric Motor | Fans | N/A | N/A |  |  | 6/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/1/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 6/1/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1008 | 10671 | 6/21/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | High Pressure Core Spray System (BWR) | Pumps | Turbine‐driven pump | N/A | N/A |  |  | 6/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/21/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 6/21/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1009 | 10672 | 6/26/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/26/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 |  |  | Unknown | [7 empty] | 6/26/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1010 | 10673 | 9/4/2001 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Lube Oil |  | N/A | N/A |  |  | 9/4/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/4/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 9/4/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown | [7 empty] | 9/4/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1011 | 10674 | 12/5/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 12/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/5/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 12/5/2002 | Not Challenging | 06:45:00 | 06:45:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 12/5/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1012 | 10675 | 12/31/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 12/31/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/31/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 12/31/2002 | Not Challenging |  | 14:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 12/31/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1013 | 10676 | 3/29/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/29/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 3/29/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1014 | 10677 | 4/4/2003 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 4/4/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/4/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/4/2003 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/4/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1015 | 10678 | 5/29/2003 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 5/29/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 5/29/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | [7 empty] | 5/29/2003 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1016 | 10679 | 1/9/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 1/9/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/9/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/9/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 1/9/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1017 | 10680 | 7/10/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 7/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/10/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/10/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 7/10/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1018 | 10681 | 11/12/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 11/12/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Liquid | Other (Specify) | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/12/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/12/2004 | Not Challenging |  | 14:55:00 | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 11/12/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1019 | 10682 | 4/2/2005 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/2/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/2/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/2/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/2/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1020 | 10683 | 4/5/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/5/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/5/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1021 | 10684 | 4/6/2005 | Potentially Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/6/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/6/2005 | Potentially Challenging | Final | Not Challenging | [5 empty] | 4/6/2005 | Potentially Challenging |  |  | Known | 0 | 0 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/6/2005 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
1022 | 10685 | 4/11/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/11/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/11/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/11/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/11/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1023 | 10686 | 4/13/2005 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 4/13/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/13/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/13/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1024 | 10687 | 5/4/2005 | Not Challenging | No | [9 empty] | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/4/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 5/4/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1025 | 10688 | 10/31/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/31/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/31/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/31/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/31/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1026 | 10689 | 1/26/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 1/26/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/26/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/26/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/26/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1027 | 10690 | 2/9/2007 | Not Challenging | No | Cable vault/tunnel area | Other (Specify in comments) | Feedwater System | Other |  | N/A | N/A |  |  | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/9/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 2/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1028 | 10691 | 2/25/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Other generator (specify in com |  |  |  |  | 2/25/2007 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/25/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed,Unknown | [7 empty] | 2/25/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1029 | 10692
1030 | 10693 | 3/4/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 3/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/4/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 3/4/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1031 | 10694 | 7/10/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/10/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1032 | 10695 | 7/27/2007 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | 110V | AC |  |  | 7/27/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/27/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 7/27/2007 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1033 | 10696 | 8/30/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 8/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/30/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 8/30/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 8/30/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1034 | 10697 | 2/25/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 2/25/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 2/25/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/25/2008 | Not Challenging |  | 09:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 2/25/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1035 | 10698 | 4/18/2008 | Not Challenging | No |  | Radwaste Building |  | Other |  | 110V | AC |  |  | 4/18/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/18/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/18/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1036 | 10699 | 4/24/2008 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 4/24/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/24/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/24/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/24/2008 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1037 | 10700 | 7/18/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 7/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | [10 empty] | 7/18/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/18/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1038 | 10701 | 8/25/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 8/25/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/25/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/25/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1039 | 10702 | 2/8/2009 | Not Challenging | No |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Electric bus bar or bus duct |  |  |  |  | 2/8/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/8/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 2/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1040 | 10703 | 11/21/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 11/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/21/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/21/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/21/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1041 | 10704 | 3/28/2002 | Not Challenging | No |  | Reactor Building (BWR) | High Pressure Core Spray System (BWR) | Pumps | Turbine‐driven pump |  |  |  |  | 3/28/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/28/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/28/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1042 | 10705 | 12/3/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 12/3/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/3/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 12/3/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1043 | 10706 | 12/4/2003 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 12/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/4/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 12/4/2003 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1044 | 10707 | 8/8/2004 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 8/8/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/8/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/8/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1045 | 10708 | 9/22/2004 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 9/22/2004 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/22/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 9/22/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 9/22/2004 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1046 | 10709 | 2/1/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | DC Power System | Electrical panel | Battery charger | 125VDC | DC |  |  | 2/1/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/1/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/1/2005 | Not Challenging | 07:20:00 | 07:20:00 | Known | 5 | 5 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 2/1/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1047 | 10710 | 11/21/2005 | Not Challenging | No |  | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator | N/A | N/A |  |  | 11/21/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/21/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/21/2005 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1048 | 10711 | 1/8/2006 | Not Challenging | No | N/A | Diesel Generator Building | DC Power System, class 1E | Generator | Class 1A emergency generator | N/A | N/A |  |  | 1/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/8/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 1/8/2006 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1049 | 10712 | 10/8/2006 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 10/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No | [8 empty] | 10/8/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/8/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1050 | 10713 | 3/25/2007 | Undetermined (NC‐PC) | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 3/25/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/25/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 3/25/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 3/25/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1051 | 10714
1052 | 10715 | 2/5/2009 | Potentially Challenging | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/5/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/5/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/5/2009 | Potentially Challenging |  | 04:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/5/2009 | Potentially Challenging | Refueling | Refueling |  |  |  |  | Challenging
1053 | 10716 | 7/26/2009 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 7/26/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/26/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/26/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 7/26/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1054 | 10717 | 4/12/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 4/12/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/12/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/12/2003 | Not Challenging |  | 01:35:00 | Unknown | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 4/12/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1055 | 10718 | 5/20/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 5/20/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/20/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/20/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | [7 empty] | 5/20/2004 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1056 | 10719 | 6/1/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 6/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/1/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/1/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1057 | 10720 | 4/8/2006 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Main turbine generator | N/A | N/A |  |  | 4/8/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/8/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/8/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 4/8/2006 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1058 | 10721 | 8/26/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 8/26/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/26/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 8/26/2007 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1059 | 10722 | 9/3/2007 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 9/3/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/3/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/3/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 9/3/2007 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1060 | 10723 | 10/4/2007 | Potentially Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Main turbine generator | N/A | N/A |  |  | 10/4/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/4/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/4/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/4/2007 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
1061 | 10724 | 10/7/2007 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 10/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/7/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/7/2007 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1062 | 10725 | 10/29/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 10/29/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 10/29/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/29/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/29/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1063 | 10726 | 11/4/2007 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 11/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/4/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/4/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1064 | 10727 | 2/5/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/5/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 2/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 2/5/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1065 | 10728 | 8/23/2009 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 8/23/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/23/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 8/23/2009 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1066 | 10729 | 4/3/2009 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/3/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Lube Oil or Grease | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | [7 empty] | 4/3/2009 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1067 | 10730 | 3/16/2006 | Not Challenging | No |  | Containment (PWR) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 3/16/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/16/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/16/2006 | Not Challenging |  |  | Unknown |  |  | Unknown |  |  | Unknown | [6 empty] | 3/16/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1068 | 10731 | 6/27/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 6/27/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/27/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 6/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/27/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1069 | 10732 | 4/22/2002 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 4/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/22/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/22/2002 | Not Challenging |  | 01:35:00 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 4/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1070 | 10733 | 4/7/2003 | Not Challenging | No | N/A | Turbine Building | Cable Raceway System | Cable/Wiring | [5 empty] | 4/7/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Unknown | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/7/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1071 | 10734 | 4/27/2004 | Not Challenging | No |  | Turbine Building | Main Generator Hydrogen Cooling System | Other | [5 empty] | 4/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/27/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/27/2004 | Not Challenging |  | 15:30:00 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1072 | 10735 | 4/28/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 4/28/2006 | Not Challenging | Unknown | In_Situ | Other (Specify) |  | Fire not observed and fire type indeterminate from post‐inspection | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/28/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 4/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/28/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1073 | 10736 | 12/6/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/6/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/6/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 12/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 12/6/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1074 | 10737 | 11/30/2006 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Other instrument/control cabin |  |  |  |  | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No | [8 empty] | 11/30/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/30/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/30/2006 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1075 | 10738 | 8/22/2001 | Not Challenging | No |  | Auxiliary Building (PWR) | Feedwater System | Other | [5 empty] | 8/22/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/22/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/22/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/22/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1076 | 10739 | 4/24/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 4/24/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/24/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/24/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 4/24/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1077 | 10740 | 10/8/2009 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 10/8/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1078 | 10741 | 9/21/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Crane |  | N/A | N/A |  |  | 9/21/2007 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/21/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/21/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1079 | 10742 | 4/11/2004 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps | 480V |  |  |  | 4/11/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/11/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/11/2004 | Not Challenging | 10:00:00 | 10:00:00 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin |  | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/11/2004 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1080 | 10743 | 4/19/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 4/19/2001 | Unknown |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | Unknown | Confined to the object of origin | No | [8 empty] | 4/19/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out | [7 empty] | 4/19/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1081 | 10744 | 8/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/17/2001 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/17/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1082 | 10745 | 7/25/2006 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 7/25/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/25/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/25/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1083 | 10746 | 5/12/2000 | Not Challenging | No |  | Control building | Instrument and Uninterruptible Power System, Class 1E | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 5/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/12/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/12/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1084 | 10747 | 1/15/1999 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 1/15/1999 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/15/1999 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/15/1999 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1085 | 10748 | 5/29/2003 | Not Challenging | No |  |  |  | Electric Motor | [5 empty] | 5/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/29/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/29/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1086 | 10749 | 9/10/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 9/10/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/10/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/10/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/10/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1087 | 10750 | 2/28/2009 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Cable/Wiring |  | 480V | AC |  |  | 2/28/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/28/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 2/28/2009 | Not Challenging |  | 05:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical | [6 empty] | 2/28/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1088 | 10751 | 1/28/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 1/28/2000 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/28/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/28/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 1/28/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1089 | 10752
1090 | 10753
1091 | 10754
1092 | 20264 | 1/19/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Motor control center |  |  |  |  | 1/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/19/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/2/1990 | Undetermined (NC‐PC | Operate | Operate |  |  |  |  | Not Challenging
1093 | 20265 | 2/2/1990 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Pumps | Turbine‐driven pump |  |  |  |  | 2/2/1990 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 2/2/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/2/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/2/1990 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1094 | 20266 | 2/19/1990 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 2/19/1990 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 2/19/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Unknown | [7 empty] | 2/19/1990 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1095 | 20267 | 3/12/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Motor control center |  |  |  |  | 3/12/1990 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/12/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/12/1990 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1096 | 20268 | 4/19/1990 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure |  | Electrical panel | Motor control center |  |  |  |  | 4/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 4/19/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 4/19/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/19/1990 D | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1097 | 20269 | 4/30/1990 | Undetermined (NC‐PC) | No |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 4/30/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 4/30/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 4/30/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 4/30/1990 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1098 | 20270 | 6/7/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Motor control center |  |  |  |  | 6/7/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 6/7/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/7/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 6/7/1990 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1099 | 20271 | 7/9/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Transformers | Dry transformer |  |  |  |  | 7/9/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/9/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/9/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/9/1990 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1100 | 20272 | 9/10/1990 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Relay rack |  |  |  |  | 9/10/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/10/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 9/10/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/10/1990 | Undetermined (NC‐PC | Unknown | Unknown |  |  |  |  | Not Challenging
1101 | 20273 | 9/18/1990 | Potentially Challenging | No | Switchgear Room |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 9/18/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No | [8 empty] | 9/18/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 9/18/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 9/18/1990 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1102 | 20274 | 10/9/1990 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor | MG set |  |  |  |  | 10/9/1990 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 10/9/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/9/1990 | Potentially Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | [7 empty] | 10/9/1990 | Potentially Challenging | Operate | Operate | 0 |  |  |  | Challenging
1103 | 20275 | 10/11/1990 | Undetermined (NC‐PC) | No |  |  |  | Electrical panel | Motor control center |  |  |  |  | 10/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/11/1990 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 10/11/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 10/11/1990 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1104 | 20276 | 10/12/1990 | Undetermined (NC‐PC) | No |  | Turbine Building | Reactor Coolant System | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 10/12/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/12/1990 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 10/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/12/1990 D | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1105 | 20277 | 11/16/1990 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 11/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/16/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 11/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/16/1990 | : Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1106 | 20278 | 11/24/1990 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 11/24/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/24/1990 | Not Challenging | Final | Not Challenging | [5 empty] | 11/24/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 11/24/1990 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 |  |  | Not Challenging
1107 | 20279 | 11/28/1990 | Undetermined (NC‐PC) | No |  |  |  | Transformers | Dry transformer | 480V | AC |  |  | 11/28/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/28/1990 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/28/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 11/28/1990 | : Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1108 | 20280 | 12/5/1990 | Undetermined (PC‐CH) | No |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 12/5/1990 | Undetermined (PC‐CH) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 12/5/1990 | Not Challenging | Final | Challenging | [5 empty] | 12/5/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 12/5/1990 | : Undetermined (PC‐CH) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Challenging
1109 | 20281 | 6/24/1991 | Undetermined (NC‐PC) | No | [9 empty] | 6/24/1991 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 6/24/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 6/24/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 6/24/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1110 | 20282 | 9/17/1991 | Undetermined (NC‐PC) | No |  |  |  | Electrical panel | Motor control center |  |  |  |  | 9/17/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 9/17/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 9/17/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/17/1991 | : Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1111 | 20283 | 10/3/1991 | Undetermined (NC‐PC) | No |  | Radwaste Building |  | Electric Motor | [5 empty] | 10/3/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/3/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/3/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/3/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1112 | 20284 | 10/14/1991 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Bus Duct | Other | 4KV | AC |  |  | 10/14/1991 | Undetermined (NC‐PC) | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/14/1991 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 10/14/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 10/14/1991 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1113 | 20285 | 10/25/1991 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/25/1991 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/25/1991 | Not Challenging | Final | Not Challenging | [5 empty] | 10/25/1991 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 10/25/1991 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1114 | 20286 | 1/23/1992 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers |  | 13 KV or greater | AC |  |  | 1/23/1992 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 1/23/1992 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/23/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/23/1992 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1115 | 20287 | 2/29/1992 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Motor control center |  |  |  |  | 2/29/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/29/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 2/29/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/29/1992 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1116 | 20288 | 3/9/1992 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 3/9/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 3/9/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/9/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 3/9/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1117 | 20289 | 3/16/1992 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | [7 empty] | 3/16/1992 | Undetermined (NC‐PC) | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 3/16/1992 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/16/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/16/1992 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1118 | 20290 | 4/26/1992 | Not Challenging | No | [9 empty] | 4/26/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Unknown | Unknown | No damage | No | [8 empty] | 4/26/1992 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/26/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/26/1992 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1119 | 20291 | 4/28/1992 | Potentially Challenging | No |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 4/28/1992 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/28/1992 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/28/1992 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 4/28/1992 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1120 | 20292 | 6/25/1992 | Undetermined (NC‐PC) | No |  | Turbine Building | Main Generator Hydrogen Cooling System | Generator | Main turbine generator |  |  |  |  | 6/25/1992 | Undetermined (NC‐PC) | Personnel error: Misuse of material ignited | Gas | Hydrogen | Jet from a pressurized source | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 6/25/1992 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 6/25/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/25/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1121 | 20293 | 9/1/1992 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 9/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/1/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 9/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 9/1/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1122 | 20294 | 10/5/1992 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | [7 empty] | 10/5/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/5/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/5/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 10/5/1992 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1123 | 20295 | 10/12/1992 | Undetermined (NC‐PC) | No |  | Radwaste Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 10/12/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/12/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/12/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/12/1992 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 |  |  | Not Challenging
1124 | 20296 | 10/23/1992 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 10/23/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/23/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/23/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown | [7 empty] | 10/23/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1125 | 20297 | 11/17/1992 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 11/17/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/17/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 11/17/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/17/1992 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1126 | 20298 | 1/11/1993 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electric Motor | Elevator motor |  |  |  |  | 1/11/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 1/11/1993 | Undetermined (NC‐PC) | Preliminary | Challenging | [5 empty] | 1/11/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/11/1993 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1127 | 20299 | 3/9/1993 | Not Challenging | No |  |  |  | Other | [5 empty] | 3/9/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/9/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 3/9/1993 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/9/1993 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1128 | 20300 | 3/30/1993 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 3/30/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Insulation | Type not specified | Unknown | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/30/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/30/1993 | Undetermined (NC‐PC) R |  | Refueling | 0 | 0 | None |  | Not Challenging
1129 | 20301 | 4/13/1993 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 4/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 4/13/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/13/1993 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 |  |  | Not Challenging
1130 | 20302 | 7/25/1993 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Electrical panel | Motor control center |  |  |  |  | 7/25/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/25/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 7/25/1993 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/25/1993 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1131 | 20303 | 10/14/1993 | Potentially Challenging | No |  | Diesel Generator Building |  | Other | [5 empty] | 10/14/1993 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/14/1993 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/14/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify] | [6 empty] | 10/14/1993 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1132 | 20304 | 11/2/1993 | Potentially Challenging | No |  | Reactor Building (BWR) | General Ventillation Systems | [6 empty] | 11/2/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/2/1993 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/2/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 11/2/1993 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
1133 | 20305 | 11/18/1993 | Not Challenging | No |  | Turbine Building | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 11/18/1993 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/18/1993 | Not Challenging | Final | Not Challenging | [5 empty] | 11/18/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/18/1993 | Not Challenging | Operate | Refueling | 0 | 0 | None |  | Not Challenging
1134 | 20306 | 12/30/1993 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 12/30/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/30/1993 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 12/30/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 12/30/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1135 | 20307 | 1/25/1994 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 1/25/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/25/1994 | Not Challenging | Final | Not Challenging | [5 empty] | 1/25/1994 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 1/25/1994 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1136 | 20308 | 3/9/1994 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 3/9/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/9/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/9/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 3/9/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1137 | 20309 | 3/11/1994 | Not Challenging | Yes |  | Turbine Building |  | Other | [5 empty] | 3/11/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/11/1994 | Not Challenging | Preliminary | Not Challenging | [5 empty] | 3/11/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 3/11/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1138 | 20310 | 3/26/1994 | Undetermined (NC‐PC) | No | Containment/Drywell | Reactor Building (BWR) | [7 empty] | 3/26/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/26/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 3/26/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/26/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1139 | 20311 | 4/4/1994 | Undetermined (NC‐PC) | No | Containment/Drywell | [8 empty] | 4/4/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 4/4/1994 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 4/4/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 4/4/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1140 | 20312 | 7/27/1994 | Undetermined (NC‐PC) | No | [9 empty] | 7/27/1994 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 7/27/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/27/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 7/27/1994 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1141 | 20313 | 9/29/1994 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Boilers | [5 empty] | 9/29/1994 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 9/29/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 9/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 9/29/1994 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1142 | 20314 | 12/19/1994 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electric Motor | Other (specify in comments) |  |  |  |  | 12/19/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/19/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 12/19/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 12/19/1994 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1143 | 20315 | 2/20/1995 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 2/20/1995 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/20/1995 | Not Challenging | Final | Not Challenging | [5 empty] | 2/20/1995 | Not Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 2/20/1995 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1144 | 20316 | 2/24/1995 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 2/24/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/24/1995 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/24/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 2/24/1995 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1145 | 20317 | 4/10/1995 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 4/10/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 4/10/1995 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 4/10/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 4/10/1995 D | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1146 | 20318 | 8/9/1995 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 8/9/1995 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 8/9/1995 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/9/1995 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Other [specify] | [6 empty] | 8/9/1995 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1147 | 20319 | 8/15/1995 | Undetermined (NC‐PC) | No |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 8/15/1995 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No | [8 empty] | 8/15/1995 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 8/15/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | Portable: Other [specify] | [6 empty] | 8/15/1995 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | Entered an LCO |  | Not Challenging
1148 | 20320 | 3/21/1996 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 3/21/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 3/21/1996 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 3/21/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 3/21/1996 D | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1149 | 20321 | 7/10/1996 | Not Challenging | Yes |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 7/10/1996 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 7/10/1996 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/10/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/10/1996 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1150 | 20322 | 9/13/1996 | Undetermined (NC‐PC) | No |  | Turbine Building | Feedwater System | Lube Oil | Turbine‐driven pump |  |  |  |  | 9/13/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 9/13/1996 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 9/13/1996 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 9/13/1996 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1151 | 20323 | 1/8/1997 | Challenging | No |  | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electric Motor | MG set | 480V | AC |  |  | 1/8/1997 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 1/8/1997 | Challenging | Preliminary | Challenging | [5 empty] | 1/8/1997 | Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments) | Portable: Other [specify] | [6 empty] | 1/8/1997 | Challenging | Operate | Operate |  |  |  |  | Challenging
1152 | 20324 | 8/12/1997 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 8/12/1997 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/12/1997 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 8/12/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/12/1997 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1153 | 20325 | 1/16/1998 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure |  | Cable/Wiring | [5 empty] | 1/16/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 1/16/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 1/16/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify | [6 empty] | 1/16/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1154 | 20326 | 10/12/1998 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 10/12/1998 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/12/1998 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 10/12/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 10/12/1998 D | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1155 | 20327 | 11/2/1998 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin | 4KV | AC |  |  | 11/2/1998 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/2/1998 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/1998 | Not Challenging | 05:55:00 | 05:55:00 | Known | 7 | 7 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/2/1998 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1156 | 20328 | 5/6/1999 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 5/6/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 5/6/1999 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 5/6/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 5/6/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1157 | 20329 | 9/1/1999 | Undetermined (NC‐PC) | No | Switchgear Room |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 9/1/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/1/1999 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 9/1/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | [7 empty] | 9/1/1999 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1158 | 20330 | 10/3/1999 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 10/3/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 10/3/1999 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 10/3/1999 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 10/3/1999 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1159 | 20331 | 11/4/1999 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 11/4/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/4/1999 | Not Challenging | Final | Not Challenging | [5 empty] | 11/4/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 11/4/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1160 | 20332 | 12/14/1999 | Not Challenging | No | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 12/14/1999 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/14/1999 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/14/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 12/14/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1161 | 20333 | 1/12/1990 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 1/12/1990 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/12/1990 | Not Challenging | Final | Not Challenging | [5 empty] | 1/12/1990 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 1/12/1990 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1162 | 20334 | 2/20/1990 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 2/20/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 2/20/1990 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/20/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/20/1990 | Undetermined (NC‐PC) | Operate | Operate | 0 | 0 | None |  | Not Challenging
1163 | 20335 | 4/13/1990 | Not Challenging | No |  | Turbine Building | [7 empty] | 4/13/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 4/13/1990 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/13/1990 | Not Challenging |  |  | Unknown | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 4/13/1990 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1164 | 20336 | 2/14/1991 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | [7 empty] | 2/14/1991 | Undetermined (NC‐PC) | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 2/14/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 2/14/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 2/14/1991 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1165 | 20337 | 4/21/1991 | Undetermined (NC‐PC) | No |  | Turbine Building | [7 empty] | 4/21/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 4/21/1991 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/21/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/21/1991 | Undetermined (NC‐PC) |  | Operate | 0 | 0 | None |  | Not Challenging
1166 | 20338 | 10/11/1991 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | High Pressure Safety Injection System (PWR) | Pumps | Electric motor driven pumps |  |  |  |  | 10/11/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 10/11/1991 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/11/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Unknown | [7 empty] | 10/11/1991 | 10/11/1991 | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1167 | 20339 | [12 empty] | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1168 | 20340 | 12/1/1992 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/1/1992 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 12/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 12/1/1992 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1169 | 20341 | 3/31/1993 | Undetermined (NC‐PC) | No | [9 empty] | 3/31/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | In_Situ | Other (Specify) |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 3/31/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/31/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/31/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1170 | 20342 | 4/30/1993 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 4/30/1993 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 4/30/1993 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 4/30/1993 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1171 | 20343 | 8/13/1993 | Not Challenging | No |  | Reactor Building (BWR) | [7 empty] | 8/13/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Unknown | Unknown | No damage | No | [8 empty] | 8/13/1993 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 8/13/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Air supply cut off (smothered, covered) | [7 empty] | 8/13/1993 D | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1172 | 20344 | 2/20/1994 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electric Motor | [5 empty] | 2/20/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No | [8 empty] | 2/20/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 2/20/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 2/20/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1173 | 20345 | 3/28/1994 | Not Challenging | No |  | Turbine Building | [7 empty] | 3/28/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No | [8 empty] | 3/28/1994 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/28/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 3/28/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1174 | 20346 | 3/30/1994 | Undetermined (NC‐PC) | No | Switchgear Room | Other (Specify in comments) |  | Electrical panel | Switchgear |  |  |  |  | 3/30/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 3/30/1994 | Undetermined (NC‐PC) | Preliminary | Challenging | [5 empty] | 3/30/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/30/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1175 | 20347 | 4/15/1994 | Not Challenging | No |  | Turbine Building | [7 empty] | 4/15/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 4/15/1994 | Not Challenging | Preliminary | Challenging | [5 empty] | 4/15/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 4/15/1994 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1176 | 20348 | 4/16/1994 | Undetermined (NC‐PC) | No | Containment/Drywell | Drywell (BWR) | [7 empty] | 4/16/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 4/16/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/16/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 4/16/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1177 | 20349 | 4/23/1994 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 4/23/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 4/23/1994 | Undetermined (NC‐PC) | Preliminary | Challenging | [5 empty] | 4/23/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 4/23/1994 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1178 | 20350 | 6/9/1994 | Undetermined (NC‐PC) | No | Fuel handling area | Reactor Building (BWR) |  | Crane | [5 empty] | 6/9/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 6/9/1994 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/9/1994 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/9/1994 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1179 | 20351 | 6/21/1994 | Undetermined (NC‐PC) | No | Main Control Room | Radwaste Building |  | Electrical panel | Main control board (i.e., the ma |  |  |  |  | 6/21/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 6/21/1994 | Undetermined (NC‐PC) | Preliminary | Challenging | [5 empty] | 6/21/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 6/21/1994 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1180 | 20352 | 6/23/1994 | Potentially Challenging | No |  | Main Transformer or Switch Yard |  | Transformers | Oil‐filled Transformer |  |  |  |  | 6/23/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/23/1994 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 6/23/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 6/23/1994 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1181 | 20353 | 7/13/1994 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Air Compressors |  | 480V | AC |  |  | 7/13/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/13/1994 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/13/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/13/1994 | Potentially Challenging | Operate |  | 100 | 100 | None |  | Challenging
1182 | 20354 | 10/8/1994 | Not Challenging | Yes |  | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  | 110V | AC |  |  | 10/8/1994 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Bundle | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 10/8/1994 | Not Challenging | Final | Challenging | [5 empty] | 10/8/1994 | Not Challenging |  |  | Known |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/8/1994 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1183 | 20355 | 10/31/1994 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabin |  |  |  |  | 10/31/1994 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/31/1994 | Not Challenging | Preliminary | Not Challenging | [5 empty] | 10/31/1994 | Not Challenging | 09:22:00 | 09:22:00 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed | [7 empty] | 10/31/1994 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1184 | 20356 | 2/19/1995 | Potentially Challenging | No |  | Turbine Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 2/19/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No | [8 empty] | 2/19/1995 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 2/19/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/19/1995 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1185 | 20357 | 5/24/1995 | Potentially Challenging | No |  | Turbine Building |  | Electrical panel | Motor control center |  |  |  |  | 5/24/1995 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 5/24/1995 | Potentially Challenging | Final | Not Challenging | [5 empty] | 5/24/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/24/1995 | Potentially Challenging | Operate | Hot Standby | 100 | 0 | Scram |  | Challenging
1186 | 20358 | 1/23/1996 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Instrument and Uninterruptible Power System | Air Compressors |  | 600V | AC |  |  | 1/23/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 1/23/1996 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 1/23/1996 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/23/1996 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1187 | 20359 | 3/3/1996 | Potentially Challenging | No |  | Turbine Building |  | Air Compressors | [5 empty] | 3/3/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No | [8 empty] | 3/3/1996 | Potentially Challenging | Final | Challenging | [5 empty] | 3/3/1996 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 3/3/1996 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1188 | 20360 | 5/25/1996 | Undetermined (PC‐CH) | No |  | Turbine Building |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 5/25/1996 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to fire rated compartment of origin | No | [8 empty] | 5/25/1996 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 5/25/1996 | Undetermined (PC‐CH) |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/25/1996 | Undetermined (PC‐CH) | Unknown | Unknown |  |  |  |  | Challenging
1189 | 20361 | 1/7/1997 | Undetermined (NC‐PC) | No | Fuel handling area | Other (Specify in comments) | [7 empty] | 1/7/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 1/7/1997 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/7/1997 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/7/1997 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1190 | 20362 | 3/2/1997 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 3/2/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/2/1997 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/2/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/2/1997 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1191 | 20363 | 7/27/1997 | Not Evaluated | No |  | Auxiliary Building (PWR) |  | Junction Boxes | [5 empty] | 7/27/1997 | Not Evaluated | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 7/27/1997 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/27/1997 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed | [7 empty] | 7/27/1997 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1192 | 20364 | 12/4/1997 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | General Ventillation Systems | Electric Motor | Elevator motor | 220V | AC |  |  | 12/4/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 12/4/1997 | Undetermined (NC‐PC) | Preliminary | Challenging | [5 empty] | 12/4/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/4/1997 | Undetermined (NC‐PC) | Operate | Operate |  |  | None |  | Not Challenging
1193 | 20365 | 1/13/1998 | Potentially Challenging | No |  | Radwaste Building | Offgas System (BWR) | [6 empty] | 1/13/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Interior finish |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 1/13/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 1/13/1998 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/13/1998 | Potentially Challenging | Operate | Operate | 100 | 75 | Reduced Power |  | Challenging
1194 | 20366 | 2/6/1998 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/6/1998 | Undetermined (NC‐PC) | Unknown | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 2/6/1998 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/6/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/6/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1195 | 20367 | 2/24/1998 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Pumps | Diesel driven pumps |  |  |  |  | 2/24/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (Specify) | Leak - Oil soaked Insulation | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 2/24/1998 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 2/24/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/24/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1196 | 20368 | 6/7/1998 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Instrument and Uninterruptible Power System | Air Compressors |  | 600V | AC |  |  | 6/7/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/7/1998 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 6/7/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/7/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1197 | 20369 | 6/14/1998 | Potentially Challenging | No |  |  |  | Transformers | Other (Capacitor Voltage, Poten | 4KV | AC |  |  | 6/14/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 6/14/1998 | Potentially Challenging | Final | Not Challenging | [5 empty] | 6/14/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/14/1998 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1198 | 20370 | 7/1/1998 | Undetermined (NC‐PC) | No |  | Circulating Water Pump house/Intake Structure |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 7/1/1998 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/1/1998 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 7/1/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/1/1998 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1199 | 20371 | 9/9/1998 | Undetermined (NC‐PC) | No |  | Radwaste Building | Offgas System (BWR) | [6 empty] | 9/9/1998 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Unknown | [6 empty] | No | [8 empty] | 9/9/1998 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 9/9/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown | [7 empty] | 9/9/1998 | Undetermined (NC‐PC) | Unknown | Unknown |  |  |  |  | Not Challenging
1200 | 20372 | 11/23/1998 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  |  |  | 480V | AC |  |  | 11/23/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/23/1998 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 11/23/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/23/1998 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
1201 | 20373 | 3/16/1999 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 3/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 3/16/1999 | Potentially Challenging | Final | Not Challenging | [5 empty] | 3/16/1999 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/16/1999 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1202 | 20374 | 3/19/1999 | Potentially Challenging | No |  | Turbine Building | General Ventillation Systems | Electric Motor | Fans | 600V |  |  |  | 3/19/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/19/1999 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/19/1999 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/19/1999 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1203 | 20375 | 3/29/1999 | Not Challenging | No |  | Turbine Building | [7 empty] | 3/29/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/29/1999 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/29/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 3/29/1999 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1204 | 20376 | 7/29/1999 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 7/29/1999 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 7/29/1999 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 7/29/1999 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 7/29/1999 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1205 | 20377 | 2/8/2000 | Challenging | No |  | Other (Specify in comments) | [7 empty] | 2/8/2000 | Challenging | Personnel error: Misuse of heating devices | In_Situ | Structural component |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 2/8/2000 | Challenging | Preliminary | Challenging | [5 empty] | 2/8/2000 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water | [6 empty] | 2/8/2000 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1206 | 20378 | 2/25/2000 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 2/25/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 2/25/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 2/25/2000 | Potentially Challenging | 23:33:00 | 23:33:00 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify] | [6 empty] | 2/25/2000 | Potentially Challenging | Operate | Operate | 59 | 40 | Reduced Power |  | Challenging
1207 | 20379 | 6/20/2000 | Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Transformers | Dry transformer | 4KV | AC |  |  | 6/20/2000 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 6/20/2000 | Challenging | Preliminary | Challenging | [5 empty] | 6/20/2000 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon | [6 empty] | 6/20/2000 | Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Challenging
1208 | 20380 | 8/16/2000 | Potentially Challenging | No |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 8/16/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/16/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/16/2000 | Potentially Challenging | 15:48:00 | 15:48:00 | Known | 21 | 21 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 8/16/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | Entered an LCO | Alert | Challenging
1209 | 20381 | 10/17/2000 | Undetermined (NC‐PC) | No |  | Reactor Building (BWR) | [7 empty] | 10/17/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/17/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Other [specify] | [6 empty] | 10/17/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1210 | 20382 | 10/23/2000 | Potentially Challenging | No |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Switchgear |  |  |  |  | 10/23/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/23/2000 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/23/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/23/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1211 | 20383 | 11/5/2000 | Undetermined (NC‐PC) | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 110V | AC |  |  | 11/5/2000 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 11/5/2000 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 11/5/2000 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/5/2000 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1212 | 20384 | [57 empty] | 12/27/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None
1213 | 20385 | 12/27/2000 | Undetermined (PC‐CH) | No |  | Turbine Building | Main Turbine System | Pumps | Electric motor driven pumps |  |  |  |  | 12/27/2000 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/27/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 12/27/2000 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 12/27/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
1214 | 30265 | 8/5/2008 | Not Challenging | No |  | Service Water Pump house |  | Pumps | Diesel driven pumps |  |  |  |  | 8/5/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/5/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/5/2008 | Not Challenging | 02:26:00 | 02:26:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/5/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1215 | 30266 | 1/20/2009 | Potentially Challenging | No |  | Turbine Building |  | Electric Motor | Fans |  |  |  |  | 1/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/20/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/20/2009 | Potentially Challenging | 19:26:00 | 19:26:00 | Known | 5 | 5 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 1/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1216 | 30267
1217 | 30268 | 8/9/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/9/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/9/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 8/9/2000 | Not Challenging | 12:36:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 8/9/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1218 | 30269 | 8/14/2002 | Not Challenging | No |  | Reactor Building (BWR) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Fire not observed and fire type indeterminate from post‐inspection | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/14/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/14/2002 | Not Challenging | 15:41:00 |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 8/14/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1219 | 30270 | 3/16/2003 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/16/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/16/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/16/2003 | Potentially Challenging | 11:35:00 | 11:35:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/16/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1220 | 30271 | 9/11/2003 | Undetermined (PC‐CH) | No |  | Turbine Building | Feedwater System | Lube Oil | [5 empty] | 9/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/11/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 9/11/2003 | Undetermined (PC‐CH) | 02:46:00 | 02:46:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/11/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
1221 | 30272 | [12 empty] | 7/9/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 7/9/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/9/2004 | Not Challenging | 08:30:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Other: Water | [6 empty] | 7/9/2004 | Not Challenging | Operate | Operate | 100 | 100
1222 | 30273
1223 | 30274 | 7/9/2004 | Not Challenging | Yes |  | Other (Specify in comments) | [60 empty] | Not Challenging
1224 | 30275 | 1/13/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | [5 empty] | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/13/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/13/2006 | Not Challenging | 08:56:00 |  | Unknown |  |  | Unknown | Unknown | Power Supply Removed | [7 empty] | 1/13/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1225 | 30276 | 7/24/2006 | Potentially Challenging | No | Main Control Room | Control building |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 7/24/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/24/2006 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/24/2006 | Potentially Challenging | 19:10:00 | 19:10:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | [7 empty] | 7/24/2006 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1226 | 30277 | 12/3/2007 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 12/3/2007 | Potentially Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/3/2007 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/3/2007 | Potentially Challenging | 16:59:00 | 16:59:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/3/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1227 | 30278 | 10/15/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/15/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical,Other: Other [specify] | [6 empty] | 10/15/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1228 | 30279 | 5/12/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/12/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 5/12/2002 | Not Challenging | 11:30:00 |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1229 | 30280
1230 | 30281 | 6/5/2008 | Potentially Challenging | No | Main Control Room | Control building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | Other (specify) | AC |  |  | 6/5/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/5/2008 | Potentially Challenging | Final | Challenging | [5 empty] | 6/5/2008 | Potentially Challenging | 13:13:00 |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 6/5/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1231 | 30282 | 11/26/2001 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 11/26/2001 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 11/26/2001 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/26/2001 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 11/26/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1232 | 30283 | 3/20/2002 | Potentially Challenging | No |  | Diesel Generator Building |  | Generator | Class 1A emergency generator |  |  |  |  | 3/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/20/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/20/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/20/2002 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1233 | 30284 | 3/12/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 3/12/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 3/12/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/12/2004 | Not Challenging |  |  | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | [7 empty] | 3/12/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1234 | 30285 | 11/2/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/2/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/2/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1235 | 30286 | 6/18/2009 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 6/18/2009 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 6/18/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 6/18/2009 | Potentially Challenging | 16:18:00 |  | Estimated | 2 | 2 | Fire Watch |  | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 6/18/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1236 | 30287 | 10/1/2009 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/1/2009 | Potentially Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 10/1/2009 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 10/1/2009 | Potentially Challenging |  |  | Known | 9 | 9 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 10/1/2009 | Potentially Challenging | Refueling | Refueling | 0 |  |  |  | Challenging
1237 | 30288 | 4/14/2000 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 4/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/14/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/14/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 4/14/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1238 | 30289 | 7/8/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 7/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No | [8 empty] | 7/8/2000 | Not Challenging | Final | Challenging | [5 empty] | 7/8/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 7/8/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1239 | 30290 | 1/20/2001 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 1/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/20/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 1/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Portable: CO2 | [6 empty] | 1/20/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1240 | 30291 | 3/14/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | [5 empty] | 3/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/14/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical | [6 empty] | 3/14/2001 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1241 | 30292 | 6/17/2001 | Not Challenging | Yes |  |  |  | Cable/Wiring | [5 empty] | 6/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/17/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 6/17/2001 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1242 | 30293 | 8/20/2001 | Not Challenging | No |  |  |  | Electrical panel | [5 empty] | 8/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/20/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/20/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1243 | 30294 | 11/7/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 11/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/7/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/7/2001 | Not Challenging | 10:30:00 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 11/7/2001 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1244 | 30295 | 3/15/2002 | Not Challenging | No |  |  |  | Other | [5 empty] | 3/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/15/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/15/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/15/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1245 | 30296 | 11/22/2002 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring | [5 empty] | 11/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 11/22/2002 | Potentially Challenging | Final | Challenging | [5 empty] | 11/22/2002 | Potentially Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/22/2002 | Potentially Challenging | Refueling | Refueling |  |  |  |  | Challenging
1246 | 30297 | 8/7/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/7/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/7/2003 | Not Challenging | Cold Shutdown | Cold Shutdown |  |  |  |  | Not Challenging
1247 | 30298 | 4/13/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/13/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water | [6 empty] | 4/13/2006 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1248 | 30299 | 4/25/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Pumps | [5 empty] | 4/25/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 4/25/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1249 | 30300 | 5/13/2006 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 5/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/13/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 5/13/2006 | Not Challenging | 13:13:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 5/13/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1250 | 30301 | 6/7/2006 | Not Challenging | Yes |  |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 6/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/7/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/7/2006 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1251 | 30302 | 1/26/2007 | Potentially Challenging | No |  | Turbine Building |  | Electric Motor | Other (specify in comments) |  |  |  |  | 1/26/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/26/2007 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 1/26/2007 | Potentially Challenging | Operate | Operate |  |  | None |  | Challenging
1252 | 30303 | 6/8/2007 | Not Challenging | No | Cable Spreading Room | Control building | Instrument and Uninterruptible Power System, Class 1E | Electrical panel | Inverter | 110V | AC |  |  | 6/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/8/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 6/8/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1253 | 30304 | 11/29/2007 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 11/29/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/29/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/29/2007 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1254 | 30305 | 12/14/2007 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Cable/Wiring | [5 empty] | 12/14/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ |  |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/14/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 12/14/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1255 | 30306 | 1/17/2009 | Not Challenging | No |  |  |  | Other | [5 empty] | 1/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/17/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 1/17/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1256 | 30307 | 3/27/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 3/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/27/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 3/27/2000 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1257 | 30308 | 4/3/2001 | Not Challenging | No | [9 empty] | 4/3/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 4/3/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1258 | 30309 | 7/21/2001 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | [7 empty] | 7/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/21/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 7/21/2001 | Not Challengin | Operate | Operate |  |  |  |  | Not Challenging
1259 | 30310 | 9/7/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Pumps | [5 empty] | 9/7/2001 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/7/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/7/2001 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1260 | 30311 | 9/24/2001 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 9/24/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/24/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 9/24/2001 | Not Challenging | Operate | Operate | 10 | 100 |  |  | Not Challenging
1261 | 30312 | 3/29/2003 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 7KV | AC |  |  | 3/29/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/29/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/29/2003 | Potentially Challenging | Hot Standby | Hot Standby | 0 | 0 | None |  | Challenging
1262 | 30313 | 11/5/2007 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 11/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/5/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 11/5/2007 | Not Challenging | Operate | Operate | 100 | 100 | Scram |  | Not Challenging
1263 | 30314 | 12/19/2001 | Undetermined (PC‐CH) | No |  | Auxiliary Building (PWR) |  | Cable/Wiring | [5 empty] | 12/19/2001 | Undetermined (PC‐CH | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No | [8 empty] | 12/19/2001 | Undetermined (PC‐CH) | Final | Challenging | [22 empty] | 12/19/2001 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
1264 | 30315
1265 | 30316 | 3/16/2003 | Not Challenging | Yes |  |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 3/16/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/16/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 3/16/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1266 | 30317 | 4/18/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/18/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/18/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1267 | 30318 | 5/16/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Pumps | [5 empty] | 5/16/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Fuel Oil |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 5/16/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 5/16/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1268 | 30319 | 7/18/2005 | Not Challenging | No |  | Turbine Building | [7 empty] | 7/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/18/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 7/18/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1269 | 30320 | 5/8/2008 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/8/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/8/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 5/8/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1270 | 30321 | 11/21/2008 | Not Challenging | No | [9 empty] | 11/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/21/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1271 | 30322 | 10/28/2006 | Potentially Challenging | No |  |  | Lube Oil System | Lube Oil |  | 480V | AC |  |  | 10/28/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/28/2006 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/28/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1272 | 30323 | 12/9/2006 | Not Challenging | No |  |  | General Ventillation Systems | Pumps | Electric motor driven pumps | 480V | AC |  |  | 12/9/2006 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/9/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 12/9/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1273 | 30324 | 1/11/2007 | Potentially Challenging | No |  |  | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 220V | AC |  |  | 1/11/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/11/2007 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 1/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1274 | 30325 | 11/6/2007 | Not Challenging | No |  |  | Essential Service Water System | Other | [5 empty] | 11/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 11/6/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1275 | 30326 | 5/1/2008 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 5/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/1/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 5/1/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1276 | 30327 | 3/6/2009 | Potentially Challenging | No |  |  | Heat Rejection System (Circulating Water) | Pumps |  | 480V | AC |  |  | 3/6/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/6/2009 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/6/2009 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1277 | 30328
1278 | 30329
1279 | 30330 | 4/30/2000 | Potentially Challenging | No |  | Turbine Building | Lube Oil System | Lube Oil |  | 480V | AC |  |  | 4/30/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/30/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/30/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1280 | 30331 | 10/12/2000 | Not Challenging | No |  |  | Turbine Lube Oil System | Lube Oil |  | 481V | AC |  |  | 10/12/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/12/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/12/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1281 | 30332 | 4/6/2003 | Not Challenging | Yes |  | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Other |  | 13 KV or greater | AC |  |  | 4/6/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/6/2003 | Not Challenging | Final | Challenging | [22 empty] | 4/6/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1282 | 30333 | 7/31/2003 | Undetermined (PC‐CH) | No |  |  | Condensate System | Other |  | N/A | N/A |  |  | 7/31/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient_Liquid | Cleaning solvents or paint | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/31/2003 | Undetermined (PC‐CH) | Final | Challenging | [22 empty] | 7/31/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
1283 | 30334 | 9/27/2003 | Not Challenging | No | [5 empty] | 480V | AC |  |  | 9/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/27/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/27/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1284 | 30335 | 1/24/2004 | Not Challenging | No | Main Control Room | Control building | DC Power System, class 1E | Electrical panel | Other instrument/control cabin | 125VDC | DC |  |  | 1/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/24/2004 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/24/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1285 | 30336 | [32 empty] | Not Challenging | Final | Not Challenging
1286 | 30337 | [32 empty] | Not Challenging | Final | Not Challenging
1287 | 30338 | 3/30/2006 | Undetermined (NC‐PC) | No |  |  | Condensate System | Electrical panel | Other instrument/control cabin | 110V | AC |  |  | 3/30/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/30/2006 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 3/30/2006 | Undetermined (NC‐PC) | Operate | Operate |  |  | None |  | Not Challenging
1288 | 30339 | 6/21/2000 | Not Challenging | No | Cable Spreading Room |  |  | Transformers | [5 empty] | 6/21/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/21/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 6/21/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1289 | 30340 | 11/10/2000 | Potentially Challenging | No |  | Turbine Building |  | Air Compressors |  | 24‐48VDC | DC |  |  | 11/10/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/10/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 11/10/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1290 | 30341 | 1/2/2001 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor |  | 220V | AC |  |  | 1/2/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/2/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 1/2/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1291 | 30342 | 2/11/2002 | Undetermined (NC‐PC) | No | Fuel handling area | Auxiliary Building (PWR) |  | Crane |  | 480V | AC |  |  | 2/11/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) |  | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/11/2002 | Undetermined (NC‐PC) | Final | Not Challenging | [22 empty] | /11/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1292 | 30343 | 5/3/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/3/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/3/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 5/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1293 | 30344 | 1/23/2003 | Potentially Challenging | No |  | Turbine Building |  | Air Compressors |  | 480V | AC |  |  | 1/23/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/23/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 1/23/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1294 | 30345 | 8/29/2003 | Not Challenging | No | [9 empty] | 8/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/29/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 8/29/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1295 | 30346 | 10/22/2003 | Not Challenging | No | Cable vault/tunnel area | Turbine Building |  | Other | [5 empty] | 10/22/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/22/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/22/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1296 | 30347 | 3/27/2009 | Not Challenging | No | [9 empty] | 3/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/27/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 3/27/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1297 | 30348 | 11/22/2004 | Not Challenging | No |  | Turbine Building |  | Lube Oil | [5 empty] | 11/22/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/22/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/22/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1298 | 30349
1299 | 30350 | 7/26/2004 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 7/26/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/26/2004 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 7/26/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1300 | 30351 | 5/14/2005 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 5/14/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/14/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 5/14/2005 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1301 | 30352
1302 | 30353
1303 | 30354 | 2/8/2005 | Not Challenging | Yes |  | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel |  | 4KV | AC |  |  | 2/8/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes | [8 empty] | 2/8/2005 | Not Challenging | Final | Challenging | [22 empty] | 2/8/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1304 | 30355 | 2/17/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electrical panel | Inverter | 110V | AC |  |  | 2/17/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/17/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 2/17/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1305 | 30356 | 11/21/2006 | Not Challenging | No |  | Turbine Building | Condensate System | Other | [5 empty] | 11/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (Specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/21/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/21/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1306 | 30357 | 6/20/2007 | Undetermined (NC‐PC) | No |  | Control building |  | Other | [5 empty] | 6/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/20/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 6/20/2007 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1307 | 30358 | 8/2/2007 | Not Challenging | Yes |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 480V | AC |  |  | 8/2/2007 | Not Challenging | Electrical failure resulting in overheating materials |  |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/2/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1308 | 30359 | 1/10/2008 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 1/10/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/10/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 1/10/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1309 | 30360 | 4/21/2008 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 4/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/21/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 4/21/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1310 | 30361 | 4/11/2001 | Potentially Challenging | No |  | Turbine Building |  | Other | Other instrument/control cabin | 110V | AC |  |  | 4/11/2001 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1311 | 30362 | 12/16/2001 | Potentially Challenging | No |  |  | Essential Service Water System | Pumps |  | 4KV | AC |  |  | 12/16/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/16/2001 | Potentially Challenging | Final | Challenging | [22 empty] | 12/16/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1312 | 30363 | 5/5/2003 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Cable/Wiring |  |  | 110V | AC |  |  | 5/5/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/5/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 5/5/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1313 | 30364 | 5/26/2003 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/26/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/26/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 5/26/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1314 | 30365 | 9/8/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 9/8/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/8/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 9/8/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1315 | 30366 | 12/2/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 12/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/2/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 12/2/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1316 | 30367 | 3/30/2004 | Not Challenging | No | [9 empty] | 3/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/30/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 3/30/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1317 | 30368 | 7/6/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 7/6/2004 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Structural component |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/6/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 7/6/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1318 | 30369 | 10/29/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/29/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/29/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1319 | 30370 | 10/31/2005 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/31/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/31/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/31/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1320 | 30371 | 11/8/2005 | Not Challenging | Yes | [5 empty] | N/A | N/A |  |  | 11/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No | [8 empty] | 11/8/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1321 | 30372 | 11/18/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/18/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 11/18/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1322 | 30373 | 11/20/2005 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/20/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1323 | 30374 | 11/30/2005 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 11/30/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/30/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 11/30/2005 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1324 | 30375 | 5/9/2007 | Not Challenging | No |  |  |  | Pumps | [5 empty] | 5/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/9/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 5/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1325 | 30376 | 10/14/2007 | Not Challenging | No | [9 empty] | 10/14/2007 | Not Challenging |  | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/14/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 10/14/2007 | Not Challengin | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1326 | 30377 | 11/3/2007 | Not Challenging | No | [9 empty] | 11/3/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/3/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 11/3/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1327 | 30378 | 11/6/2007 | Not Challenging | No | [9 empty] | 11/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/6/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1328 | 30379 | 11/16/2007 | Not Challenging | No | Containment/Drywell |  |  | Other | [5 empty] | 11/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/16/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 11/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1329 | 30380 | 12/17/2007 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 12/17/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/17/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 12/17/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1330 | 30381 | 4/7/2008 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Other |  | 110V | AC |  |  | 4/7/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/7/2008 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/7/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1331 | 30382 | 5/21/2009 | Not Challenging | No | [9 empty] | 5/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/21/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 5/21/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1332 | 30383 | 2/11/2009 | Not Challenging | Yes | [9 empty] | 2/11/2009 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/11/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 2/11/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1333 | 30384 | 10/18/2000 | Not Challenging | No | [9 empty] | 10/18/2000 | Not Challenging |  | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/18/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 10/18/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1334 | 30385 | 10/27/2000 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 10/27/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/27/2000 | Potentially Challenging | Preliminary | Undetermined (NC‐PC) | [22 empty] | 10/27/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1335 | 30386 | 5/11/2001 | Potentially Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 5/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/11/2001 | Potentially Challenging | Preliminary | Potentially Challenging | [22 empty] | 5/11/2001 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1336 | 30387 | 5/24/2001 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 5/24/2001 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 5/24/2001 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 5/24/2001 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1337 | 30388 | 4/6/2002 | Potentially Challenging | No | [9 empty] | 4/6/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/6/2002 | Potentially Challenging | Preliminary | Potentially Challenging | [22 empty] | 4/6/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1338 | 30389 | 10/18/2005 | Not Challenging | No | [9 empty] | 10/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (Specify) | Contained within component | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/18/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/18/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1339 | 30390 | 5/7/2008 | Potentially Challenging | No |  | Containment (PWR) | [7 empty] | 5/7/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/7/2008 | Potentially Challenging | Preliminary | Potentially Challenging | [22 empty] | 5/7/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1340 | 30391 | 11/13/2009 | Not Challenging | No | [9 empty] | 11/13/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/13/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 11/13/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1341 | 30392 | 3/20/2000 | Undetermined (NC‐PC) | No | Containment/Drywell | Other (Specify in comments) |  | Other | [5 empty] | 3/20/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/20/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 3/20/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1342 | 30393 | 3/24/2000 | Undetermined (NC‐PC) | No | Containment/Drywell | Other (Specify in comments) |  | Cable/Wiring |  | 110V |  |  |  | 3/24/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/24/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | : 3/24/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1343 | 30394 | 2/2/2003 | Potentially Challenging | No |  | Reactor Building (BWR) | General Ventillation Systems | Electric Motor | [5 empty] | 2/2/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/2/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 2/2/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1344 | 30395 | 3/21/2004 | Undetermined (PC‐CH) | No |  | Turbine Building | [7 empty] | 3/21/2004 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) |  | Other (Specify) |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 3/21/2004 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 3/21/2004 | Undetermined (PC‐CH) | Refueling | Refueling | 0 | 0 |  |  | Challenging
1345 | 30396 | 3/22/2009 | Not Challenging | No |  | Turbine Building | Lube Oil System | Lube Oil | [5 empty] | 3/22/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/22/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 3/22/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1346 | 30397 | 4/4/2009 | Not Challenging | No |  | Turbine Building |  |  |  | N/A |  |  |  | 4/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/4/2009 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/4/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1347 | 30398 | 10/17/2006 | Not Challenging | No |  | Turbine Building | Feedwater System | Cable/Wiring | [5 empty] | 10/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/17/2006 | Not Challenging | Final | Not Challenging | [22 empty] | 10/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1348 | 30399
1349 | 30400 | 9/18/2007 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 9/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/18/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/18/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1350 | 30401 | 2/6/2008 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 2/6/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/6/2008 | Not Challenging | Final | Potentially Challenging | [22 empty] | 2/6/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1351 | 30402 | 4/29/2008 | Not Challenging | No |  | Turbine Building | Condensate System | Cable/Wiring |  | 480V | AC |  |  | 4/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/29/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 4/29/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1352 | 30403 | 9/24/2009 | Not Challenging | No |  | Turbine Building | Condensate System | Other |  | N/A | N/A |  |  | 9/24/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/24/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 9/24/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1353 | 30404 | 4/21/2009 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Hydrogen Supply System | Other | [5 empty] | 4/21/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 4/21/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 4/21/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1354 | 30405 | 10/26/2009 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Electric Motor | Other (specify in comments) |  |  |  |  | 10/26/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Unknown |  |  | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 10/26/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 10/26/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1355 | 30406
1356 | 30407 | 4/30/2002 | Potentially Challenging | No |  | Containment (PWR) |  | Cable/Wiring | [5 empty] | 4/30/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/30/2002 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/30/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1357 | 30408 | 3/19/2001 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/19/2001 | Potentially Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/19/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/19/2001 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1358 | 30409 | 8/21/2000 | Potentially Challenging | No |  | Main Transformer or Switch Yard |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 8/21/2000 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/21/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 8/21/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1359 | 30410 | 10/25/2000 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps |  |  |  |  | 10/25/2000 | Potentially Challenging | Unknown | In_Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/25/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/25/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1360 | 30411 | 3/28/2000 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/28/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/28/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1361 | 30412 | 4/25/2002 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring | [5 empty] | 4/25/2002 | Potentially Challenging | Personnel error: Misuse of material ignited | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2002 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/25/2002 | Potentially Challenging | Refueling | Cold Shutdown | 0 | 0 |  |  | Challenging
1362 | 30413 | 4/25/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/25/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 4/25/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1363 | 30414 | 3/28/2002 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 3/28/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/28/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/28/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1364 | 30415 | 4/29/2002 | Not Challenging | No | Containment/Drywell | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 4/29/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/29/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/29/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1365 | 30416 | 4/29/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 4/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/29/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 4/29/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1366 | 30417 | 3/20/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 3/20/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/20/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 3/20/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1367 | 30418 | 2/19/2002 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Batteries | [5 empty] | 3/18/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/19/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 2/19/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1368 | 30419 | 10/4/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/4/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/4/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/4/2001 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1369 | 30420 | 3/18/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) | [7 empty] | 3/18/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/18/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/18/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1370 | 30421 | 3/5/2002 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 3/5/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin | No | [8 empty] | 3/5/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 3/5/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1371 | 30422 | 11/27/2001 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps |  |  |  |  | 11/27/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/27/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 11/27/2001 | Potentially Challenging | Operate | Operate | 0 | 0 |  |  | Challenging
1372 | 30423 | 3/17/2001 | Not Challenging | No |  | Turbine Building |  | Pumps | [5 empty] | 3/17/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/17/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 3/17/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1373 | 30424 | 4/11/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC |  |  | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/11/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1374 | 30425 | 10/7/2002 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 10/7/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/7/2002 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/7/2002 | Potentially Challenging | Operate | Operate | 0 | 0 |  |  | Challenging
1375 | 30426 | 10/31/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 10/31/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/31/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1376 | 30427
1377 | 30428
1378 | 30429 | 5/6/2004 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Pumps | Electric motor driven pumps |  |  |  |  | 5/6/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/6/2004 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 5/6/2004 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1379 | 30430 | 1/13/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/13/2006 | Not Challenging | Final | Challenging | [22 empty] | 1/13/2006 | Not Challenging | Operate |  | 100 | 100 |  |  | Not Challenging
1380 | 30431 | 6/18/2006 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 6/18/2006 | Not Challenging | Unknown | Unknown |  |  | No Fire ‐ False actuation of detection device | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No | [8 empty] | 6/18/2006 | Not Challenging | Final | Not Challenging | [22 empty] | 6/18/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1381 | 30432
1382 | 30433 | 6/2/2007 | Not Challenging | No |  |  |  |  | Other |  |  |  |  | 6/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/2/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/2/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1383 | 30434 | 8/12/2007 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 8/12/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/12/2007 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 8/12/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1384 | 30435 | 8/16/2007 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Other | [5 empty] | 8/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/16/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/16/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1385 | 30436 | 9/30/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 9/30/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/30/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 9/30/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1386 | 30437 | 10/6/2000 | Potentially Challenging | No | Containment/Drywell |  |  | Transformers | [5 empty] | 10/6/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/6/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/6/2000 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Challenging
1387 | 30438 | 5/15/2007 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other | [5 empty] | 5/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/15/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 5/15/2007 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1388 | 30439 | 3/21/2008 | Undetermined (NC‐PC) | No |  | Auxiliary Building (PWR) | Auxiliary/Emergency Feedwater System (PWR) | Pumps |  | N/A | N/A |  |  | 3/21/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/21/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 3/21/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 |  |  |  | Not Challenging
1389 | 30440 | 10/26/2005 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | Emergency Onsite Power Supply System | Other | [5 empty] | 10/26/2005 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/26/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 10/26/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1390 | 30441 | 9/5/2001 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps |  | N/A | N/A |  |  | 9/5/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/5/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/5/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1391 | 30442 | 9/5/2001 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 9/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/5/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/5/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1392 | 30443 | 12/31/2001 | Not Challenging | No | [9 empty] | 12/31/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/31/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 12/31/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1393 | 30444 | 3/13/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 3/13/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/13/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 3/13/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1394 | 30445 | 10/18/2002 | Not Challenging | No |  |  |  | Transformers | [5 empty] | 10/18/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/18/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 10/18/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1395 | 30446 | 4/1/2003 | Potentially Challenging | No |  |  |  | Electrical panel | Relay rack |  |  |  |  | 4/1/2003 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Unknown | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/1/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/1/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1396 | 30447 | 7/11/2004 | Potentially Challenging | No | [9 empty] | 7/11/2004 | Potentially Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/11/2004 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 7/11/2004 | Potentially Challenging | Operate | Operate | 0 | 0 | None |  | Challenging
1397 | 30448
1398 | 30449 | 10/8/2005 | Not Challenging | No |  |  |  | Pumps | [5 empty] | 10/8/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 10/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1399 | 30450
1400 | 30451
1401 | 30452 | 8/8/2008 | Not Challenging | No | [9 empty] | 8/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/8/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 8/8/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1402 | 30453 | 1/30/2009 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | [6 empty] | 1/30/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Contained within component | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/30/2009 | Potentially Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 1/30/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1403 | 30454 | 6/22/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 6/22/2009 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 6/22/2009 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/22/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1404 | 30455 | 3/14/2000 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 3/14/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/14/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/14/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1405 | 30456 | 3/7/2001 | Potentially Challenging | No |  |  |  | Crane | [5 empty] | 3/7/2001 | Potentially Challenging |  | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/7/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/7/2001 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1406 | 30457 | 10/24/2006 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 10/24/2006 | Undetermined (NC‐PC) |  | Transient_Gas | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/24/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 10/24/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1407 | 30458 | 1/18/2003 | Not Challenging | No |  | Turbine Building | Main Turbine System | Other | [5 empty] | 1/18/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/18/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/18/2003 | Not Challenging | Operate | Operate |  |  |  |  | Not Challenging
1408 | 30459 | 3/9/2003 | Potentially Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 3/9/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/9/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/9/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1409 | 30460 | 3/18/2003 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/18/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/18/2003 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/18/2003 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1410 | 30461 | 3/23/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 3/23/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 3/23/2004 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/23/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1411 | 30462 | 5/24/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 5/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 5/24/2004 | Not Challenging | Final | Potentially Challenging | [22 empty] | : 5/24/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1412 | 30463 | 10/28/2009 | Not Challenging | No |  |  |  | Pumps | [5 empty] | 10/28/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/28/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 10/28/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1413 | 30464 | 9/23/2008 | Not Challenging | No |  | Turbine Building | Condensate System | Pumps |  | 110V | AC |  |  | 9/23/2008 | Not Challenging | Unknown | In_Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/23/2008 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1414 | 30465 | 9/24/2008 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 9/24/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/24/2008 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 9/24/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1415 | 30466
1416 | 30467
1417 | 30468
1418 | 30469 | 11/11/2007 | Potentially Challenging | No |  | Other (Specify in comments) |  | Transformers | [5 empty] | 11/11/2007 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/11/2007 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 11/11/2007 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1419 | 30470 |  |  | No
1420 | 30471 | 4/4/2008 | Potentially Challenging | No |  | Diesel Generator Building |  | Generator | Class 1A emergency generator | 4KV | AC |  |  | 4/4/2008 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/4/2008 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/4/2008 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1421 | 30472 | 9/29/2006 | Not Challenging | No |  | Reactor Building (BWR) |  | Cable/Wiring | [5 empty] | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/29/2006 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 9/29/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1422 | 30473 | 9/20/2001 | Not Challenging | No | [9 empty] | 9/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/20/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/20/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1423 | 30474 | 8/12/2002 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No | [8 empty] | 8/12/2002 | Not Challenging | Final | Challenging | [22 empty] | 8/12/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1424 | 30475 | 4/26/2003 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 4/26/2003 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/26/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/26/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1425 | 30476 | 10/12/2003 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 10/12/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 10/12/2003 | Not Challenging | Final | Challenging | [22 empty] | 10/12/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1426 | 30477
1427 | 30478 | 9/9/2005 | Potentially Challenging | No |  | Turbine Building |  | Electrical panel | Relay rack |  |  |  |  | 9/9/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 9/9/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/9/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1428 | 30479 | 9/24/2005 | Not Challenging | No | [9 empty] | 9/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/24/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 9/24/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1429 | 30480 | 9/25/2005 | Not Challenging | No | [9 empty] | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/25/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 9/25/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1430 | 30481 | 9/25/2005 | Not Challenging | No |  | Turbine Building | [7 empty] | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/25/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/25/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1431 | 30482 | 10/5/2005 | Not Challenging | No | [9 empty] | 10/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No | [8 empty] | 10/5/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 10/5/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1432 | 30483 | 10/9/2005 | Not Challenging | No |  | Turbine Building | [7 empty] | 10/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No | [8 empty] | 10/9/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/9/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1433 | 30484
1434 | 30485 | 9/17/2006 | Not Challenging | No |  | Turbine Building | [7 empty] | 9/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/17/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 9/17/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1435 | 30486
1436 | 30487 | 12/4/2006 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 12/4/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Other (Specify) | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/4/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 12/4/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1437 | 30488 | [57 empty] | 10/5/2007 | Not Challenging | Refueling | Refueling | 0 | 0
1438 | 30489 | 10/5/2007 | Not Challenging | No |  | Turbine Building | Condensate System | Other |  | N/A | N/A |  |  | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/5/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 6/21/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1439 | 30490
1440 | 30491
1441 | 30492
1442 | 30493 | 7/24/2008 | Challenging | No |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 7/24/2008 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No | [8 empty] | 7/24/2008 | Challenging | Final | Challenging | [22 empty] | 7/24/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1443 | 30494
1444 | 30495
1445 | 30496
1446 | 30497
1447 | 30498 | 6/21/2009 | Not Challenging | No |  | Turbine Building | General Ventillation Systems | Other | [5 empty] | 6/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 6/21/2009 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/21/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1448 | 30499
1449 | 30500 | 5/29/2002 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Other | [5 empty] | 5/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/29/2002 | Not Challenging | Preliminary | Potentially Challenging | [22 empty] | 5/29/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1450 | 30501
1451 | 30502 | 10/8/2003 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 10/8/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/8/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/8/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1452 | 30503 | 3/8/2002 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or Grease | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/8/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 3/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1453 | 30504 | 3/17/2002 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Crane | Other instrument/control cabin | 110V | AC |  |  | 3/17/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/17/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/17/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1454 | 30505 | 3/11/2003 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 3/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 3/11/2003 | Not Challenging | Final | Challenging | [22 empty] | 3/11/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1455 | 30506 | 12/17/2003 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Electric Motor |  | 110V | AC |  |  | 12/17/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/17/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 12/17/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1456 | 30507 | 7/26/2005 | Potentially Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 7/26/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/26/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 7/26/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1457 | 30508 | 3/26/2009 | Potentially Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 3/26/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/26/2009 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/26/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1458 | 30509 | 8/11/2009 | Not Challenging | No |  | Control building | [7 empty] | 8/11/2009 | Not Challenging | False actuation of detector, no ignition or overheat condition |  |  |  | No Fire ‐ False actuation of detection device |  |  | : No damage | No | [8 empty] | 8/11/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 8/11/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1459 | 30510 | 1/17/2008 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 1/17/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/17/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 1/17/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1460 | 30511 | 1/23/2008 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 1/23/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/23/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 1/23/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1461 | 30512 | 2/15/2006 | Potentially Challenging | No |  | Turbine Building |  | Other |  | 480V | AC |  |  | 2/15/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/15/2006 | Potentially Challenging | Final with disagreement | Potentially Challenging | [22 empty] | 2/15/2006 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1462 | 30513 | 5/27/2008 | Potentially Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Transformers | Other (Capacitor Voltage, Poten | 110V | AC |  |  | 5/27/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/27/2008 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 5/27/2008 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1463 | 30514 | 3/7/2003 | Not Challenging | No | [9 empty] | 3/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/7/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 3/7/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1464 | 30515 | [57 empty] | 6/25/2005 | Not Challenging | Operate | Operate | 100 | 100
1465 | 30516 | 6/25/2005 | Not Challenging | Yes |  | Main Transformer or Switch Yard | Switchyard System | Other |  | 13 KV or greater | AC |  |  | 6/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/25/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/25/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1466 | 30517 | 7/29/2005 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 7/29/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No | [8 empty] | 7/29/2005 | Not Challenging | Preliminary | Potentially Challenging | [22 empty] | 7/29/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1467 | 30518
1468 | 30519 | 1/5/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 1/5/2009 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No | [8 empty] | 1/5/2009 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/5/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1469 | 30520 | 3/1/2000 | Not Challenging | No |  | Turbine Building |  | Electrical panel | [5 empty] | 3/1/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/1/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/1/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1470 | 30521 | 9/11/2000 | Not Challenging | No |  | Turbine Building | [7 empty] | 9/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/11/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 9/11/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1471 | 30522 | 9/12/2000 | Potentially Challenging | No |  | Auxiliary Building (PWR) | Closed/Component Cooling Water | Electrical panel | Other instrument/control cabin |  |  |  |  | 9/12/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/12/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 9/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1472 | 30523 | 9/14/2000 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 9/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/14/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 9/14/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1473 | 30524 | 12/14/2000 | Undetermined (NC‐PC) | No |  |  |  | Pumps | [5 empty] | 12/14/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 12/14/2000 | Undetermined (NC‐PC) | Final | Not Challenging | [22 empty] | 12/14/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1474 | 30525 | 3/7/2001 | Not Challenging | Yes |  |  |  | Cable/Wiring | [5 empty] | 3/7/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/7/2001 | Not Challenging | Final | Challenging | [22 empty] | 3/7/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1475 | 30526 | 6/12/2001 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 6/12/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/12/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 6/12/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1476 | 30527 | 2/1/2002 | Not Challenging | No |  |  |  | Other | [5 empty] | 2/1/2002 | Not Challenging | Unknown | In_Situ | Structural component |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/1/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 2/1/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1477 | 30528 | 2/24/2002 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 2/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/24/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 2/24/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1478 | 30529 | 3/8/2002 | Not Challenging | No |  | Containment (PWR) | [7 empty] | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/8/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 3/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1479 | 30530 | 3/23/2002 | Not Challenging | Yes |  |  |  | Pumps | [5 empty] | 3/23/2002 | Not Challenging | Unknown | In_Situ | Structural component |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/23/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 3/23/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1480 | 30531 | 4/17/2002 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 4/17/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/17/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 4/17/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1481 | 30532 | 6/14/2002 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 6/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 6/14/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/12/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1482 | 30533 | 2/10/2003 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 2/10/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/10/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 2/10/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1483 | 30534 | 3/4/2004 | Not Challenging | No |  | Turbine Building | [7 empty] | 3/4/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Fire not observed and fire type indeterminate from post‐inspection | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/4/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 3/4/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1484 | 30535 | 4/16/2004 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/16/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 4/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1485 | 30536 | 9/13/2004 | Not Challenging | No | [9 empty] | 9/13/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) |  |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/13/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 9/13/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1486 | 30537 | 6/15/2005 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 6/15/2005 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/15/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/15/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1487 | 30538 | 1/23/2005 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | [5 empty] | 1/23/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 1/23/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/23/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1488 | 30539 | 2/3/2005 | Not Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) | Cable/Wiring | [5 empty] | 2/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component |  |  | Confined to the object of origin | No | [8 empty] | 2/3/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 2/3/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1489 | 30540 | 5/2/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 5/2/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/2/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 5/2/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1490 | 30541 | 7/6/2005 | Potentially Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Fans |  |  |  |  | 7/6/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/6/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 7/6/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1491 | 30542 | 7/28/2005 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 7/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/28/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 7/28/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1492 | 30543 | 8/24/2005 | Not Challenging | Yes | [9 empty] | 8/24/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 8/24/2005 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/24/2005 | Not Challenging | Operate | Operate | 100 | 10 |  |  | Not Challenging
1493 | 30544 | 10/4/2005 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/4/2005 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/4/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1494 | 30545 | 1/16/2006 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 1/16/2006 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 1/16/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/16/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1495 | 30546 | 4/26/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 4/26/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 4/26/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/26/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1496 | 30547 | 4/19/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 4/19/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 4/19/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/19/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1497 | 30548 | 7/24/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 7/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 7/24/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 7/24/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1498 | 30549 | 9/5/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Batteries | [5 empty] | 9/5/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component |  |  | Confined to the object of origin | No | [8 empty] | 9/5/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/5/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1499 | 30550 | 10/5/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 10/5/2006 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/5/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/5/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1500 | 30551 | 10/20/2006 | Not Challenging | No |  | Turbine Building |  | Pumps | [5 empty] | 10/20/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/20/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/20/2006 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1501 | 30552 | 5/8/2007 | Not Challenging | No | [9 empty] | 5/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/8/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 5/8/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1502 | 30553 | 8/28/2007 | Not Challenging | No | [9 empty] | 8/28/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/28/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 8/28/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1503 | 30554 | 10/17/2007 | Not Challenging | No |  |  |  | Pumps | [5 empty] | 10/17/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/17/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 10/17/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1504 | 30555 | 4/1/2008 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 4/1/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/1/2008 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/1/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1505 | 30556 | 4/4/2008 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 4/4/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/4/2008 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 4/4/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1506 | 30557 | 4/30/2008 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/30/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/30/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 4/30/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1507 | 30558 | 10/20/2008 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) | General Ventillation Systems | Other |  | 24‐48VDC | DC |  |  | 10/20/2008 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Unknown | No | [8 empty] | 10/20/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 10/20/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1508 | 30559 | 11/21/2008 | Not Challenging | No |  |  |  | Electric Motor | [5 empty] | 11/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/21/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 11/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1509 | 30560 | 2/4/2009 | Not Challenging | No | [9 empty] | 2/4/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/4/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 2/4/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1510 | 30561 | 4/3/2008 | Not Challenging | No |  | Containment (PWR) | [7 empty] | 4/3/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2008 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/3/2008 | Not Challenging | Refueling | Refueling | 100 | 100 |  |  | Not Challenging
1511 | 30562 | 3/17/2008 | Not Challenging | No | [9 empty] | 3/17/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/17/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 3/17/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1512 | 30563 | 3/9/2008 | Not Challenging | No | [9 empty] | 3/9/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/9/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 3/9/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1513 | 30564 | 11/18/2003 | Not Challenging | No |  | Radwaste Building |  | Other | [5 empty] | 11/18/2003 | Not Challenging | Unknown | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 11/18/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 11/18/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1514 | 30565 | 2/11/2000 | Not Challenging | No | [9 empty] | 2/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | No damage | No | [8 empty] | 2/11/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 2/11/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1515 | 30566 | 9/11/2000 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 9/11/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 9/11/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 9/11/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1516 | 30567 | 10/17/2000 | Not Challenging | No | [9 empty] | 10/17/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/17/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 10/17/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1517 | 30568 | 1/19/2002 | Not Challenging | No | [9 empty] | 1/19/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/19/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 1/19/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1518 | 30569 | 10/16/2006 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Other |  | N/A |  |  |  | 10/16/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 10/16/2006 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/16/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1519 | 30570 | 3/28/2001 | Not Challenging | No | [9 empty] | 3/28/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No | [8 empty] | 3/28/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 3/28/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1520 | 30571 | 1/12/2001 | Not Challenging | No |  |  |  | Other | [5 empty] | 1/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No | [8 empty] | 1/12/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 1/12/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1521 | 30572 | 5/12/2002 | Not Challenging | Yes |  |  |  | Other |  | N/A | N/A |  |  | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/12/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 5/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1522 | 30573 | 6/6/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/6/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 6/6/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1523 | 30574 | 11/2/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | 480V | AC |  |  | 11/2/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 11/2/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 11/2/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1524 | 30575
1525 | 30576 | 8/15/2006 | Not Challenging | Yes |  |  |  | Other | [5 empty] | 8/15/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No | [8 empty] | 8/15/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/15/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1526 | 30577 | 3/3/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 3/3/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/3/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/3/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1527 | 30578 | 2/27/2003 | Undetermined (PC‐CH) | No | Fuel handling area | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 480V | AC |  |  | 2/27/2003 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/27/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 2/27/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1528 | 30579 | 6/6/2007 | Not Challenging | Yes | [9 empty] | 6/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 6/6/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 6/6/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1529 | 30580 | 6/21/2000 | Not Challenging | Yes | [9 empty] | 6/21/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 6/21/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/21/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1530 | 30581 | 6/19/2007 | Not Challenging | No | [9 empty] | 6/19/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/19/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 6/19/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1531 | 30582 | 6/7/2000 | Not Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) |  |  | 110V | AC |  |  | 6/7/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No | [8 empty] | 6/7/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 6/7/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1532 | 30583 | 6/30/2003 | Not Challenging | Yes |  | Containment (PWR) | [7 empty] | 6/30/2003 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 6/30/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 6/30/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1533 | 30584 | 5/24/2001 | Not Challenging | No |  | Other (Specify in comments) | Low Voltage Power System (600V and less) |  |  | 110V | AC |  |  | 5/24/2001 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/24/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 5/24/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1534 | 30585 | 5/3/2001 | Not Challenging | No | [9 empty] | 5/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/3/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 5/3/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1535 | 30586 | 1/11/2006 |  | No |  | Other (Specify in comments) | Emergency Onsite Power Supply System | Generator |  | 24‐48VDC | DC |  |  | 1/11/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 1/11/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 1/11/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100
1536 | 30587 | 3/4/2009 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Other (specify in comments) | 110V | AC |  |  | 3/4/2009 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No | [8 empty] | 3/4/2009 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 3/4/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1537 | 30588 | 5/14/2009 | Not Challenging | No |  | Turbine Building | [7 empty] | 5/14/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/14/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 5/14/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1538 | 30589 | 10/11/2009 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 10/11/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/11/2009 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/11/2009 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1539 | 30590 | 12/22/2009 | Not Challenging | No | [9 empty] | 12/22/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/22/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 12/22/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1540 | 30591 | 10/17/2005 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 10/17/2005 | Not Challenging | Personnel error: Misuse of heating devices | Unknown |  |  | Other (specify) | Unknown | Unknown | Unknown | No | [8 empty] | 10/17/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/17/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1541 | 30592
1542 | 30593 | 2/7/2008 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 2/7/2008 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/7/2008 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 2/7/200 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
1543 | 30594 | 6/17/2007 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 6/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No | [8 empty] | 6/17/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 6/17/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1544 | 30595 | 10/10/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/10/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/10/2008 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/10/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1545 | 30596 | 10/17/2008 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/17/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/17/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 10/17/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1546 | 30597 | 2/5/2009 | Potentially Challenging | No |  | Turbine Building | Hydrogen Supply System | Other |  | N/A | N/A |  |  | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 2/5/2009 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 2/5/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1547 | 30598 | 11/20/2009 | Potentially Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/20/2009 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 11/20/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1548 | 30599 | 3/23/2001 | Not Challenging | No | [9 empty] | 3/23/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/23/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 3/23/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1549 | 30600 | 11/9/2001 | Not Challenging | No | Main Control Room | Control building | [7 empty] | 11/9/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/9/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 11/9/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1550 | 30601 | 9/14/2001 | Not Challenging | No |  | Radwaste Building |  | Other |  | 10V | AC |  |  | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/14/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 9/14/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1551 | 30602 | 5/19/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Diesel driven pumps |  |  |  |  | 5/19/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/19/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 5/19/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1552 | 30603 | 1/13/2005 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  | N/A |  |  | 1/13/2005 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/13/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 1/13/20 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1553 | 30604 | 5/28/2005 | Potentially Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Pumps | Diesel driven pumps |  |  |  |  | 5/28/2005 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/28/2005 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 5/28/2005 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1554 | 30605 | 9/19/2005 | Not Challenging | No |  | Other (Specify in comments) |  | Junction Boxes | [5 empty] | 9/19/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/19/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 9/19/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1555 | 30606 | 12/19/2007 | Not Challenging | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 12/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/19/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 12/19/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1556 | 30607 | 3/20/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 3/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/20/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 3/20/2001 | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
1557 | 30608 | 1/10/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 1/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 1/10/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 1/10/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1558 | 30609 | 4/17/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/17/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1559 | 30610 | 7/21/2002 | Not Challenging | No |  | Auxiliary Building (PWR) | Closed/Component Cooling Water | Pumps | Electric motor driven pumps |  |  |  |  | 7/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Confined to the object of origin | No | [8 empty] | 7/21/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 7/21/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1560 | 30693 | 2/3/2004 | Potentially Challenging | No |  | Other (Specify in comments) | Emergency Onsite Power Supply System | Generator | Other generator (specify in com |  |  |  |  | 2/3/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 2/3/2004 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 2/3/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1561 | 30694 | 8/10/2004 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 8/10/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No | [8 empty] | 8/10/2004 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/10/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1562 | 30695 | 9/21/2006 | Not Challenging | No |  | Turbine Building |  | Other | [5 empty] | 9/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Jet from a pressurized source | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/21/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/21/2006 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1563 | 30696 | 9/26/2006 | Not Challenging | No | [9 empty] | 9/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/26/2006 | Not Challenging | Final | Not Challenging | [22 empty] | 9/26/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1564 | 30697 | 9/29/2006 | Not Challenging | No |  | Containment (PWR) | [7 empty] | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/29/2006 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/29/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1565 | 30698 | 2/22/2007 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | 2/22/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/22/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 2/22/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1566 | 30699 | 3/7/2007 | Not Challenging | No | [9 empty] | 3/7/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/7/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 3/7/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1567 | 30700 | 4/19/2007 | Not Challenging | No | [9 empty] | 4/19/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/19/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 4/19/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1568 | 30701 | 8/13/2007 | Not Challenging | No | [9 empty] | 8/13/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/13/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 8/13/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1569 | 30702 | 9/11/2007 | Not Challenging | No | [9 empty] | 9/11/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/11/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 9/11/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1570 | 30703 | 10/2/2007 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 10/2/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/2/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/2/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1571 | 30704 | 10/17/2007 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/17/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 10/17/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1572 | 30705 | 9/20/2007 | Not Challenging | No | [9 empty] | 9/20/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/20/2007 | Not Challenging | Final | Not Challenging | [22 empty] | 9/20/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1573 | 30706 | 6/28/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Junction Boxes | [5 empty] | 9/20/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/28/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 6/28/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1574 | 30707 | 10/1/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 10/1/2000 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/1/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 10/1/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1575 | 30708 | 2/6/2001 | Not Challenging | No | [9 empty] | 2/6/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/6/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 2/6/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1576 | 30709 | 7/13/2001 | Not Challenging | No | [9 empty] | 7/13/2001 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/13/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 7/13/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1577 | 30710 | 9/19/2001 | Not Challenging | No | [9 empty] | 9/19/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No | [8 empty] | 9/19/2001 | Not Challenging | Final | Potentially Challenging | [22 empty] | 9/19/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1578 | 30711 | 11/16/2001 | Not Challenging | No | [9 empty] | 11/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Smoldering combustion – internal to component |  |  | Confined to the object of origin | No | [8 empty] | 11/16/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 11/16/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1579 | 30712 | 4/24/2002 | Not Challenging | Yes |  | Circulating Water Pump house/Intake Structure |  | Other | [5 empty] | 4/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 4/24/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/24/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1580 | 30713 | 4/29/2002 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 4/29/2002 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/29/2002 | Not Challenging | Final | Potentially Challenging | [22 empty] | 4/29/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1581 | 30714
1582 | 30715
1583 | 30716 | 9/2/2002 | Not Challenging | No |  |  |  | Cable/Wiring | [5 empty] | 9/2/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/2/2002 | Not Challenging | Final | Not Challenging | [22 empty] | 9/2/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1584 | 30717 | 12/10/2002 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 12/10/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/10/2002 Undetermined (NC‐PC) | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 12/10/2002 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1585 | 30718 | 4/15/2003 | Undetermined (NC‐PC) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Other | [5 empty] | 4/15/2003 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/15/2003 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 4/15/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1586 | 30719 | 6/11/2003 | Undetermined (PC‐CH) | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | [6 empty] | 6/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/11/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 6/11/2003 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Challenging
1587 | 30720 | 7/2/2003 | Not Challenging | No |  |  |  | Other | [5 empty] | 7/2/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient_Liquid | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/2/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 7/2/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1588 | 30721 | 8/27/2003 | Not Challenging | No | [9 empty] | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (Specify) | Other (Specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 8/27/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 8/27/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1589 | 30722 | 10/19/2003 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/19/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | Unknown | Confined to the object of origin | No | [8 empty] | 10/19/2003 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 10/19/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1590 | 30723 | 11/3/2008 | Not Challenging | No |  |  |  | Other | [5 empty] | 11/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/3/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 11/3/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1591 | 30724 | 11/16/2008 | Not Challenging | No | [9 empty] | 11/3/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/16/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 11/16/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1592 | 30725 | 4/12/2000 | Potentially Challenging | No |  |  |  | Electric Motor | Fans |  |  |  |  | 4/12/2000 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 4/12/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/12/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1593 | 30726 | 5/19/2000 | Not Challenging | No |  | Turbine Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 5/19/2000 | Not Challenging |  | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/19/2000 | Not Challenging | Final | Not Challenging | [22 empty] | 5/19/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1594 | 30727 | 10/30/2000 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/30/2000 | Potentially Challenging |  | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 10/30/2000 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 10/30/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1595 | 30728 | 12/21/2000 | Not Challenging | No | Containment/Drywell |  |  | Other |  | N/A | N/A |  |  | 12/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/21/2000 | Not Challenging | Final | Potentially Challenging | [22 empty] | 12/21/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1596 | 30729 | 12/22/2000 | Not Challenging | No | Containment/Drywell |  |  | Other | [5 empty] | 12/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/22/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 12/22/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1597 | 30730 | 3/5/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 3/5/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/5/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 3/5/2001 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1598 | 30731 | 3/19/2001 | Potentially Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 3/19/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component |  |  | No damage | No | [8 empty] | 3/19/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 3/19/2001 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Challenging
1599 | 30732 | 12/3/2001 | Potentially Challenging | No | N/A |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 12/3/2001 | Potentially Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/3/2001 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 12/3/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1600 | 30733 | 6/27/2002 | Potentially Challenging | No |  |  |  | Generator |  | 4KV | AC |  |  | 6/27/2002 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Structural component |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No | [8 empty] | 6/27/2002 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 6/27/2002 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
1601 | 30734 | 8/26/2002 | Potentially Challenging | No |  |  | DC Power System | Cable/Wiring |  | 125VDC | DC |  |  | 8/26/2002 | Potentially Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/26/2002 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 8/26/2002 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
1602 | 30735 | 3/4/2003 | Not Challenging | Yes | N/A |  |  | Other | [5 empty] | 3/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Unknown | Unknown | No damage | No | [8 empty] | 3/4/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 3/4/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1603 | 30736 | 3/13/2003 | Undetermined (PC‐CH) | No |  | Other (Specify in comments) | [7 empty] | 3/13/2003 | Undetermined (PC‐CH) | Unknown | Unknown |  | Unknown | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No | [8 empty] | 3/13/2003 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 3/13/2003 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
1604 | 30737 | 5/12/2003 | Not Challenging | No | N/A | [8 empty] | 5/12/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/12/2003 | Not Challenging | Final | Potentially Challenging | [22 empty] | 5/12/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1605 | 30738 | 9/23/2003 | Not Challenging | No |  |  |  | Transformers |  | 600V | AC |  |  | 9/23/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | No | [8 empty] | 9/23/2003 | Not Challenging | Final | Not Challenging | [22 empty] | 9/23/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1606 | 30739 | 3/29/2001 | Not Challenging | No | [9 empty] | 3/29/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component |  | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/29/2001 | Not Challenging | Final | Not Challenging | [22 empty] | 3/29/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1607 | 30740 | 2/6/2004 | Potentially Challenging | No | N/A |  |  | Other | [5 empty] | 2/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/6/2004 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 2/6/2004 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1608 | 30741 | 3/24/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 3/24/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/24/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 3/24/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1609 | 30742 | 4/15/2004 | Not Challenging | No | [9 empty] | 4/15/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/15/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 4/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1610 | 30743 | 4/27/2004 | Not Challenging | No | [9 empty] | 4/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/27/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 4/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1611 | 30744 | 6/2/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | Hot work (cutting/welding/grinding/etc.) | Not Challenging | Unknown | Transient | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 6/2/2004 | Not Challenging | Final | Challenging | [22 empty] | 6/2/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1612 | 30745 | 10/10/2004 | Not Challenging | No | [9 empty] | 10/10/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/10/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 10/10/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1613 | 30746 | 10/28/2004 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/28/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/28/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [22 empty] | 10/28/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1614 | 30747 | 11/6/2004 | Not Challenging | No | [9 empty] | 11/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/6/2004 | Not Challenging | Final | Not Challenging | [22 empty] | 11/6/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1615 | 30748 | 11/27/2004 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 11/27/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/27/2004 | Not Challenging | Final | Potentially Challenging | [22 empty] | 11/27/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1616 | 30749 | 1/9/2005 | Not Challenging | No | [9 empty] | 1/9/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/9/2005 | Not Challenging | Final | Not Challenging | [22 empty] | 1/9/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1617 | 30750 | 5/9/2005 | Undetermined (PC‐CH) | No | [9 empty] | 5/9/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Other (Specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/9/2005 | Undetermined (PC‐CH) | Final | Potentially Challenging | [22 empty] | 5/9/2005 | Undetermined (PC‐CH) | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Challenging
1618 | 30751 | 3/28/2006 | Not Challenging | No | [9 empty] | 3/28/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/28/2006 | Not Challenging | Final | Not Challenging | [22 empty] | 3/28/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1619 | 30752 | 4/3/2007 | Potentially Challenging | No | N/A | Turbine Building |  | Other | [5 empty] | 4/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Contained within reservoir | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/3/2007 | Potentially Challenging | Final | Potentially Challenging | [22 empty] | 4/3/2007 | Potentially Challenging | Operate | Operate |  |  |  |  | Challenging
1620 | 30753 | 5/16/2007 | Not Challenging | No |  | Other (Specify in comments) | [7 empty] | 5/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/16/2007 | Not Challenging | Final | Potentially Challenging | [22 empty] | 5/16/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1621 | 30754 | 2/2/2008 | Not Challenging | No | [9 empty] | 2/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/2/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 2/2/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1622 | 30755 | 4/7/2008 | Not Challenging | No | [9 empty] | 4/7/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/7/2008 | Not Challenging | Final | Not Challenging | [22 empty] | 4/7/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1623 | 30756 | 11/23/2008 | Undetermined (PC‐CH) | No | N/A |  |  | Other | [5 empty] | 11/23/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/23/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [22 empty] | 11/23/2008 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Challenging
1624 | 30757 | 8/24/2009 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 8/24/2009 | Undetermined (NC‐PC) | Unknown | Transient |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/24/2009 | Undetermined (NC‐PC) | Final | Potentially Challenging | [22 empty] | 8/24/2009 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1625 | 30758 | 9/3/2009 | Not Challenging | No |  |  |  | Air Compressors | [5 empty] | 9/3/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/3/2009 | Not Challenging | Final | Not Challenging | [22 empty] | 9/3/2009 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1626 | 40730 | 10/27/2000 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | N/A | N/A |  |  | 10/27/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/27/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/27/2000 | Not Challenging |  | 14:00:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1627 | 40731 | 2/13/2001 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A |  |  | 2/13/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/13/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/13/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/13/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1628 | 40732 | 3/8/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/8/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/8/2001 | Not Challenging |  | 15:50:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments | [7 empty] | 3/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1629 | 40733 | 3/14/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) | Hydrogen Supply System | Other |  | N/A | N/A |  |  | 3/14/2001 | Potentially Challenging | Unknown | Unknown | Hydrogen | Other (Specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/14/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/14/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 3/14/2001 | Potentially Challenging | Operate | Operate | 100 |  | None |  | Challenging
1630 | 40734 | 3/19/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/19/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/19/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/19/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1631 | 40735 | 4/4/2001 | Not Challenging | No | N/A | Other (Specify in comments) | Hydrogen Supply System | Other |  | N/A | N/A |  |  | 4/4/2001 | Potentially Challenging | Unknown | Gas | Hydrogen | Confined liquid spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/4/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/4/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered | Portable: Other [specify] | [6 empty] | 4/4/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1632 | 40736 | 4/15/2001 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/15/2001 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/15/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/15/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/15/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1633 | 40737 | 4/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  |  |  | N/A | N/A |  |  | 4/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | Liquid |  | Other (Specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1634 | 40738 | 6/5/2002 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other |  | N/A | N/A |  |  | 6/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/5/2002 | Not Challenging | Final | Challenging | [5 empty] | 6/5/2002 | Not Challenging |  | 03:00:00 | Known | 105 | 105 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water | [6 empty] | 6/5/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1635 | 40739 | 7/23/2002 | Not Challenging | No |  | Auxiliary Building (PWR) |  |  |  | N/A | N/A |  |  | 7/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/23/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 7/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | [7 empty] | 7/23/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1636 | 40740 | 3/3/2003 | Not Challenging | No | N/A | Turbine Building | [7 empty] | 3/3/2003 | Not Challenging | Unknown | Unknown |  |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/3/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1637 | 40741 | 4/16/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | Confined to the object of origin | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/16/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/16/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 4/16/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1638 | 40742 | 7/7/2003 | Not Challenging | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC |  |  | 7/7/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ |  |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 7/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/7/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1639 | 40743 | 10/7/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  |  | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 10/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 10/7/200 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1640 | 40744 | 3/24/2004 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 110V | AC |  |  | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/24/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 3/24/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1641 | 40745 | 10/20/2005 | Not Challenging | No | N/A | Turbine Building |  | Other |  | 24‐48VDC | DC |  |  | 10/20/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No | [8 empty] | 10/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/20/2005 | Not Challenging | Refueling | Refueling |  |  | None |  | Not Challenging
1642 | 40746 | 8/15/2006 | Potentially Challenging | No |  | Turbine Building | [7 empty] | 8/15/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/15/2006 | Potentially Challenging | Final | Not Challenging | [5 empty] | 8/15/2006 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Other (specify in comments) | Portable: CO2 | [6 empty] | 8/15/2006 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1643 | 40747 | 4/17/2007 | Not Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 4/17/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/17/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/17/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1644 | 40748 | 11/28/2007 | Not Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 11/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/28/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 11/28/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 11/28/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1645 | 40749 | 6/13/2008 | Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 6/13/2008 | Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to room of origin | No | [8 empty] | 6/13/2008 | Challenging | Final | Challenging | [5 empty] | 6/13/2008 | Not Challenging |  |  | Known | 9 | 9 | Dedicated Fire Watch | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified,Multiple portable fire extinguishers | Portable: CO2,Other: Water | [6 empty] | 6/13/2008 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1646 | 40750 | 11/16/2009 | Not Challenging | No |  | Auxiliary Building (PWR) | [7 empty] | 11/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/16/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 11/16/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/16/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1647 | 50356 | 1/11/2000 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Other |  | 110V | AC |  |  | 1/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/11/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 1/11/2000 | Not Challenging |  | 10:30:00 | Known | 0 | 0 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/11/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1648 | 50357 | 3/21/2000 | Not Challenging | No | Main Control Room | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 110V | AC |  |  | 3/21/2000 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/21/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/21/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | Other: None | [6 empty] | 3/21/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1649 | 50358 | 6/1/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/1/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (Specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/1/2000 | Not Challenging | Final | Challenging | [5 empty] | 6/1/2000 | Not Challenging |  | 10:11:00 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Hose stream or hose reel,Supervised burn out | Other: Water | [6 empty] | 6/1/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1650 | 50359 | 8/24/2000 | Not Challenging | No |  | Control building | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  |  | 8/24/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/24/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 8/24/2000 | Not Challenging |  | 14:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1651 | 50360 | 12/20/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | [5 empty] | 12/20/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/20/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/20/2000 | Not Challenging |  | 03:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/20/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1652 | 50361 | 4/11/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC |  |  | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/11/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 4/11/2001 | Potentially Challenging |  | 18:10:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments),Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/11/2001 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
1653 | 50362 | 7/16/2001 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans | 480V | AC |  |  | 7/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/16/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/16/2001 | Not Challenging |  | 15:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/16/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1654 | 50363
1655 | 50364 | 10/4/2001 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 10/4/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/4/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/4/2001 | Not Challenging |  | 10:00:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed | Portable: None | [6 empty] | 10/4/2001 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1656 | 50365 | 3/4/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/4/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/4/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/4/2002 | Not Challenging |  | 02:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments) | [7 empty] | 3/4/2002 | Not Challenging | Operate | Operate | 97 | 97 | None |  | Not Challenging
1657 | 50366 | 3/8/2002 | Not Challenging | No |  | Control building | [7 empty] | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Unknown | No Fire ‐ False actuation of detection device | Unknown | Unknown | Confined to the object of origin | No | [8 empty] | 3/8/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/8/2002 | Not Challenging |  | 15:00:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments) | [7 empty] | 3/8/2002 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1658 | 50367 | 3/14/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | Other (specify) | AC |  |  | 3/14/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/14/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/14/2002 | Not Challenging | 21:30:00 | 21:30:00 | Known | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Other (specify in comments) | [7 empty] | 3/14/2002 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1659 | 50368 | 6/6/2002 | Not Challenging | No | Main Control Room |  | General Ventillation Systems | Other |  | 110V | AC |  |  | 6/6/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/6/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/6/2002 | Not Challenging | 04:08:00 | 04:08:00 | Known | 1 | 1 | Smoke detector | Plant area had installed detection which actuated | Unknown | [7 empty] | 6/6/2002 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1660 | 50369 | 8/14/2002 | Not Challenging | No | N/A | Control building | DC Power System | Transformers | Other (Capacitor Voltage, Poten | 125VDC | DC |  |  | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/14/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/14/2002 | Not Challenging |  | 03:50:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/14/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1661 | 50370 | 10/23/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 110V | AC |  |  | 10/23/2002 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/23/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/23/2002 | Not Challenging |  | 13:18:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 10/23/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1662 | 50371 | 11/1/2002 | Not Challenging | No | Switchgear Room | Control building | Low Voltage Power System, Class 1E | Transformers |  | 480V | AC |  |  | 11/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/1/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/1/2002 | Not Challenging |  | 17:12:00 | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/1/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1663 | 50372 | 5/9/2003 | Not Challenging | No |  | Turbine Building |  | Electric Motor |  | 125VDC | DC |  |  | 5/9/2003 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/9/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 5/9/2003 | Not Challenging |  | 00:30:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed,Other (specify in comments) | [7 empty] | 5/9/2003 | Not Challenging | Hot Standby | Hot Standby | 0 | 0 | None |  | Not Challenging
1664 | 50373 | 10/7/2003 | Not Challenging | No |  | Turbine Building | Feedwater System | Other | [5 empty] | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/7/2003 | Not Challenging |  | 10:36:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | Portable: Dry Chemical | [6 empty] | 10/7/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1665 | 50374 | 4/22/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) | 110V | AC |  |  | 4/22/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/22/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/22/2004 | Not Challenging |  | 07:50:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/22/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1666 | 50375 | 9/30/2004 | Not Challenging | No |  | Auxiliary Building (PWR) | Closed/Component Cooling Water | Pumps | Electric motor driven pumps |  |  |  |  | 9/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (Specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/30/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/30/2004 | Not Challenging |  | 05:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/30/2004 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1667 | 50376 | 3/24/2005 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 9/30/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/24/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/24/2005 | Not Challenging |  | 08:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/24/2005 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1668 | 50377 | 7/2/2005 | Not Challenging | No |  | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 7/2/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/2/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/2/2005 | Not Challenging |  | 10:15:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 7/2/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1669 | 50378 | 7/27/2005 | Potentially Challenging | No |  | Control building | Instrument and Uninterruptible Power System | Transformers | Other (Capacitor Voltage, Poten | 110V | AC |  |  | 7/27/2005 | Other electrical or electronic equipment | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/27/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/27/2005 | Potentially Challenging | 12:53:00 | 12:55:00 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/27/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1670 | 50379 | 2/24/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 2/24/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/24/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/24/2006 | Not Challenging | 08:05:00 | 08:05:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed | [7 empty] | 2/24/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1671 | 50380 | 8/31/2006 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 8/31/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/31/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 8/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/31/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1672 | 50381 | 12/14/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/14/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/14/2006 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 12/14/2006 | Not Challenging |  | 08:30:00 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 12/14/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1673 | 50382 | 1/29/2007 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 1/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ |  |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/29/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/29/2007 | Not Challenging | 12:10:00 | 12:10:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 1/29/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1674 | 50383 | 3/1/2007 | Not Challenging | No |  | Control building |  | Other |  | 125VDC | DC |  |  | 3/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/1/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/1/2007 | Not Challenging | 02:00:00 | 02:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/1/2007 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Not Challenging
1675 | 50384 | 3/22/2007 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 3/22/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/22/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/22/2007 | Not Challenging |  | 00:21:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/22/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1676 | 50385 | 5/30/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 5/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/30/2007 | Not Challenging | Final | Challenging | [5 empty] | 5/30/2007 | Not Challenging |  | 11:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 5/30/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1677 | 50386
1678 | 50387 | 3/29/2008 | Not Challenging | No | N/A | Turbine Building | Feedwater System | Other |  | N/A | N/A |  |  | 3/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/29/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/29/2008 | Not Challenging |  | 14:19:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/29/2008 | Not Challenging | Refueling | Refueling | 0 | 100 | None |  | Not Challenging
1679 | 50388 | 6/8/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Transformers | Dry transformer | 110V | AC |  |  | 6/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/8/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 6/8/2008 | Not Challenging |  | 00:44:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 6/8/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1680 | 50389 | 6/23/2008 | Not Challenging | No |  | Auxiliary Building (PWR) |  | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 6/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/23/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/23/2008 | Not Challenging | 12:25:00 | 12:25:00 | Known | 6 | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Not Challenging
1681 | 50390 | 10/1/2008 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | 480V | AC |  |  | 10/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/1/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 10/1/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Air supply cut off (smothered, covered) | [7 empty] | 10/1/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1682 | 50391 | 7/2/2009 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 7/2/2009 | Not Challenging | Unknown | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 7/2/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/2/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 7/2/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1683 | 50392 | 8/13/2000 | Not Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 8/13/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/13/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 8/13/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention) | [7 empty] | 8/13/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1684 | 50393 | 10/17/2000 | Undetermined (NC‐PC) | No |  |  |  | Other |  | N/A | N/A |  |  | 10/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/17/2000 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/17/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1685 | 50394 | 4/21/2001 | Not Challenging | No |  |  | High Pressure Core Spray System (BWR) | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 4/21/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/21/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/21/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1686 | 50395 | 4/16/2001 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 4/16/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/16/2001 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 4/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments) | [7 empty] | 4/16/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1687 | 50396 | 5/1/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 5/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/1/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 5/1/2001 | Not Challenging |  | 23:05:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 5/1/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1688 | 50397 | 1/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 1/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/13/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/13/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 1/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1689 | 50398 | 12/2/2003 | Not Challenging | No | N/A |  |  | Electrical panel | [5 empty] | 12/2/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/2/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/2/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1690 | 50399 | 2/26/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 2/26/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/26/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 2/26/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/26/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1691 | 50400 | 8/7/2004 | Not Challenging | No |  |  | Reactor Core Isolation Cooling System (BWR) | Other | [5 empty] | 8/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/7/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments) | [7 empty] | 8/7/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1692 | 50401 | 10/4/2005 | Not Challenging | No |  |  |  | Other | [5 empty] | 10/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/4/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1693 | 50402 | 11/8/2005 | Not Challenging | No |  | Radwaste Building | General Ventillation Systems | Pumps | Electric motor driven pumps |  |  |  |  | 11/8/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/8/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/8/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments) | [7 empty] | 11/8/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1694 | 50403 | 11/8/2003 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 11/8/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas | Other (Specify) | Pressurized spray | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/8/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Water | [6 empty] | 11/8/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1695 | 50404 | 11/25/2005 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Electrical panel | Other (specify in comments) |  |  |  |  | 11/25/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/25/2005 | Undetermined (NC‐PC) | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/25/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/25/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1696 | 50405 | 3/4/2006 | Undetermined (NC‐PC) | No |  |  |  | Air Compressors | [5 empty] | 3/4/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/4/2006 | Undetermined (NC‐PC) | Preliminary | Potentially Challenging | [5 empty] | 3/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 3/4/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1697 | 50406 | 8/21/2007 | Not Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps |  |  |  |  | 8/21/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/21/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 8/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/21/2007 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1698 | 50407 | 3/11/2008 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 3/11/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/11/2008 | Potentially Challenging | Preliminary | Potentially Challenging | [5 empty] | 3/11/2008 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/11/2008 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1699 | 50408
1700 | 50409 | 10/5/2006 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) | [7 empty] | 10/5/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No | [8 empty] | 10/5/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/5/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 10/5/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1701 | 50410 | 9/29/2005 | Not Challenging | No |  |  |  | Other | [5 empty] | 9/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/29/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/29/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 9/29/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1702 | 50411 | 7/9/2005 | Undetermined (NC‐PC) | No | Main Control Room | Control building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 7/9/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure |  | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/9/2005 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 7/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/9/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1703 | 50412
1704 | 50413
1705 | 50414
1706 | 50415
1707 | 50416
1708 | 50417
1709 | 50418
1710 | 50419
1711 | 50420
1712 | 50421
1713 | 50422
1714 | 50423 | 2/28/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 2/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/28/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 2/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 2/28/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1715 | 50424 | 3/15/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 3/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/15/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/15/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1716 | 50425 | 3/16/2000 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 3/16/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/16/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Multiple portable fire extinguishers,Other (specify in comments) | [7 empty] | 3/16/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1717 | 50426 | 5/2/2000 | Potentially Challenging | No |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 5/2/2000 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 5/2/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/2/2000 | Potentially Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/2/2000 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1718 | 50427 | 8/19/2000 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 8/19/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/19/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 8/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/19/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1719 | 50428 | 9/20/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 9/20/2000 | Not Challenging | Unknown | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/20/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/20/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/20/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1720 | 50429 | 3/19/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/19/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/19/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 3/19/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1721 | 50430 | 2/18/2000 | Not Challenging | No |  | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/18/2000 | Not Challenging | Mechanical equipment malfunction/failure |  | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/18/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 2/18/2000 | Not Challenging |  | 06:21:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 2/18/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1722 | 50431
1723 | 50432 | 3/19/2001 | Not Challenging | No |  |  | General Ventillation Systems | Electrical panel | Motor control center |  |  |  |  | 3/19/2001 | Not Challenging | Electrical failure resulting in overheating materials |  | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/19/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/19/2001 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1724 | 50433 | 8/17/2001 | Not Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/17/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 8/17/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1725 | 50434 | 10/28/2001 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electrical panel | Motor control center |  |  |  |  | 10/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/28/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 10/28/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1726 | 50435 | 7/22/2002 | Not Challenging | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 7/22/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/22/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 7/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 7/22/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1727 | 50436 | 8/12/2002 | Not Challenging | Yes | Cable vault/tunnel area | Other (Specify in comments) |  | Other | [5 empty] | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/12/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/12/2002 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown | [7 empty] | 8/12/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1728 | 50437
1729 | 50438 | 1/7/2003 | Not Challenging | No |  | Other (Specify in comments) | Switchyard System | Transformers | [5 empty] | 1/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 1/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | [7 empty] | 1/7/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1730 | 50439 | 3/3/2003 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 3/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/3/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/3/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1731 | 50440 | 10/13/2004 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 10/13/2004 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No | [8 empty] | 10/13/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/13/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/13/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1732 | 50441 | 10/23/2004 | Not Challenging | Yes |  |  |  | Air Compressors | [5 empty] | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/23/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 10/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1733 | 50442 | 11/8/2004 | Potentially Challenging | No |  | Radwaste Building | Main Generator Hydrogen Cooling System | Other | [5 empty] | 11/8/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Other (Specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/8/2004 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/8/2004 | Potentially Challenging | 21:23:00 | 21:23:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/8/2004 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1734 | 50443 | 3/20/2005 | Not Challenging | No |  |  |  | Electric Motor | Crane motor |  |  |  |  | 3/20/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/20/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1735 | 50444 | 4/27/2005 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments) |  |  |  |  | 4/27/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/27/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/27/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1736 | 50445 | 4/28/2005 | Not Challenging | No |  |  | Condensate System | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 4/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 4/28/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/28/2005 | Not Challenging | 16:00:00 | 16:00:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/28/2005 | Not Challenging | Operate | Operate | 53 | 53 | None |  | Not Challenging
1737 | 50446 | 7/14/2005 | Not Challenging | No | Switchgear Room |  | DC Power System | Electrical panel | Relay rack | 125VDC | DC |  |  | 7/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 7/14/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1738 | 50447 | 9/14/2005 | Potentially Challenging | No |  |  | General Ventillation Systems | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 9/14/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/14/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 9/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/14/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1739 | 50448 | 10/11/2005 | Potentially Challenging | No |  | Turbine Building |  | Other | [5 empty] | 10/11/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/11/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/11/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments) | [7 empty] | 10/11/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
1740 | 50449 | 2/21/2006 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 2/21/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/21/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/21/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 2/21/2006 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1741 | 50450 | 2/28/2006 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 2/28/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/28/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/28/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 2/28/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1742 | 50451 | 7/15/2006 | Not Challenging | Yes |  | Other (Specify in comments) | General Ventillation Systems | Cable/Wiring | [5 empty] | 7/15/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/15/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/15/2006 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/15/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1743 | 50452 | 8/18/2006 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 8/18/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/18/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 8/18/2006 | Undetermined (NC‐PC) |  | 13:00:00 | Known | 4 | 4 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | [7 empty] | 8/18/2006 | Undetermined (NC‐PC) | Operate | Operate | 97 | 97 | None |  | Not Challenging
1744 | 50453 | 8/22/2006 | Not Challenging | Yes |  | Other (Specify in comments) |  | Other | [5 empty] | 8/22/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/22/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/22/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/22/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1745 | 50454 | 11/8/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 11/8/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/8/2006 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/8/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1746 | 50455 | 11/30/2006 | Not Challenging | No | Main Control Room | Control building | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 110V | AC |  |  | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/30/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 11/30/2006 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/30/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1747 | 50456 | 2/15/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 2/15/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/15/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 2/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/15/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1748 | 50457 | 7/28/2007 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 7/28/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | [10 empty] | 7/28/2007 | Not Challenging | Final | Challenging | [5 empty] | 7/28/2007 | Not Challenging | 16:05:00 | 16:05:00 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel,Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water | [6 empty] | 7/28/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1749 | 50458 | 8/15/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 8/15/2007 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/15/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/15/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1750 | 50459 | 2/8/2008 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/8/2008 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/8/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/8/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | [7 empty] | 2/8/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1751 | 50460 | 4/16/2008 | Not Challenging | No | N/A | Turbine Building |  | Other | [5 empty] | 4/16/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/16/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/16/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments) | [7 empty] | 4/16/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1752 | 50461 | 4/24/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 4/24/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 4/24/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 4/24/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1753 | 50462 | 6/12/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 6/12/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/12/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/12/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments) | Portable: Water | [6 empty] | 6/12/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1754 | 50463 | 4/11/2000 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 4/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/11/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/11/2000 | Not Challenging |  |  | Estimated | 10 | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/11/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1755 | 50464 | 4/26/2000 | Not Challenging | No | N/A | Containment (PWR) |  | Cable/Wiring |  | 480V | AC |  |  | 4/26/2000 | Not Challenging | Personnel error: Misuse of heating devices | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/26/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/26/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 4/26/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1756 | 50465
1757 | 50466 | 2/4/2005 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps |  |  |  |  | 2/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | Liquid | Lube Oil or Grease | Contained within reservoir | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/4/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 2/4/2005 | Not Challenging |  |  | Unknown |  |  |  | Plant area had installed detection which actuated | Unknown | [7 empty] | 2/4/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1758 | 50467 | 2/4/2006 | Undetermined (NC‐PC) | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | 11/2/2007 |  |  | 2/4/2006 | Undetermined (NC‐PC) | Unknown | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 2/4/2006 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 2/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/4/2006 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1759 | 50468 | 11/2/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/2/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/2007 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Unknown | [7 empty] | 11/2/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1760 | 50469 | 7/28/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries | [5 empty] | 7/28/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/28/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/28/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 7/28/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1761 | 50470 | 11/19/2008 | Not Challenging | No |  |  |  | Electrical panel | Other (specify in comments) |  |  |  |  | 11/19/2008 | Not Challenging |  | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/19/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention) | [7 empty] | 11/19/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1762 | 50471 | 12/2/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Switchyard System | Cable/Wiring |  | 480V | AC |  |  | 12/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/2/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/2/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 12/2/2008 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1763 | 50472 | 8/30/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/30/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1764 | 50473 | 6/26/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Wall Mounted or Sealed |  |  |  |  | 6/26/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/26/2000 | Potentially Challenging | Final with disagreement | Potentially Challenging | [5 empty] | 6/26/2000 | Potentially Challenging |  | 15:13:00 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/26/2000 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
1765 | 50474 | 8/29/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 8/29/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/29/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 8/29/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1766 | 50475 | 10/11/2000 | Undetermined (PC‐CH) | No |  |  |  | Electrical panel | Electric bus bar or bus duct |  |  |  |  | 10/11/2000 | Undetermined (PC‐CH) |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | [9 empty] | 10/11/2000 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 10/11/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 10/11/2000 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 |  |  | Challenging
1767 | 50476 | 12/19/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 12/19/2000 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/19/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 12/19/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1768 | 50477 | 3/18/2000 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/18/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Liquid | Other (Specify) | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/18/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/18/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/18/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1769 | 50478 | 3/19/2000 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 3/19/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/19/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 3/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 3/19/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1770 | 50479 | 3/22/2000 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Dryers | [5 empty] | 3/22/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/22/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/22/2000 | Potentially Challenging |  | 07:15:00 | Known | 19 | 19 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: Dry Chemical | [6 empty] | 3/22/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1771 | 50480 | 4/7/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 4/7/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/7/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/7/2000 | Not Challenging | 19:35:00 | 19:35:00 | Known | 4 | 4 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/7/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1772 | 50481 | 11/4/2006 | Not Challenging | No | N/A | Turbine Building | Main Generator System | Generator | Main turbine generator | 13 KV or greater | AC |  |  | 11/4/2006 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | Unknown | No damage | No | [8 empty] | 11/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Other (specify in comments) | [7 empty] | 11/4/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1773 | 50482 | 3/8/2006 | Not Challenging | Yes | N/A |  | Feedwater System | Pumps | Electric motor driven pumps | 480V | AC |  |  | 3/8/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin | No | [8 empty] | 3/8/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/8/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 3/8/2006 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1774 | 50483 | 3/11/2008 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Emergency Onsite Power Supply System | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 3/11/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/11/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/11/2008 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/11/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1775 | 50484 | 3/23/2008 | Not Challenging | No |  |  | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 3/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Other (Specify) | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/23/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 3/23/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1776 | 50485
1777 | 50486 | 4/20/2008 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Cable/Wiring |  | 13 KV or greater | AC |  |  | 4/20/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 4/20/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/20/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 4/20/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1778 | 50487 | 3/6/2009 | Not Challenging | No | N/A | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 3/6/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/6/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 3/6/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/6/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1779 | 50488 | 5/27/2009 | Not Challenging | Yes | N/A |  | Turbine Lube Oil System | Lube Oil |  | N/A | N/A |  |  | 5/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/27/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 5/27/2009 | Not Challenging | 15:55:00 | 15:55:00 | Known | 5 | 5 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 5/27/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1780 | 50489 | 8/30/2009 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Low Voltage Power System (600V and less) | Cable/Wiring |  | 480V | AC |  |  | 8/30/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 8/30/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1781 | 50490 | 9/16/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 9/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/16/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 9/16/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 9/16/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1782 | 50491 | 10/16/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 220V | AC |  |  | 10/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/16/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/16/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/16/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1783 | 50492 | 11/2/2009 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Transformers | [5 empty] | 11/2/2009 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/2/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 11/2/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/2/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1784 | 50493
1785 | 50494 | 2/5/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 2/5/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ |  |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 2/5/2009 | Not Challenging | Final | Challenging | [5 empty] | 2/5/2009 | Not Challenging | 18:28:00 | 18:28:00 | Known | 16 | 16 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 2/5/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1786 | 50495 | 11/11/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 11/11/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/11/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 11/11/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/11/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1787 | 50496 | 1/21/2002 | Not Challenging | No | Switchgear Room |  | Non Essential Service Water System | Electrical panel | Other instrument/control cabin | Other (specify) | AC |  |  | 1/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Temporary thermal insulation materials |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/21/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 1/21/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 1/21/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1788 | 50497 | 8/15/2006 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  | 220V | AC |  |  | 8/15/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/15/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 8/15/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/15/2006 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1789 | 50498
1790 | 50499 | 4/1/2004 | Not Challenging | Yes | Switchgear Room | Other (Specify in comments) | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 125VDC | DC |  |  | 4/1/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/1/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 4/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/1/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1791 | 50500 |  | Not Challenging | [63 empty] | Not Challenging
1792 | 50501 | 11/6/2001 | Not Challenging | No | N/A | Control building |  | Other | [5 empty] | : 11/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 11/6/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/6/2001 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 11/6/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1793 | 50502 | 10/16/2002 | Not Challenging | No |  | Turbine Building |  | Cable/Wiring | [5 empty] | 10/16/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/16/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 10/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/16/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1794 | 50503 | 6/14/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | : 6/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : No damage | No | [8 empty] | 6/14/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 6/14/2001 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1795 | 50504 | 5/20/2002 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel |  | 480V | AC |  |  | : 5/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Structural component |  |  |  | Unknown | : Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/20/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/20/2002 | Potentially Challenging | 08:54:00 | 08:54:00 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/20/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1796 | 50505
1797 | 50506 | 12/9/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Switchyard System | Transformers | Other (Capacitor Voltage, Poten | Other (specify) | AC |  |  | 12/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/9/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/9/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 12/9/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1798 | 50507 | 11/15/2005 | Not Challenging | No | Containment/Drywell | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/15/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/15/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify] | [6 empty] | 11/15/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1799 | 50508 | 11/26/2005 | Not Challenging | No | Containment/Drywell | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 11/26/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/26/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/26/2005 | Not Challenging | 00:40:00 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water | [6 empty] | 11/26/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1800 | 50509 | [8 empty] | N/A | N/A
1801 | 50510 | 4/19/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/19/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/19/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 4/19/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 4/19/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1802 | 50511 | 5/15/2004 | Not Challenging | No | N/A | Turbine Building |  | Lube Oil |  | N/A | N/A |  |  | : 5/15/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) |  | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/15/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 5/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: None | [6 empty] | 5/15/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1803 | 50512 | 5/31/2000 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 5/31/2000 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/31/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 5/31/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/31/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1804 | 50513 | 8/27/2003 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/27/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/27/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/27/2003 | Not Challenging | Operate | Operate | 77 | 77 | None |  | Not Challenging
1805 | 50514 | 4/29/2009 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/29/2009 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 4/29/2009 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 4/29/2009 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments) | [7 empty] | 4/29/2009 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1806 | 50515 | 11/30/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 11/30/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/30/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/30/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 11/30/2001 | Undetermined (NC‐PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1807 | 50516 | 10/5/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 10/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/5/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/5/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 10/5/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1808 | 50517 | 10/8/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 10/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/8/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/8/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1809 | 50518 | 11/18/2001 | Undetermined (NC‐PC) | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring | [5 empty] | 11/18/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Smoldering combustion – external to component | Smoldering combustion – external to component | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/18/2001 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/18/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 11/18/2001 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1810 | 50519 | 10/19/2009 | Not Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System, Class 1E | Cable/Wiring | Other (specify in comments) | 250VDC | DC |  |  | 10/19/2009 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/19/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/19/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 10/19/2009 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1811 | 50520 | 12/7/2001 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 12/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/7/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/7/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 12/7/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1812 | 50521 | 2/1/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 2/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/1/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/1/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 2/1/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1813 | 50522 | 9/8/2003 | Undetermined (NC‐PC) | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 9/8/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 9/8/2003 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 9/8/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/8/2003 | Undetermined (NC‐PC) | Operate | Operate |  |  |  |  | Not Challenging
1814 | 50523 | 9/19/2003 | Not Challenging | No | N/A | Other (Specify in comments) | Low Voltage Power System, Class 1E | Cable/Wiring |  | 110V | AC |  |  | 9/19/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/19/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/19/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/19/2003 | Not Challenging | Operate | Operate |  |  | None |  | Not Challenging
1815 | 50524 | 1/23/2008 | Not Challenging | No |  |  |  | Other | [5 empty] | 1/23/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/23/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 1/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/23/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1816 | 50525 | 12/18/2009 | Not Evaluated | No | N/A | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers |  | 13 KV or greater | AC |  |  | 12/18/2009 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/18/2009 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 12/18/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 12/18/2009 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1817 | 50526 | 12/7/2006 | Not Evaluated | No | [9 empty] | 12/7/2006 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ |  |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/7/2006 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 12/7/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 12/7/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1818 | 50527 | 6/23/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/23/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/23/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 6/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water | [6 empty] | 6/23/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1819 | 50528 | 6/19/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 6/19/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 6/19/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/19/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 6/19/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1820 | 50529 | 3/31/2003 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 3/31/2003 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/31/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/31/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/31/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1821 | 50530 | 10/21/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Electric Motor | Fans | 4KV | AC |  |  | 10/21/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/21/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/21/2008 | Potentially Challenging |  | 08:56:00 | Known | 540 | 540 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/21/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1822 | 50531
1823 | 50532
1824 | 50533
1825 | 50534 | 1/7/2002 | Not Evaluated | No | N/A | Turbine Building | Hydrogen Supply System | Other |  | N/A | N/A |  |  | 1/7/2002 | Not Evaluated | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/7/2002 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 1/7/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments) | [7 empty] | 1/7/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1826 | 50535 | 1/8/2002 | Not Challenging | Yes | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 1/8/2002 | Not Challenging | Preliminary | Undetermined (NC‐PC) | [5 empty] | 1/8/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 1/8/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1827 | 50536 | 3/21/2002 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 3/21/2002 | Not Evaluated | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 3/21/2002 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/21/2002 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 3/21/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1828 | 50537 | 3/23/2002 | Not Challenging | No |  |  |  | Electric Motor | Fans |  |  |  |  | 3/23/2002 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Interior finish |  | Fire not observed and fire type indeterminate from post‐inspection | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 3/23/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 3/23/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1829 | 50538 | 3/27/2002 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/27/2002 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Other (Specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/27/2002 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/27/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Fuel supply removed | [7 empty] | 3/27/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1830 | 50539 | 5/22/2002 | Not Challenging | Yes | Containment/Drywell | Containment (PWR) | General Ventillation Systems | Other |  | N/A | N/A |  |  | 5/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/22/2002 | Not Challenging | Preliminary | Potentially Challenging | [5 empty] | 5/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 5/22/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1831 | 50540 | 5/25/2002 | Not Challenging | No |  |  |  | Other | [5 empty] | 5/25/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/25/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 5/25/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed | [7 empty] | 5/25/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1832 | 50541 | 4/6/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/6/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 4/6/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 4/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed | [7 empty] | 4/6/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1833 | 50542 | 7/30/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 7/30/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 7/30/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 7/30/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/30/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1834 | 50543 | 3/27/2001 | Potentially Challenging | No | Containment/Drywell | Containment (PWR) | Reactor Coolant System | Other |  | N/A | N/A |  |  | 3/27/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/27/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/27/2001 | Potentially Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/27/2001 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
1835 | 50544
1836 | 50545 | 9/18/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 9/18/2003 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/18/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 9/18/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/18/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1837 | 50546 | 12/1/2004 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other | [5 empty] | 12/1/2004 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/1/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/1/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1838 | 50547 | 4/4/2006 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 4/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 4/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 4/4/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1839 | 50548 | 6/9/2006 | Not Challenging | Yes |  |  |  | Other |  | N/A | N/A |  |  | 6/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/9/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 6/9/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 6/9/2006 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1840 | 50549 | 1/21/2007 | Not Challenging | No |  |  |  | Other | [5 empty] | 1/21/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/21/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/21/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 100 | 100 | None |  | Not Challenging
1841 | 50550 | 6/9/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | [7 empty] | 6/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/9/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 6/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/9/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1842 | 50551 | 10/6/2008 | Not Challenging | No | Battery Room | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans | 220V | AC |  |  | 10/6/2008 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/6/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 10/6/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/6/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1843 | 50552 | 3/23/2009 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Other |  | N/A | N/A |  |  | 3/23/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/23/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 3/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 3/23/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1844 | 50553 | 5/2/2003 | Potentially Challenging | No | Main Control Room | Control building |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 5/2/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/2/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/2/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Halon | [6 empty] | 5/2/2003 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
1845 | 50554 | 5/19/2003 | Not Challenging | No | Fuel handling area |  | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabin | 110V | AC |  |  | 5/19/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/19/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 5/19/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 5/19/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1846 | 50555 | 6/25/2003 | Not Challenging | Yes |  | Other (Specify in comments) | [7 empty] | : 6/25/2003 | Not Challenging | Unknown | Unknown |  |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 6/25/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/25/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 6/25/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1847 | 50556 | 2/25/2005 | Undetermined (NC‐PC) | No | N/A | Reactor Building (BWR) | Medium Voltage Power System (601V to 35kV) | Electric Motor | MG set | 13 KV or greater | AC |  |  | 2/25/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Flaming combustion – external to component | No smoke present | Unknown | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 2/25/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 2/25/2005 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/25/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1848 | 50557 | 1/16/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electric Motor | MG set | 250VDC | DC |  |  | 1/16/2001 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/16/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 1/16/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/16/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1849 | 50558 | 1/2/2007 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electric Motor | MG set | 250VDC | DC |  |  | 1/2/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/2/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | [7 empty] | 1/2/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1850 | 50559
1851 | 50560
1852 | 50561
1853 | 50562 | 5/28/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Offgas System (BWR) | Other | [5 empty] | 5/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/28/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 5/28/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/28/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1854 | 50563 | 11/16/2005 | Undetermined (PC‐CH) | No | N/A | Turbine Building | Hydrogen Supply System | Other | [5 empty] | 11/16/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/16/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/16/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 11/16/2005 | Undetermined (PC‐CH) | Operate | Operate | 100 | 100 | None |  | Challenging
1855 | 50564 | 1/15/2007 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 1/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/15/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/15/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 1/15/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1856 | 50565 | 8/26/2008 | Not Challenging | No | N/A | Radwaste Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 8/26/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/26/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/26/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1857 | 50566 | 9/17/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring |  | 13 KV or greater | AC |  |  | 9/17/2008 | Not Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/17/2008 | Not Challenging | Final | Challenging | [5 empty] | 9/17/2008 | Not Challenging | 09:30:00 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/17/2008 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1858 | 50567
1859 | 50568
1860 | 50569 | 3/24/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Outlets | [5 empty] | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/24/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/24/2004 | Not Challenging | 01:25:00 |  | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 3/24/2004 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1861 | 50570 | 6/21/2004 | Undetermined (NC‐PC) | No | N/A | Service Water Pump house | Low Voltage Power System (600V and less) | Pumps | Electric motor driven pumps | 480V | AC |  |  | 6/21/2004 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/21/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 6/21/2004 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/21/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 |  |  | Not Challenging
1862 | 50571 | 7/22/2004 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 7/22/2004 | Not Challengin | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/22/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 7/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 7/22/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1863 | 50572 | 10/8/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/8/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/8/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2003 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 10/8/2003 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1864 | 50573 | 8/24/2004 | Not Challenging | No |  | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps |  |  |  |  | 8/24/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Other (Specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/24/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/24/2004 | Not Challenging | 08:37:00 | 08:38:00 | Known | 31 | 31 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Power Supply Removed，Self‐extinguished (no plant staff intervention) | [7 empty] | 8/24/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1865 | 50574 | 9/16/2004 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 9/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 9/16/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/16/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 9/16/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1866 | 50575 | 9/14/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries |  | Other (specify) | AC |  |  | 9/14/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/14/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/14/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1867 | 50576 | 9/17/2004 | Not Challenging | No | Battery Room | Reactor Building (BWR) | General Ventillation Systems | Other |  | 110V | AC |  |  | 9/17/2004 | Not Challenging | Personnel error during test and maintenance activity | Transient_Liquid | Other (Specify) | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/17/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/17/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical | [6 empty] | 9/17/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1868 | 50577 | 10/23/2004 | Not Challenging | No | N/A | Control building |  | Electric Motor | Elevator motor | N/A | N/A |  |  | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/23/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 10/23/2004 | Not Challenging | 00:00:00 |  | Estimated | 0 | 0 | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 10/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1869 | 50578 | 11/23/2004 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | [6 empty] | 11/23/2004 | Not Challenging |  | Liquid | Lube Oil or Grease | Other (Specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | onfined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/23/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 11/23/2004 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/23/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1870 | 50579 | 5/4/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/4/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water | [6 empty] | 5/4/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1871 | 50580 | 10/9/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center | 480V | AC |  |  | 10/9/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No | [8 empty] | 10/9/2004 | Not Challenging | Final | Challenging | [5 empty] | 10/9/2004 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/9/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1872 | 50581 | 6/24/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 6/24/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/24/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water | [6 empty] | 6/24/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1873 | 50582 | 8/22/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  |  | N/A |  |  | 8/22/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Contained within component | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No | [8 empty] | 8/22/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 8/22/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 8/22/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1874 | 50583 | 9/3/2005 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Medium Voltage Power System (601V to 35kV) | Electrical panel | Circuit breaker or other distribu | Circuit breaker or other distribu | AC |  |  | 9/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 9/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | Reduced Power |  | Not Challenging
1875 | 50584 | 6/27/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Relay rack | 125VDC | DC |  |  | 6/27/2005 | Not Challenging |  | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/27/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/27/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/27/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1876 | 50585 | 10/8/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/8/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/8/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1877 | 50586 | 9/28/2005 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Relay rack |  |  |  |  | 9/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 9/28/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/28/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 9/28/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1878 | 50587 | 2/4/2006 | Not Challenging | Yes | N/A |  | Medium Voltage Power System (601V to 35kV) | Electrical panel | Electric bus bar or bus duct | 13 KV or greater | AC |  |  | 2/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 2/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/4/2006 | Not Challenging | Operate | Operate | 100 | 100 | Reduced Power |  | Not Challenging
1879 | 50588 | 2/4/2006 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 2/4/2006 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | Overheating – no smoldering or flaming combustion | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 2/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/4/2006 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 2/4/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1880 | 50589 | 4/15/2006 | Not Challenging | No | Cable vault/tunnel area | Reactor Building (BWR) |  | Lighting Ballasts |  | 110V | AC |  |  | 4/15/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No | [8 empty] | 4/15/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 4/15/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 4/15/2006 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1881 | 50590 | 5/6/2006 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Switchgear | 13 KV or greater | AC |  |  | 5/6/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/6/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 5/6/2006 | Not Challenging | 05:50:00 |  | Known | 5 | 5 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/6/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1882 | 50591 | 5/29/2006 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other |  | N/A | N/A |  |  | 5/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/29/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 5/29/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1883 | 50592 | 7/11/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 220V | AC |  |  | 7/11/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 7/11/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/11/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1884 | 50593 | 10/4/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 480V | AC |  |  | 10/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/4/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1885 | 50594 | 10/5/2006 | Not Challenging | No | N/A | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Outlets |  | 110V | AC |  |  | 10/5/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/5/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Plant area did not have installed detection capability | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/5/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1886 | 50595 | 10/28/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/28/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 10/28/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 10/28/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Plant area did not have installed detection capability | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 10/28/2007 | Not Challenging | Operate | Operate | 0 | 0 |  |  | Not Challenging
1887 | 50596 | 1/5/2007 | Not Challenging | No | Cable vault/tunnel area | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 1/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/5/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 1/5/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/5/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1888 | 50597 | 12/18/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 12/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/18/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 12/18/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/18/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1889 | 50598 | 3/10/2008 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Electric Motor | Fans |  |  |  |  | 3/10/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  |  |  | No | [8 empty] | 3/10/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/10/2008 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 3/10/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1890 | 50599 | 3/31/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC |  |  | 3/31/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Single Cable | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/31/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/31/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/31/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1891 | 50600 | 12/2/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring |  | 13 KV or greater | AC |  |  | 12/2/2008 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/2/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/2/2008 | Not Challenging |  |  | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 12/2/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1892 | 50601 | 8/30/2009 | Not Challenging | No |  | Other (Specify in comments) |  | Lighting Ballasts |  | 110V | AC |  |  | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/30/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/30/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1893 | 50602
1894 | 50603 | 2/24/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Junction Boxes |  | 220V | AC |  |  | 2/24/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/24/2007 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 2/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/24/2007 | Not Challenging | Operate | Operate | 73 | 73 | None |  | Not Challenging
1895 | 50604 | 11/27/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/27/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 11/27/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/27/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1896 | 50605 | 10/4/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No | [8 empty] | 10/4/2009 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/4/2009 | Not Challenging |  | 23:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/4/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1897 | 50606 | 10/8/2001 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts |  | 110V | AC |  |  | 10/8/2001 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/8/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/8/2001 | Not Challenging |  | 04:30:00 | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1898 | 50607 | 3/1/1997 | Not Evaluated | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 3/1/1997 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/1/1997 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/1/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/1/1997 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1899 | 50608 | 5/28/1997 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Cable/Wiring |  | 110V | AC |  |  | 5/28/1997 | Not Evaluated | Electrical arcing or sparks (non-HEAF) |  |  |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No | [8 empty] | 5/28/1997 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 5/28/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/28/1997 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1900 | 50609 | 11/23/2000 | Not Evaluated | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 11/23/2000 | Not Evaluated | Mechanical equipment malfunction/failure | In_Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/23/2000 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 11/23/2000 | Not Evaluated |  |  | Estimated | 0 | 0 | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/23/2000 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1901 | 50610 | 5/30/2005 | Not Evaluated | No | Fuel handling area | Reactor Building (BWR) |  | Cable/Wiring |  | 480V | AC |  |  | 5/30/2005 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/30/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 5/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 5/30/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1902 | 50611 | 3/19/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 3/19/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/19/2008 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/19/2008 | Not Challenging | 13:07:00 | 13:07:00 | Known | 1 | 1 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/19/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1903 | 50612 | 10/21/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 10/21/2002 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/21/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 10/21/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/21/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Challenging
1904 | 50613 | 7/3/2003 | Not Evaluated | No | Fuel handling area | Turbine Building |  | Other | [5 empty] | 7/3/2003 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/3/2003 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 7/3/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 7/3/2003 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1905 | 50614 | 3/9/2004 | Not Evaluated | No | N/A |  |  | Other |  | N/A | N/A |  |  | 3/9/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient_Gas |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/9/2004 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/9/2004 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 3/9/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1906 | 50615 | 3/11/2004 | Not Evaluated | No | N/A |  |  |  |  | N/A | N/A |  |  | 3/11/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/11/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/11/2004 | Not Evaluated |  | 17:30:00 | Estimated | 0 | 0 | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 3/11/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1907 | 50616 | 3/21/2004 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A |  |  | 3/21/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 3/21/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 3/21/2004 | Not Evaluated |  | 03:00:00 | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 3/21/2004 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1908 | 50617 | 3/29/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A |  |  | 3/29/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/29/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/29/2005 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 3/29/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1909 | 50618 | 9/14/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 9/14/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/14/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 9/14/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1910 | 50619 | 2/8/2006 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 2/8/2006 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/8/2006 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 2/8/2006 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 2/8/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1911 | 50620 | 3/27/2008 | Not Challenging | No | N/A | Control building |  | Lighting Ballasts | [24 empty] | 3/27/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 3/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/27/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1912 | 50621 | 9/11/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 9/11/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/11/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 9/11/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/11/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1913 | 50622 | 11/8/2009 | Not Challenging | No | N/A |  |  | Lighting Ballasts | [5 empty] | 11/8/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/8/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 11/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/8/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1914 | 50623 | 12/15/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Outlets |  | 110V | AC |  |  | 12/15/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 12/15/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/15/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1915 | 50624 | 5/14/2003 | Not Challenging | No |  | Turbine Building |  | Lighting Ballasts | [5 empty] | 5/14/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/14/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/14/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 5/14/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1916 | 50625 | 1/8/2001 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 1/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | Other (Specify) | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/8/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/8/2001 | Not Challenging |  | 12:03:00 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown | [7 empty] | 1/8/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1917 | 50626
1918 | 50627 | 3/24/2001 | Not Challenging | No |  |  |  | Other | [5 empty] | 3/24/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No | [8 empty] | 3/24/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/24/2001 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1919 | 50628 | 3/9/2000 | Not Challenging | No | Main Control Room | Control building |  | Other |  | 110V | AC |  |  | 3/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/9/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 3/9/2000 | Not Challenging |  |  | Unknown | 0 | 0 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/9/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1920 | 50629 | 10/16/2000 | Not Challenging | No |  |  |  | Transformers | Dry transformer |  |  |  |  | 10/16/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/16/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/16/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1921 | 50630 | 10/22/2000 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring | [5 empty] | 10/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/22/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/22/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1922 | 50631 | 10/27/2000 | Not Challenging | No |  |  |  | Electrical panel | Motor control center |  |  |  |  | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/27/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1923 | 50632 | 10/27/2000 | Not Challenging | No | N/A | Control building |  | Electrical panel | Relay rack |  |  |  |  | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/27/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/27/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1924 | 50633 | 11/12/2000 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/12/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/12/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 11/12/2000 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1925 | 50634 | 3/6/2002 | Not Challenging | No |  |  |  | Electrical panel | Battery charger | 250VDC | DC |  |  | 3/6/2002 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/6/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/6/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1926 | 50635 | 12/12/2000 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Electrical panel | Relay rack |  |  |  |  | 12/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/12/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/12/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/12/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1927 | 50636 | 2/10/2001 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 2/10/2001 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/10/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 2/10/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/10/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1928 | 50637 | 4/18/2001 | Not Challenging | No |  |  |  | Other | [5 empty] | 4/18/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/18/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/18/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1929 | 50638 | 5/14/2001 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 480V | AC |  |  | 5/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/14/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 5/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/14/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1930 | 50639 | 11/10/2001 | Not Challenging | Yes | N/A |  | Heat Rejection System (Circulating Water) | Transformers | Other (Capacitor Voltage, Poten | 220V | AC |  |  | 11/10/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/10/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/10/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/10/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1931 | 50640 | 12/23/2001 | Not Challenging | Yes | N/A |  | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 220V | AC |  |  | 12/23/2001 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/23/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 12/23/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/23/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1932 | 50641 | 3/4/2002 | Not Challenging | No |  |  |  | Electric Motor | Other (specify in comments) |  |  |  |  | 3/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Pressurized in a container | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/4/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 3/4/2002 | Not Challenging |  | 18:33:00 | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/4/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1933 | 50642 | 4/16/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/16/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/16/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 4/16/2002 | Not Challenging | 10:30:00 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 4/16/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1934 | 50643 | 4/18/2002 | Not Challenging | No |  |  |  | Electrical panel | [5 empty] | 4/18/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/18/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 4/18/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/18/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1935 | 50644 | 6/24/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Main control board (i.e., the ma | 110V | AC |  |  | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/24/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 6/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/24/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1936 | 50645 | 12/23/2002 | Not Challenging | No | Main Control Room | Control building |  | Lighting Ballasts | [5 empty] | 12/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/23/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 12/23/2002 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 12/23/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1937 | 50646 | 3/7/2003 | Not Challenging | No |  |  |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 3/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/7/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/7/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/7/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1938 | 50647 | 8/12/2003 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Other (specify in comments) | N/A | N/A |  |  | 8/12/2003 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/12/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 8/12/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/12/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1939 | 50648 | 12/2/2003 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Crane |  | N/A | N/A |  |  | 12/2/2003 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No | [8 empty] | 12/2/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1940 | 50649 | 4/22/2003 | Not Challenging | No | N/A | Diesel Generator Building |  | Other |  | 110V | AC |  |  | 4/22/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Single Cable | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/22/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/22/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/22/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1941 | 50650 | 9/26/2003 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other | Electric motor driven pumps | 110V | AC |  |  | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/26/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/26/2003 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/26/2003 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1942 | 50650 | 9/26/2003 | Not Challenging | Yes | N/A | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Other | Electric motor driven pumps | 110V | AC |  |  | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/26/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/26/2003 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/26/2003 | Not Challenging | Unknown | Unknown |  |  |  |  | Not Challenging
1943 | 50651 | 10/17/2003 | Not Challenging | Yes | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Cleaning solvents or paint |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/17/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water | [6 empty] | 10/17/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
1944 | 50652 | 3/18/2004 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 3/18/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/18/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/18/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/18/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1945 | 50653 | 10/4/2005 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 10/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/4/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 10/4/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
1946 | 50654 | 9/24/2007 | Not Challenging | No | N/A |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 9/24/2007 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/24/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/24/2007 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
1947 | 50655 | 12/4/2007 | Undetermined (NC‐PC) | No |  |  |  | Other | [5 empty] | 12/4/2007 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/4/2007 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 12/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/4/2007 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
1948 | 50656 | 8/18/2008 | Not Challenging | No |  |  |  | Electrical panel | Electrical panel |  |  |  |  | 8/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/18/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 8/18/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/18/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1949 | 50657 | 3/2/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC |  |  | 3/2/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/2/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/2/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/2/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1950 | 50658 | 4/24/2004 | Not Challenging | Yes | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/24/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/24/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 4/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 4/24/2004 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1951 | 50659 | 8/11/2004 | Not Challenging | No | N/A | Containment (PWR) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 8/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/11/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/11/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/11/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1952 | 50660 | 9/24/2000 | Not Challenging | No |  |  |  | Other | [5 empty] | 9/24/2000 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/24/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1953 | 50661 | 4/25/2001 | Not Evaluated | No | N/A | Main Transformer or Switch Yard | Main Generator Output Power System | Other |  | 13 KV or greater | AC |  |  | 4/25/2001 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2001 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 4/25/2001 | Not Evaluated |  |  | Unknown |  |  | Unknown | Unknown | Unknown | Unknown | [6 empty] | 4/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1954 | 50662 | 6/5/2001 | Not Evaluated | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/5/2001 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/5/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 6/5/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/5/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1955 | 50663 | 8/12/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Other |  | 220V | AC |  |  | 8/12/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/12/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/12/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/12/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1956 | 50664 | 6/29/2001 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/29/2001 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/29/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/29/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/29/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1957 | 50665 | 9/17/2004 | Not Challenging | No | N/A | Circulating Water Pump house/Intake Structure | Closed/Component Cooling Water | Pumps | Electric motor driven pumps |  |  |  |  | 9/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ |  |  | Other (specify) | Overheating – no smoldering or flaming combustion | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/17/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/17/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/17/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1958 | 50666 | 3/22/2005 | Not Challenging | No | N/A | Service Water Pump house |  | Pumps | Electric motor driven pumps |  |  |  |  | 3/22/2005 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/22/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/22/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/22/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1959 | 50667 | 3/28/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Lighting Ballasts |  | 220V | AC |  |  | 3/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Leak - Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/28/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/28/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/28/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1960 | 50668 | 4/16/2005 | Not Challenging | No |  |  |  | Electrical panel | Relay rack |  |  |  |  | 4/16/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/16/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/16/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/16/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1961 | 50669 | 1/3/2002 | Not Evaluated | No |  |  |  | Pumps | Diesel driven pumps |  |  |  |  | 1/3/2002 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/3/2002 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 1/3/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1962 | 50670 | 10/12/2005 | Not Challenging | No | N/A | Turbine Building |  | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 10/12/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/12/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/12/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1963 | 50671 | 10/20/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 10/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/20/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 10/20/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Unknown | Supervised burn out | [7 empty] | 10/20/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1964 | 50672 | 4/5/2002 | Not Evaluated | No |  |  |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 4/5/2002 | Not Evaluated |  |  |  |  | Unknown | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/5/2002 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 4/5/2002 | Not Evaluated |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/5/2002 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1965 | 50673 | 4/5/2002 | Not Evaluated | No | N/A | Turbine Building |  | Other | [5 empty] | 4/5/2002 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No | [8 empty] | 4/5/2002 | Not Evaluated | Preliminary | Challenging | [5 empty] | 4/5/2002 | Not Evaluated | 09:58:00 | 09:58:00 | Known | 14 | 14 | Other plant personnel (Roving watchstander or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical | [6 empty] | 4/5/2002 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1966 | 50674 | 9/23/2005 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Low Voltage Power System (600V and less) | Transformers | Other (Capacitor Voltage, Poten | 480V | AC |  |  | 9/23/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/23/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 9/23/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/23/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1967 | 50675 | 8/12/2002 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 8/12/2002 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/12/2002 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 8/12/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 8/12/2002 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1968 | 50676 | 11/29/2005 | Not Challenging | No | N/A | Service Water Pump house |  | Other |  | N/A | N/A |  |  | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/29/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/29/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/29/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1969 | 50677 | 9/24/2002 | Not Challenging | No |  |  |  | Other | [5 empty] | 9/24/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/24/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 9/24/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1970 | 50678 | 3/28/2006 | Not Challenging | Yes | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 220V | AC |  |  | 3/28/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/28/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 3/28/2006 | Not Challenging | 02:28:00 |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/28/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1971 | 50679 | 10/4/2002 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Cable/Wiring |  | 110V | AC |  |  | 10/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Leak - Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/4/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 10/4/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/4/2002 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
1972 | 50680 | 8/24/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 8/24/2006 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/24/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 8/24/2006 | Not Challenging |  | 11:45:00 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 8/24/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1973 | 50681 | 11/22/2000 | Not Evaluated | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 11/22/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/22/2000 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 11/22/2000 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/22/2000 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1974 | 50682 | 4/10/2007 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 4/10/2007 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/10/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/10/2007 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1975 | 50683 | 5/18/2004 | Not Evaluated | No | N/A | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 5/18/2004 | Not Evaluated | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/18/2004 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 5/18/2004 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/18/2004 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1976 | 50684 | 3/8/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/8/2007 | Not Challenging | Personnel error: Misuse of material ignited | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/8/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 3/8/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1977 | 50685 | 3/30/2007 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/30/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No | [8 empty] | 3/30/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/30/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/30/2007 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1978 | 50686 | 4/4/2007 | Undetermined (NC‐PC) | No | N/A | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 4/4/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 4/4/2007 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/4/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 4/4/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1979 | 50687 | 7/23/2007 | Not Challenging | No |  |  |  | Junction Boxes | [5 empty] | 7/23/2007 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/23/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 7/23/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/23/2007 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1980 | 50688 | 5/28/2004 | Not Challenging | No | N/A |  |  | Pumps | Diesel driven pumps |  |  |  |  | 5/28/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/28/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 5/28/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 5/28/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1981 | 50689 | 10/17/2005 | Not Evaluated | No | Containment/Drywell | Containment (PWR) |  | Other | [5 empty] | 10/17/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient_Gas |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/17/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 10/17/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 10/17/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1982 | 50690 | 10/24/2005 | Not Evaluated | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | N/A | N/A |  |  | 10/24/2005 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials | Contained within reservoir | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 10/24/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 10/24/2005 | Not Evaluated | 16:55:00 | 16:55:00 | Known | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 10/24/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1983 | 50691 | 2/15/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Batteries |  | N/A | N/A |  |  | 2/15/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/15/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 2/15/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required) | [7 empty] | 2/15/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1984 | 50692 | 3/24/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 3/24/2008 | Not Evaluated | Personnel error: Misuse of heating devices | Liquid | Other (specify) | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/24/2008 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/24/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 3/24/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
1985 | 50693 | 10/13/2008 | Not Evaluated | No | N/A |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 10/13/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/13/2008 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 10/13/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/13/2008 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
1986 | 50694 | 10/24/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 10/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Lube Oil or Grease |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/24/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 10/24/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/24/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
1987 | 50695
1988 | 50696 | 4/21/2008 | Not Challenging | No |  |  |  | Junction Boxes | [5 empty] | 4/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/21/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/21/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1989 | 50697 | 7/16/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 7/16/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/16/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/16/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments) | [7 empty] | 7/16/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1990 | 50698 | 3/17/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 3/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/17/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 3/17/2009 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/17/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1991 | 50699 | 4/7/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/7/2000 | Not Challenging | Personnel error: Misuse of heating devices | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 4/7/2000 | Not Challenging | Final | Challenging | [5 empty] | 4/7/2000 | Not Challenging |  | 14:25:00 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Water，Other: Water | [6 empty] | 4/7/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1992 | 50700 | 5/13/2000 | Not Challenging | Yes | N/A | Other (Specify in comments) | Heat Rejection System (Circulating Water) | Other |  | N/A | N/A |  |  | 5/13/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 5/13/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Unknown | Portable: Water | [6 empty] | 5/13/2000 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
1993 | 50701 | 5/24/2000 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil‐filled Transformer | 13 KV or greater | AC |  |  | 5/24/2000 | Not Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 5/24/2000 | Not Challenging | Final | Challenging | [5 empty] | 5/24/2000 | Not Challenging |  |  | Estimated |  |  | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: AFFF foam | [6 empty] | 5/24/2000 | Not Challenging | Operate | Operate | 100 | 100 | Turbine Trip |  | Not Challenging
1994 | 50702 | 6/25/2000 | Not Challenging | No | Main Control Room | Control building | [7 empty] | 6/25/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/25/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 6/25/2000 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown | [7 empty] | 6/25/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1995 | 50703 | 8/22/2000 | Not Challenging | Yes | N/A | Main Transformer or Switch Yard |  | Other | Oil‐filled Transformer |  |  |  |  | 8/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No | [8 empty] | 8/22/2000 | Not Challenging | Final | Challenging | [5 empty] | 8/22/2000 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 8/22/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1996 | 50704 | 12/22/2000 | Not Challenging | Yes | N/A |  | Low Voltage Power System (600V and less) | Cable/Wiring |  | 480V | AC |  |  | 12/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 12/22/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 12/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/22/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1997 | 50705 | 4/15/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/15/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/15/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/15/2001 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Water | [6 empty] | 4/15/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1998 | 50706 | 4/17/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 4/17/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 4/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/17/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
1999 | 50707 | 4/25/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps | 480V | AC |  |  | 4/25/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/25/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 4/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 4/25/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2000 | 50708 | 5/17/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other | [5 empty] | 5/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/17/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 5/17/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/17/2001 | Not Challenging | Operate | Operate | 10 | 10 |  |  | Not Challenging
2001 | 50709 | 10/26/2001 | Not Challenging | No | Main Control Room | Control building | Instrument and Uninterruptible Power System | Electrical panel | Other instrument/control cabin | 24‐48VDC | DC |  |  | 10/26/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 10/26/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/26/2001 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
2002 | 50710 | 11/19/2001 | Not Challenging | Yes | N/A | Turbine Building | [7 empty] | 11/19/2001 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  | Leak - Oil soaked Insulation | Unknown | Unknown | Unknown | No Fire ‐ False actuation of detection device | No | [8 empty] | 11/19/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/19/2001 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | [7 empty] | 11/19/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2003 | 50711 | 11/20/2001 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 11/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/20/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 11/20/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/20/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2004 | 50712 | 12/14/2001 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps | 4KV | AC |  |  | 12/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/14/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 12/14/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Other (specify in comments) | [7 empty] | 12/14/2001 | Not Challenging | Operate | Operate | 80 | 80 |  |  | Not Challenging
2005 | 50713 | 1/1/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 1/1/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/1/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 1/1/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/1/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2006 | 50714 | 1/9/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 1/9/2002 | Not Challenging |  | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/9/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 1/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/9/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2007 | 50715 | 1/16/2002 | Not Challenging | No | Main Control Room | Control building |  | Other |  | 110V | AC |  |  | 1/16/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/16/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 1/16/2002 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/16/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2008 | 50716 | 1/24/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Lighting Ballasts |  | 220V | AC |  |  | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/24/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 1/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/24/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2009 | 50717 | 5/21/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 5/21/2002 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No | [8 empty] | 5/21/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 5/21/2002 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/21/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2010 | 50718 | 3/20/2003 | Not Challenging | Yes | N/A |  |  | Electric Motor | Other (specify in comments) | 480V | AC |  |  | 3/20/2003 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/20/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/20/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/20/2003 | Not Challenging | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
2011 | 50719 | 8/1/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 8/1/2003 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/1/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 8/1/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/1/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2012 | 50720 | 8/4/2003 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 8/4/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/4/2003 | Not Challenging | Final | Challenging | [5 empty] | 8/4/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Supervised burn out | Other: Water | [6 empty] | 8/4/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2013 | 50721 | 8/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 8/13/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 8/13/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 8/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2014 | 50722 | 10/10/2003 | Not Challenging | No | N/A | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 10/10/2003 | Not Challenging | Unknown |  |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/10/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/10/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2015 | 50723 | 1/8/2004 | Not Challenging | No | Battery Room | Reactor Building (BWR) | General Ventillation Systems | Other | [5 empty] | 1/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Other (Specify) | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/8/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 1/8/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/8/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2016 | 50724 | 3/5/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electric Motor | Other (specify in comments) |  |  |  |  | 3/5/2004 | Not Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/5/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/5/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | [8 empty] | 3/5/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2017 | 50725 | 3/10/2004 | Not Challenging | No | N/A | Reactor Building (BWR) | Residual Heat Removal/Low Pressure Coolant Injection System (BWR) | Pumps | Electric motor driven pumps |  |  |  |  | 3/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/10/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/10/2004 | Not Challenging |  |  | Unknown | [12 empty] | 3/10/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2018 | 50726 | 10/14/2003 | Not Challenging | No |  | Containment (PWR) |  | Other | [5 empty] | 10/14/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/14/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 10/14/2003 | Not Challenging | 03:15:00 | 03:15:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 10/14/2003 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
2019 | 50727
2020 | 50728 | 1/20/2009 | Potentially Challenging | No | N/A | Turbine Building | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 1/20/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 1/20/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/20/2009 | Potentially Challenging | 19:26:00 | 19:26:00 | Known | 5 | 5 | Roving Firewatch | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 1/20/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
2021 | 50729 | 4/4/2008 | Not Challenging | No | N/A | Other (Specify in comments) | Condensate System | Cable/Wiring | [5 empty] | 4/4/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) |  |  |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/4/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 4/4/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/4/2008 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
2022 | 50730 | 3/1/2006 | Not Challenging | No | N/A | Other (Specify in comments) | [7 empty] | 3/1/2006 | Not Challenging | Unknown |  |  | Other (Specify) | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Unknown | No | [8 empty] | 3/1/2006 | Not Challenging | Final | Challenging | [5 empty] | 3/1/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon | [6 empty] | 3/1/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2023 | 50731 | 2/11/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | 110V | AC |  |  | 2/11/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 2/11/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 2/11/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/11/2005 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2024 | 50732 | 11/7/2002 | Undetermined (NC‐PC) | No | Cable vault/tunnel area | Service Water Pump house |  | Other | [5 empty] | 11/7/2002 | Undetermined (NC‐PC | Mechanical equipment malfunction/failure | Insulation | Type not specified |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/7/2002 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/7/2002 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/7/2002 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2025 | 50733 | 4/23/2004 | Undetermined (NC‐PC) | No |  | Turbine Building |  | Other | [5 empty] | 4/23/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/23/2004 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 4/23/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 4/23/2004 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2026 | 50734
2027 | 50735 | 4/9/2007 | Not Challenging | No | N/A | Containment (PWR) | Cable/Wiring | [6 empty] | 4/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/9/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 4/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 4/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2028 | 50736 | 4/10/2007 | Not Challenging | No |  | Containment (PWR) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 4/10/2007 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/10/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/10/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2029 | 50737
2030 | 50738 | 3/13/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other | [5 empty] | 3/13/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/13/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 3/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention) | [7 empty] | 3/13/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2031 | 50739 | 3/28/2001 | Not Challenging | No | N/A | Control building |  | Electric Motor | Elevator motor |  |  |  |  | 3/28/2001 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) | Leak - Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/28/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 3/28/2001 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2032 | 50740 | 5/16/2000 | Undetermined (NC‐PC) | No | N/A | Circulating Water Pump house/Intake Structure |  | Other | [5 empty] | 5/16/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In_Situ | Other (specify) | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/16/2000 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 5/16/2000 | Undetermined (NC‐PC) | 08:16:00 |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/16/2000 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
2033 | 50741 | 9/18/2000 | Not Evaluated | No |  |  | Feedwater System | Pumps | Electric motor driven pumps |  |  |  |  | 9/18/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 9/18/2000 | Not Evaluated | Final | Potentially Challenging | [5 empty] | 9/18/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown | [7 empty] | 9/18/2000 | Not Evaluated | Operate | Operate | 100 | 100 |  |  | Not Evaluated
2034 | 50742 | 10/4/2006 | Not Challenging | No |  |  |  | Pumps | Electric motor driven pumps |  |  |  |  | 10/4/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/4/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/4/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2035 | 50743 | 7/17/2008 | Not Challenging | No |  |  |  | Pumps | Diesel driven pumps |  |  |  |  | 7/17/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 7/17/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 7/17/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/17/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2036 | 50744 | 8/3/2001 | Potentially Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 8/3/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (specify) |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 8/3/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 8/3/2001 | Potentially Challenging | 18:25:00 |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/3/2001 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
2037 | 50745 | 9/22/2009 | Not Challenging | No |  | Control building |  | Junction Boxes | [5 empty] | 9/22/2009 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/22/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 9/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/22/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2038 | 50746 | 5/6/2001 | Not Challenging | No |  | Turbine Building |  | Other | [24 empty] | 5/6/2001 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 5/6/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | [7 empty] | 5/6/2001 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 |  |  | Not Challenging
2039 | 50747 | 2/9/2007 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 2/9/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 2/9/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2040 | 50748 | 9/22/2000 | Not Challenging | Yes |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 9/22/2000 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/22/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 9/22/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/22/2000 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2041 | 50749 | 10/28/2008 | Challenging | No |  | Other (Specify in comments) |  | Other | [5 empty] | 10/28/2008 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes | [8 empty] | 10/28/2008 | Challenging | Final | Challenging | [5 empty] | 10/28/2008 | Challenging | 20:10:00 | 20:10:00 | Known | 40 | 40 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | [7 empty] | 10/28/2008 | Challenging | Operate | Operate | 100 | 100 | None | Unusual Event | Challenging
2042 | 50750 | 1/10/2001 | Not Evaluated | No |  | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 1/10/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/10/2001 | Not Evaluated | Final | Challenging | [5 empty] | 1/10/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water | [6 empty] | 1/10/2001 | Not Evaluated | Operate | Operate | 100 | 100 |  |  | Not Evaluated
2043 | 50751 | 11/17/2008 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/17/2008 | Not Challenging | Unknown |  |  |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No | [8 empty] | 11/17/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 11/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/17/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2044 | 50752
2045 | 50753 | 12/11/2009 | Not Challenging | No | Main Control Room | Control building |  | Other | Other instrument/control cabin |  |  |  |  | 12/11/2009 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/11/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 12/11/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/11/2009 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2046 | 50754 | 1/23/2009 | Potentially Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  |  | 1/23/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/23/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/23/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/23/2009 | Potentially Challenging | Operate | Operate | 100 | 100 |  |  | Challenging
2047 | 50755
2048 | 50756 | 9/21/2004 | Not Challenging | No | Main Control Room | Reactor Building (BWR) |  | Lighting Ballasts | [5 empty] | 9/21/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/21/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 9/21/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/21/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2049 | 50757 | 9/7/2002 | Not Challenging | No |  | Turbine Building |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 9/7/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/7/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 9/7/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 9/7/2002 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2050 | 50758 | 6/14/2004 | Not Challenging | No |  | Radwaste Building |  | Pumps | Electric motor driven pumps |  |  |  |  | 6/14/2004 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 6/14/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/14/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2051 | 50759 | 7/29/2006 | Not Challenging | No |  | Radwaste Building |  | Lighting Ballasts |  | 110V | AC |  |  | 7/29/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 7/29/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 7/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 7/29/2006 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2052 | 50760 | 11/8/2006 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/8/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/8/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 11/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 11/8/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2053 | 50761 | 1/25/2008 | Not Challenging | No |  | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 1/25/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/25/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 1/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/25/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2054 | 50762 | 10/1/2001 | Not Challenging | No |  | Other (Specify in comments) | General Ventillation Systems | Other | [5 empty] | 10/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/1/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 10/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/1/2001 | Not Challenging | Unknown | Unknown |  |  | None |  | Not Challenging
2055 | 50763 | 11/14/2008 | Undetermined (NC‐PC) | No |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten |  |  |  |  | 11/14/2008 | Undetermined (NC‐PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/14/2008 | Undetermined (NC‐PC) | Final | Undetermined (NC‐PC) | [5 empty] | 11/14/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 11/14/2008 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
2056 | 50764 | 1/14/2004 | Not Challenging | No |  | Other (Specify in comments) |  | Electrical panel | Other (specify in comments) |  |  |  |  | 1/14/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/14/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 1/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2057 | 50765 | 10/12/2004 | Not Challenging | Yes |  | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 110V | AC |  |  | 10/12/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/12/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/12/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/12/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2058 | 50766 | 8/18/2000 | Not Challenging | Yes |  | Control building |  | Other | [5 empty] | 8/18/2000 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment | Spill confined by curbs or other physical feat | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 8/18/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/18/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/18/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2059 | 50767 | 6/1/2001 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 6/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/1/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/1/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2060 | 50768 | 1/1/2002 | Potentially Challenging | No |  | Auxiliary Building (PWR) |  | Electric Motor | Fans |  |  |  |  | 1/1/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/1/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/1/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 1/1/2002 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2061 | 50769 | 12/6/2002 | Not Challenging | No | Main Control Room | Control building |  | Lighting Ballasts | [5 empty] | 12/6/2002 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/6/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 12/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed by maintenance staff (craft activity required) | [7 empty] | 12/6/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2062 | 50770 | 1/30/2003 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 1/30/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/30/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/30/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/30/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2063 | 50771 | 5/6/2003 | Potentially Challenging | No |  | Other (Specify in comments) |  | Dryers | [5 empty] | 5/6/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 5/6/2003 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 5/6/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/6/2003 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2064 | 50772 | 7/2/2003 | Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Transformers | Dry transformer | 480V | AC |  |  | 7/2/2003 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment | Leak - Oil soaked Insulation | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | Severe – room entry not possible without venting or mitigation | Confined to room of origin | [9 empty] | 7/2/2003 | Challenging | Final | Challenging | [5 empty] | 7/2/2003 | Challenging | 10:35:00 | 10:35:00 | Known | 215 | 215 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Hose stream or hose reel，Portable manual system (e.g. CO2 cart)，Multiple portable fire extinguishers，Power supply removed by maintenance staff (craft activity required)，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2，Other: Water | [6 empty] | 7/2/2003 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2065 | 50773 | 9/11/2003 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 9/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/11/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/11/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/11/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2066 | 50774 | 1/7/2004 | Not Challenging | No |  | Turbine Building | Feedwater System | Pumps | Electric motor driven pumps |  |  |  |  | 1/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/7/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 1/7/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | [7 empty] | 1/7/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2067 | 50775 | 2/13/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 2/13/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/13/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 2/13/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2068 | 50776 | 5/6/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | [23 empty] | 5/6/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/6/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2069 | 50777 | 8/5/2004 | Not Challenging | No |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 8/5/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/5/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 8/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/5/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2070 | 50778 | 10/11/2004 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 10/11/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 10/11/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 10/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 10/11/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2071 | 50779 | 10/25/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Circuit breaker or other distribu | 480V | AC |  |  | 10/25/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No | [8 empty] | 10/25/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/25/2004 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 10/25/2004 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2072 | 50780 | 1/6/2005 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 1/6/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/6/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/6/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 1/6/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2073 | 50781 | 3/10/2005 | Not Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 480V | AC |  |  | 3/10/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/10/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/10/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/10/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2074 | 50782 | 3/11/2005 | Not Challenging | No | N/A |  |  | Other |  | N/A | N/A |  |  | 3/11/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/11/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/11/2005 | Not Challenging |  | 10:35:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water | [6 empty] | 3/11/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2075 | 50783 | 6/27/2005 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts | [5 empty] | 6/27/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 6/27/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 6/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 6/27/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2076 | 50784 | 11/20/2005 | Undetermined (NC‐PC) | No | N/A | Other (Specify in comments) |  | Electrical panel | Relay rack |  |  |  |  | 11/20/2005 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/20/2005 | Undetermined (NC‐PC) | Final | Potentially Challenging | [5 empty] | 11/20/2005 | Undetermined (NC‐PC) | 01:53:00 | 01:53:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 11/20/2005 | Undetermined (NC‐PC) | Operate | Operate | 100 | 100 | None |  | Not Challenging
2077 | 50785 | 12/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 12/3/2005 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 12/3/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/3/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2078 | 50786 | 3/10/2006 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 3/10/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 3/10/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/10/2006 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2079 | 50787 | 1/4/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 1/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid |  | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/4/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 1/4/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Water | [6 empty] | 1/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2080 | 50788 | 3/8/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 3/8/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/8/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/8/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2081 | 50789 | 3/4/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Batteries | [5 empty] | 3/4/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/4/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2082 | 50790 | 6/7/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 6/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 6/7/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/4/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2083 | 50791 | 10/25/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 10/25/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/25/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/25/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 10/25/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2084 | 50792 | 11/6/2007 | Not Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 11/6/2007 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/6/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/6/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 11/6/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2085 | 50793 | 11/18/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 11/18/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/18/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/18/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/18/2007 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2086 | 50794 | 3/4/2009 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 3/4/2009 | Not Challenging | Mechanical equipment malfunction/failure | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/4/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/4/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 3/4/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2087 | 50795 | 7/12/2009 | Not Challenging | No | N/A | Turbine Building |  | Lighting Ballasts | [5 empty] | 7/12/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 7/12/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 7/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | [7 empty] | 7/12/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2088 | 50796 | 11/4/2009 | Potentially Challenging | No | N/A | Auxiliary Building (PWR) |  | Other |  | 24‐48VDC | DC |  |  | 11/4/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/4/2009 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/4/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/4/2009 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2089 | 50797 | 11/8/2009 | Not Challenging | No |  |  |  | Other | [5 empty] | 11/8/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/8/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 11/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown | [7 empty] | 11/8/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2090 | 50798 | 12/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/1/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2091 | 50799 | 12/12/2009 | Not Challenging | No | Containment/Drywell | Containment (PWR) |  | Other |  | N/A | N/A |  |  | 12/12/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/12/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 12/12/2009 | Not Challenging |  |  | Known | 365 | 365 | Other plant personnel (in vicinity or passerby) | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 12/12/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2092 | 50800
2093 | 50801
2094 | 50802
2095 | 50803 | 12/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 12/1/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2096 | 50804 | 1/13/2004 | Not Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Load center | 480V | AC |  |  | 1/13/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 1/13/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 1/13/2004 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/13/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2097 | 50805 | 2/12/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 2/12/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 2/12/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 2/12/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 2/12/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2098 | 50806 | 8/30/2004 | Not Challenging | No | N/A | Other (Specify in comments) |  | Generator | Other generator (specify in com |  |  |  |  | 8/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Unknown | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 8/30/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 8/30/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/30/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2099 | 50807 | 8/24/2007 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  |  | 8/24/2007 | Not Challenging | Personnel error during test and maintenance activity | Transient_Gas | Other (specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 8/24/2007 | Not Challenging | Final | Not Challenging | [5 empty] | 8/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 8/24/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2100 | 50808 | 3/21/2006 | Not Challenging | No | Fuel handling area | Reactor Building (BWR) |  | Electrical panel | Other (specify in comments) | 480V | AC |  |  | 3/21/2006 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Other (specify) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/21/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/21/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/21/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2101 | 50809 | 11/9/2000 | Potentially Challenging | No | Cable vault/tunnel area | Reactor Building (BWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  | 110V | AC |  |  | 11/9/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 11/9/2000 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/9/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 11/9/2000 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2102 | 50810 | 6/25/2000 | Not Challenging | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 6/25/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 6/25/2000 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 6/25/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | [7 empty] | 6/25/2000 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2103 | 50811 | 1/9/2001 | Potentially Challenging | No | N/A | Radwaste Building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | 110V | AC |  |  | 1/9/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/9/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/9/2001 | Potentially Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 1/9/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2104 | 50812 | 6/11/2001 | Not Challenging | No | N/A | Other (Specify in comments) | General Ventillation Systems | Other |  | N/A | N/A |  |  | 6/11/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 6/11/2001 | Not Challenging | Final | Not Challenging | [5 empty] | 6/11/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 6/11/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2105 | 50813 | 9/3/2002 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 9/3/2002 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/3/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/3/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/3/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2106 | 50814 | 5/31/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 5/31/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/31/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 5/31/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 5/31/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2107 | 50815 | 5/19/2005 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 5/19/2005 | Not Challenging | Personnel error: Misuse of heating devices | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/19/2005 | Not Challenging | Final | Potentially Challenging | [5 empty] | 5/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/19/2005 | Not Challenging | Operate | Operate | 100 | 1010 | None |  | Not Challenging
2108 | 50816 | 11/16/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 11/16/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/16/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 11/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/16/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2109 | 50817 | 2/13/2006 | Not Challenging | No | N/A | Radwaste Building | Offgas System (BWR) | Other |  | N/A | N/A |  |  | 2/13/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Pressurized in a container | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No | [8 empty] | 2/13/2006 | Not Challenging | Final | Not Challenging | [5 empty] | 2/13/2006 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Air supply cut off (smothered, covered) | [7 empty] | 2/13/2006 | Not Challenging | Operate | Operate | 100 | 100 | Entered an LCO |  | Not Challenging
2110 | 50818 | 3/21/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/21/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/21/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/21/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 3/21/2008 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2111 | 50819 | 6/13/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/13/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | No damageNone or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 6/13/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 6/13/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 6/13/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2112 | 50820 | 10/23/2008 | Potentially Challenging | No | N/A | Turbine Building | Low Voltage Power System (600V and less) | Junction Boxes |  | 480V | AC |  |  | 10/23/2008 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 10/23/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/23/2008 | Potentially Challenging | 16:08:00 | 16:08:00 | Known | 7 | 7 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required) | Portable: Dry Chemical | [6 empty] | 10/23/2008 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2113 | 50821 | 10/30/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/30/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/30/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 10/30/2008 | Potentially Challenging | 12:30:00 | 12:45:00 | Known | 33 | 33 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2 | [6 empty] | 10/30/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2114 | 50822 | 11/7/2008 | Not Challenging | No | Switchgear Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  |  | 11/7/2008 | Not Challenging | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/7/2008 | Not Challenging | Final | Challenging | [5 empty] | 11/7/2008 | Not Challenging | 13:04:00 | 13:04:00 | Known | 48 | 48 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon | [6 empty] | 11/7/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2115 | 50823 | 4/9/2009 | Not Challenging | No | Main Control Room | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Relay rack | 110V | AC |  |  | 4/9/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/9/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/9/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2116 | 50824 | 9/13/2009 | Not Challenging | No | N/A | Other (Specify in comments) |  | Pumps | Electric motor driven pumps |  |  |  |  | 9/13/2009 | Not Challenging | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 9/13/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/13/2009 | Not Challenging |  | 16:20:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/13/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2117 | 50825 | 10/1/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 10/1/2009 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 10/1/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 10/1/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2118 | 50826 | 12/9/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) | General Ventillation Systems | Outlets |  | 110V | AC |  |  | 12/9/2009 | Not Challenging | Personnel error: Misuse of heating devices | In_Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No | [8 empty] | 12/9/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 12/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 12/9/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2119 | 50827 | 4/27/2002 | Not Challenging | No | N/A | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator | 4KV | AC |  |  | 4/27/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/27/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 4/27/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 4/27/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2120 | 50828 | 10/2/2003 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 10/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/2/2003 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 10/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 10/2/2003 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2121 | 50829 | 9/11/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Transformers | Other (Capacitor Voltage, Poten | 13 KV or greater | AC |  |  | 9/11/2004 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 9/11/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/11/2004 | Not Challenging | 00:10:00 | 00:10:00 | Estimated | 45 | 45 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 9/11/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2122 | 50830
2123 | 50831
2124 | 50832
2125 | 50833 | 9/23/2008 | Potentially Challenging | No | N/A | Turbine Building |  | Lighting Ballasts | [5 empty] | 9/23/2008 | Potentially Challenging | Personnel error: Misuse of material ignited | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/23/2008 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 9/23/2008 | Potentially Challenging |  | 04:42:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 9/23/2008 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2126 | 50834 | 9/24/2008 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 9/24/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/24/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 9/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 9/24/2008 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2127 | 50835 | 10/1/2009 | Not Challenging | No | N/A | Turbine Building |  | Other | [5 empty] | 10/1/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/1/2009 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Air supply cut off (smothered, covered) | [7 empty] | 10/1/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2128 | 50836
2129 | 50837 | 7/9/2001 | Not Evaluated | No | N/A | Radwaste Building |  | Electrical panel | Other (specify in comments) | 220V | AC |  |  | 7/9/2001 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Unknown | No | [8 empty] | 7/9/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 7/9/2001 | Not Evaluated | 17:15:00 | 17:15:00 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 7/9/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2130 | 50838 | 11/19/2001 | Not Evaluated | No | N/A |  |  | Other |  | N/A | N/A |  |  | 11/19/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/19/2001 | Not Evaluated | Preliminary | Not Challenging | [5 empty] | 11/19/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/19/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2131 | 50839 | 11/26/2001 | Not Evaluated | No | Fuel handling area | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 11/26/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/26/2001 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 11/26/2001 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 11/26/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2132 | 50840 | 11/28/2001 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 11/28/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/28/2001 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 11/28/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 11/28/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2133 | 50841 | 11/29/2001 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 11/29/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/29/2001 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 11/29/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/29/2001 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2134 | 50842 | 8/23/2002 | Not Evaluated | No | N/A | Reactor Building (BWR) |  | Other |  | N/A | N/A |  |  | 8/23/2002 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 8/23/2002 | Not Evaluated | Preliminary | Undetermined (NC‐PC) | [5 empty] | 8/23/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 8/23/2002 | Not Evaluated | Operate | Operate | 0 | 0 | None |  | Not Evaluated
2135 | 50843 | 3/22/2003 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A | N/A |  |  | 3/22/2003 | Not Evaluated | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/22/2003 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/22/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | [7 empty] | 3/22/2003 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2136 | 50844 | 7/24/2003 | Not Evaluated | No | N/A | Turbine Building | Offgas System (BWR) | Other |  | N/A | N/A |  |  | 7/24/2003 | Not Evaluated | Personnel error during test and maintenance activity | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 7/24/2003 | Not Evaluated | Preliminary | Not Challenging | [5 empty] | 7/24/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 7/24/2003 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2137 | 50845 | 12/13/2003 | Not Evaluated | No |  |  |  | Lighting Ballasts |  | 110V | AC |  |  | 12/13/2003 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No | [8 empty] | 12/13/2003 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 12/13/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown | [7 empty] | 12/13/2003 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2138 | 50846 | 1/24/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A |  |  | 1/24/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/24/2005 | Not Evaluated | Preliminary | Not Challenging | [5 empty] | 1/24/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | [7 empty] | 1/24/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2139 | 50847 | 1/27/2005 | Not Evaluated | No |  |  |  | Outlets | [5 empty] | 1/27/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/27/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 1/27/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown | [7 empty] | 1/27/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2140 | 50848 | 1/30/2005 | Not Evaluated | No |  |  |  | Electric Motor | MG set |  |  |  |  | 1/30/2005 | Not Evaluated | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/30/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 1/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/30/2005 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2141 | 50849 | 3/8/2005 | Not Evaluated | No |  |  |  | Lighting Ballasts | [5 empty] | 3/8/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/8/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 3/8/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 3/8/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2142 | 50850 | 4/1/2005 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Other |  | N/A | N/A |  |  | 4/1/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/1/2005 | Not Evaluated | Preliminary | Not Challenging | [5 empty] | 4/1/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 4/1/2005 | Not Evaluated | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Evaluated
2143 | 50851 | 4/27/2005 | Not Evaluated | No | N/A | Circulating Water Pump house/Intake Structure |  | Pumps | Electric motor driven pumps |  |  |  |  | 4/27/2005 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 4/27/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 4/27/2005 | Not Evaluated | 09:41:00 | 09:41:00 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2 | [6 empty] | 4/27/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2144 | 50852 | 5/25/2005 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin |  |  |  |  | 5/25/2005 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 5/25/2005 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 5/25/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 5/25/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2145 | 50853 | 11/28/2005 | Not Evaluated | No |  |  |  | Other |  | N/A | N/A |  |  | 11/28/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/28/2005 | Not Evaluated | Preliminary | Not Challenging | [5 empty] | 11/28/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 11/28/2005 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2146 | 50854 | 9/18/2006 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 9/18/2006 | Not Evaluated | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 9/18/2006 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 9/18/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)，Fuel supply removed (simple manual action e.g. valve turn off) | [7 empty] | 9/18/2006 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2147 | 50855 | 4/26/2008 | Not Evaluated | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/26/2008 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/26/2008 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 4/26/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | [7 empty] | 4/26/2008 | Not Evaluated | Refueling | Refueling | 0 | 0 | None |  | Not Evaluated
2148 | 50856 | 1/31/2008 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Cable/Wiring | [5 empty] | 1/31/2008 | Not Evaluated | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 1/31/2008 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 1/31/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/31/2008 | Not Evaluated | Operate | Operate | 100 | 100 | None |  | Not Evaluated
2149 | 50857 | 11/6/2009 | Not Evaluated | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 11/6/2009 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/6/2009 | Not Evaluated | Preliminary | Potentially Challenging | [5 empty] | 11/6/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 11/6/2009 | Not Evaluated | Unknown | Unknown |  |  | None |  | Not Evaluated
2150 | 50858
2151 | 50859
2152 | 50860 | 12/14/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/14/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Unknown | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 12/14/2004 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 12/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 12/14/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2153 | 50861 | 12/20/2004 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 12/20/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 12/20/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 12/20/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 12/20/2004 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2154 | 50862 | 2/9/2006 | Not Challenging | No | N/A | Turbine Building |  | Cable/Wiring |  | N/A | N/A |  |  | 2/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage | No | [8 empty] | 2/9/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/9/2006 | Not Challenging |  |  | Unknown |  |  | Roving Firewatch | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 2/9/2006 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2155 | 50863 | 9/30/2008 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 9/30/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/30/2008 | Not Challenging | Final | Not Challenging | [5 empty] | 9/30/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments) | [7 empty] | 9/30/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2156 | 50864 | 9/24/2009 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 9/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 9/24/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 9/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | [7 empty] | 9/24/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2157 | 50865 | 1/31/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 1/31/2000 | Not Challenging | Personnel error: Misuse of material ignited | Transient_Gas |  |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 1/31/2000 | Not Challenging | Final | Not Challenging | [5 empty] | 1/31/2000 | Not Challenging | 10:05:00 | 10:05:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 1/31/2000 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2158 | 50866 | 3/28/2001 | Potentially Challenging | No | N/A | Other (Specify in comments) |  | Lighting Ballasts | [5 empty] | 3/28/2001 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/28/2001 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 3/28/2001 | Potentially Challenging |  | 06:40:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown | [7 empty] | 3/28/2001 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2159 | 50867 | 10/31/2000 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/31/2000 | Not Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/31/2000 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/31/2000 | Not Challenging | 09:45:00 | 09:45:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 10/31/2000 | Not Challenging | Operate | Operate | 0 | 0 | None |  | Not Challenging
2160 | 50868 | 7/3/2001 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 7/3/2001 | Not Challenging | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | No damage | No | [8 empty] | 7/3/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/3/2001 | Not Challenging |  | 21:15:00 | Known | 1289 | 1289 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/3/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2161 | 50869 | 10/25/2001 | Not Challenging | No | N/A | Main Transformer or Switch Yard |  | Transformers | [5 empty] | 10/25/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 10/25/2001 | Not Challenging | Final | Potentially Challenging | [5 empty] | 10/25/2001 | Not Challenging |  | 16:28:00 | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | [7 empty] | 10/25/2001 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2162 | 50870 | 1/8/2002 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/8/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 1/8/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown | [7 empty] | 1/8/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2163 | 50871 | 1/24/2002 | Potentially Challenging | No |  | Reactor Building (BWR) |  | Pumps | Electric motor driven pumps | [23 empty] | 1/24/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 1/24/2002 | Potentially Challenging |  | 17:00:00 | Estimated | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 1/24/2002 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2164 | 50872 | 3/31/2002 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 3/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/31/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/31/2002 | Not Challenging |  | 02:05:00 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 3/31/2002 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
2165 | 50873 | 5/9/2002 | Not Challenging | No |  |  |  | Other |  | N/A | N/A |  |  | 5/9/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In_Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 5/9/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 5/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention) | [7 empty] | 5/9/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2166 | 50874 | 7/12/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electrical panel | Circuit breaker or other distribu |  |  |  |  | 7/12/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 7/12/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 7/12/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | [7 empty] | 7/12/2002 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Challenging
2167 | 50875 | 11/10/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/10/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 11/10/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 11/10/2002 | Not Challenging |  | 17:35:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/10/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2168 | 50876 | 11/13/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Feedwater System | Cable/Wiring | [5 empty] | 11/13/2002 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/13/2002 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 11/13/2002 | Potentially Challenging |  | 03:00:00 | Estimated | 25 | 25 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/13/2002 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2169 | 50877
2170 | 50878 | 11/12/2002 | Potentially Challenging | No |  | Reactor Building (BWR) | Feedwater System | Other |  | N/A | N/A |  |  | 11/12/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/12/2002 | Potentially Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/12/2002 | Potentially Challenging |  | 11:56:00 | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown | [7 empty] | 11/12/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2171 | 50879 | 11/15/2002 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/15/2002 | Not Challenging | Final | Not Challenging | [5 empty] | 11/15/2002 | Not Challenging |  | 04:39:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 11/15/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2172 | 50880 | 11/15/2002 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 11/15/2002 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 11/15/2002 | Not Challenging |  | 10:18:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown | [7 empty] | 11/15/2002 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2173 | 50881 | 12/31/2002 | Not Challenging | No |  | Other (Specify in comments) | DC Power System | Electrical panel | Inverter | 110V | AC |  |  | 12/31/2002 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No | [8 empty] | 12/31/2002 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/31/2002 | Not Challenging |  | 14:25:00 | Estimated | 25 | 25 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | [7 empty] | 12/31/2002 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2174 | 50882 | 1/20/2003 | Not Challenging | No | N/A | Control building | General Ventillation Systems | Other | [5 empty] | 1/20/2003 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 1/20/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 1/20/2003 | Not Challenging |  | 05:44:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 1/20/2003 | Not Challenging | Operate | Operate | 100 | 100 |  |  | Not Challenging
2175 | 50883 | 4/18/2003 | Not Challenging | No |  | Turbine Building |  | Other |  | N/A | N/A |  |  | 4/18/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/18/2003 | Not Challenging | Final | Not Challenging | [5 empty] | 4/18/2003 | Not Challenging |  | 02:25:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher，Air supply cut off (smothered, covered) | Portable: Dry Chemical | [6 empty] | 4/18/2003 | Not Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None |  | Not Challenging
2176 | 50884 | 2/23/2004 | Undetermined (NC‐PC) | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 2/23/2004 | Undetermined (NC‐PC | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 2/23/2004 | Undetermined (NC‐PC) | Final | Challenging | [5 empty] | 2/23/2004 | Undetermined (NC‐PC) |  | 17:00:00 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel | Other: Water | [6 empty] | 2/23/2004 | Undetermined (NC‐PC) | Operate | Operate | 100 | 1010 | None |  | Not Challenging
2177 | 50885 | 6/17/2003 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 6/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 6/17/2003 | Not Challenging | Final | Potentially Challenging | [5 empty] | 6/17/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | [7 empty] | 6/17/2003 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2178 | 50886 | 2/27/2004 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 2/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 2/27/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 2/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water | [6 empty] | 2/27/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2179 | 50887 | 3/7/2004 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 3/7/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/7/2004 | Not Challenging | Final | Not Challenging | [5 empty] | 3/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical | [6 empty] | 3/7/2004 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2180 | 50888 | 7/16/2004 | Not Challenging | No | N/A | Turbine Building |  | Crane |  | N/A | N/A |  |  | 7/16/2004 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 7/16/2004 | Not Challenging | Final | Potentially Challenging | [5 empty] | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 7/16/2004 | Not Challenging | Operate |  | 0 | 0 | None |  | Not Challenging
2181 | 50889 | 3/22/2005 | Not Challenging | No | N/A | Reactor Building (BWR) | Reactor Recirculation System (BWR) | Electrical panel | Circuit breaker or other distribu | 4KV | AC |  |  | 3/22/2005 | Not Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 3/22/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 3/22/2005 | Not Challenging |  | 11:32:00 | Estimated | 2 | 2 | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker) | [7 empty] | 3/22/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2182 | 50890 | 4/3/2005 | Not Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 4/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient_Gas |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/3/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/3/2005 | Not Challenging |  | 02:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/3/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2183 | 50891 | 4/8/2005 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 4/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 4/8/2005 | Not Challenging | Final | Not Challenging | [5 empty] | 4/8/2005 | Not Challenging |  | 10:30:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/8/2005 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2184 | 50892 | 4/12/2005 | Not Challenging | No | Containment/Drywell | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 4/12/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 4/12/2005 | Not Challenging | Final | Undetermined (NC‐PC) | [5 empty] | 4/12/2005 | Not Challenging |  | 12:00:00 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 4/12/2005 | Not Challenging | Refueling | Refueling | 0 | 0 |  |  | Not Challenging
2185 | 50893 | 12/2/2005 | Potentially Challenging | No | N/A | Turbine Building |  | Transformers | Other instrument/control cabin | 480V | AC |  |  | 12/2/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/2/2005 | Potentially Challenging | Final | Potentially Challenging | [5 empty] | 12/2/2005 | Potentially Challenging |  | 00:05:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 12/2/2005 | Potentially Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2186 | 50894 | 3/12/2006 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 3/12/2006 | Not Challenging | Unknown | Gas | Hydrogen |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 3/12/2006 | Not Challenging | Final | Potentially Challenging | [5 empty] | 3/12/2006 | Not Challenging |  | 03:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 12/2/2005 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2187 | 50895 | 5/13/2007 | Potentially Challenging | No | N/A | Turbine Building | [7 empty] | 5/13/2007 | Potentially Challenging | Unknown |  |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No | [8 empty] | 5/13/2007 | Potentially Challenging | Final | Challenging | [5 empty] | 5/13/2007 | Potentially Challenging |  | 03:13:00 | Estimated | 45 | 45 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water | [6 empty] | 5/13/2007 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2188 | 50896 | 5/13/2007 | Undetermined (NC‐PC) | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 5/13/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Leak - Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 5/13/2007 | Undetermined (NC‐PC) | Final | Not Challenging | [5 empty] | 5/13/2007 | Undetermined (NC‐PC) |  | 16:15:00 | Estimated | 85 | 85 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 5/13/2007 | Undetermined (NC‐PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2189 | 50897 | 12/22/2007 | Not Challenging | No |  | Circulating Water Pump house/Intake Structure |  | Generator | Other generator (specify in com | N/A | N/A |  |  | 12/22/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No | [8 empty] | 12/22/2007 | Not Challenging | Final | Potentially Challenging | [5 empty] | 12/22/2007 | Not Challenging |  | 09:30:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | [7 empty] | 12/22/2007 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2190 | 50898 | 2/29/2008 | Not Challenging | Yes | N/A | Other (Specify in comments) |  | Electrical panel | Other instrument/control cabin | [23 empty] | 2/29/2008 | Not Challenging | Final | Potentially Challenging | [5 empty] | 2/29/2008 | Not Challenging |  | 04:06:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2 | [6 empty] | 2/29/2008 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2191 | 50899 | 10/27/2008 | Challenging | No | N/A | Other (Specify in comments) |  | Other |  | N/A | N/A |  |  | 10/27/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Other (specify) | Other (Specify) | Explosion | Unknown | Unknown | Unknown | No | [8 empty] | 10/27/2008 | Challenging | Final | Challenging | [5 empty] | 10/27/2008 | Challenging |  | 02:44:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | [7 empty] | 10/27/2008 | Challenging | Operate | Operate | 100 | 100 | None |  | Challenging
2192 | 50900 | 5/1/2009 | Not Challenging | No | N/A | Drywell (BWR) |  | Other |  | N/A | N/A |  |  | 5/1/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 5/1/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 5/1/2009 | Not Challenging |  | 14:22:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water | [6 empty] | 5/1/2009 | Not Challenging | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2193 | 50901 | 8/28/2009 | Not Challenging | No | N/A | Turbine Building |  | Other |  | N/A | N/A |  |  | 8/28/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No | [8 empty] | 8/28/2009 | Not Challenging | Final | Not Challenging | [5 empty] | 8/28/2009 | Not Challenging |  | 11:33:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | [7 empty] | 8/28/2009 | Not Challenging | Operate | Operate | 100 | 100 | None |  | Not Challenging
2194 | 50907 | 1/9/2010 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Aux. Bldg. Environmental Control System | Electric Motor | Fans |  |  |  | Blowers, compressors, fans, vacuum pumps, cooling units | 1/9/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 1/9/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/9/2010 | Potentially Challenging |  | 19:25:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | [7 empty] | 1/9/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event | Challenging
2195 | 50908 | 1/20/2010 | Challenging |  |  | Other (Specify in comments) | No Industry Std. Name for this system | Generator | Other generator (specify in comme |  |  |  | Generators, inverters, motor generators | 1/20/2010 | Challenging | Mechanical equipment malfunction/failure |  |  |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume |  | Confined to room of origin |  |  | 10 | 10 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal Damage was limited t | 0 ft Vertical, 0 ft Horizontal | 10 ft vertical 10 ft horizontal Damage was limited | 2 ft vertical 2 ft horizontal Fuel Supply - Lube O | 1/20/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage.Potentially Challenging Criteria:Fire Type, Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/20/2010 | Challenging |  | 13:17:00 | 1 |  | 98 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 1/20/2010 | Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2196 | 50909 | 3/7/2010 | Challenging |  |  | Turbine Building | Medium Voltage Power System (601V to 35kV) | Bus Duct | IsoPhase Bus Duct | 13 KV or gre | AC |  | Electrical conductors, bus, cable, wire | 3/7/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Insulation | Type not specified | Single Cable Tray | Explosion | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/7/2010 | Challenging |  | Challenging |  |  |  | Agree with challenging fire classification - however this is a weather-induced event further complicated by the condition of the cracked noryl insulation. | Challenging Criteria: Fire Type,Potentially Challenging Criteria:Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline:No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 3/7/2010 | Challenging |  | 11:16:00 | 1 |  | 0 | Installed Fire detector - Type not specified, Plant employee | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/7/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram | Unusual Event | Challenging
2197 | 50910 | 3/28/2010 | Challenging |  |  | Turbine Building | Normal AC Lighting System | Cable/Wiring |  | 4KV | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 3/28/2010 | Challenging | High Energy Arc Fault (HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to structure of origin |  |  | 25 | 25 | 25 ft Vertical, 25 ft Horizontal extinguishment | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal spacial separation | 25 ft vertical 25 ft horizontal extinguishment | 25 ft vertical 25 ft horizontal extinguishment | 3/28/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Ignition Factor Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/28/2010 | Challenging |  | 18:52:00 | 1 |  | 249 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 3/28/2010 | Challenging | Unknown | Unknown | 0 | 0 | Scram | Alert | Challenging
2198 | 50911 | 4/18/2010 | Potentially Challenging |  |  | Turbine Building | Main Turbine System | Generator | Main turbine generator |  |  |  | Valves, dampers | 4/18/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 |  | 3 | 3 |  |  | 4/18/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Ignition Factor Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/18/2010 | Potentially Challenging |  | 04:00:00 | 2 | 2 | 2 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Supervised burn out |  |  |  | <5 minutes | Initial Suppression Method Successful |  |  | 4/18/2010 | Potentially Challenging | Power Operation | Cold Shutdown | 11 | 0 | Reduced Power |  | Challenging
2199 | 50912 | 5/5/2010 | Challenging |  |  |  | Medium Voltage Power System (601V to 35kV) | Electrical panel | Electric bus bar or bus duct | 4KV | AC |  | Electrical conductors, bus, cable, wire | 5/5/2010 | Challenging | Electrical arcing or sparks (non-HEAF) | Gas | Hydrogen | Ambient pressure, within a component |  | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/5/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Detection Method Suppression Method Potentially Challenging Criteria: First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 5/5/2010 | Challenging |  | 09:39:00 | 1 |  | 211 | Thermal detector (e.g., temperature or rate of rise) | Plant area did not have installed detection capability | Automatic fixed - actuation not specified Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/5/2010 | Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2200 | 50913 | 5/12/2010 | Potentially Challenging |  |  | Turbine Building | Main Generator System | Generator | Main turbine generator |  |  |  | Pipes, fittings, rupture discs | 5/12/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/12/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/12/2010 | Potentially Challenging |  |  | 3 |  | 0 | Plant employee | Unknown | Supervised burn out,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/12/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2201 | 50914 | 6/8/2010 | Potentially Challenging |  | Main Control Room | Control building | Plant Protection System | Electrical panel | Other instrument/control cabinet |  |  |  | Filters, strainers, screens | 6/8/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire was extinguished promptly. | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 6/8/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/8/2010 | Potentially Challenging |  | 11:21:00 | 1 |  | 3 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 6/8/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2202 | 50916 | 7/13/2010 | Potentially Challenging |  | Main Control Room | Control building |  | Electrical panel | Main control board (i.e., the main |  |  |  | Annunciator modules, alarms | 7/13/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/13/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 7/13/2010 | Potentially Challenging |  | 15:49:00 | 1 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 7/13/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2203 | 50917 | 7/13/2010 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 4KV | AC | 1500 | Pumps, eductors | 7/13/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/13/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 7/13/2010 | Potentially Challenging |  | 00:46:00 | 1 |  | 24 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 7/13/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 77 | Reduced Power |  | Challenging
2204 | 50919 | 8/22/2010 | Undetermined (PC‐CH) |  |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Pumps, eductors | 8/22/2010 | Undetermined (PC-CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal The fire was extinguished using a dry chemical extinguisher and | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Proper fire fighting | 0 ft vertical 0 ft horizontal The fire was extingu | 8/22/2010 | Undetermined (PC-CH) |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 8/22/2010 | Undetermined (PC-CH) |  | 15:29:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 8/22/2010 | Undetermined (PC-CH) | Unknown | Unknown | 0 | 0 |  |  | Challenging
2205 | 50921 | 10/11/2010 | Potentially Challenging |  | Cable vault/tunnel area | Other (Specify in comments) | Containment Spray System | Electrical panel | Circuit breaker or other distributio |  |  |  | Circuit breakers, contactors, motor controllers, manual switches | 10/11/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage due to fire. | 0 ft vertical 0 ft horizontal Fire was promptly ex | 0 ft vertical 0 ft horizontal No evidence of secon | 0 ft vertical 0 ft horizontal No smoke damage | 0 ft vertical 0 ft horizontal Fire was extinguishe | 10/11/2010 | Potentially Challenging |  | Undetermined(NC-PC) |  |  | Other | Determined to be PC from event writeup | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/11/2010 | Potentially Challenging |  | 08:24:00 | 1 |  | 7 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/11/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2206 | 50922 | 11/7/2010 | Challenging |  |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors | 11/7/2010 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Contained within component | Explosion | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/7/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Ignition Factor Fire Type Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/7/2010 | Challenging |  | 18:38:00 | 3 |  | 1 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/7/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram |  | Challenging
2207 | 50923 | 12/19/2010 | Undetermined (NC‐PC) |  | Fuel handling area | Other (Specify in comments) | [6 empty] | Control board/panel | 12/19/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal Power to the heater | 0 ft vertical 0 ft horizontal No suppression was u | 0 ft vertical 0 ft horizontal There was no evidenc | 1 ft vertical 1 ft horizontal Power to the heater | 1 ft vertical 1 ft horizontal Power to the heater | 12/19/2010 | Undetermined (NC-PC) |  | Potentially Challenging |  |  |  | Does not appear to be active fire, only smoke. U(NC-PC) because of multiple mentions of fire and active suppression, removing power. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 12/19/2010 | Undetermined (NC-PC) |  | 23:51:00 | 1 |  | 45 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/19/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 |  | Unusual Event | Not Challenging
2208 | 50925 | 2/8/2011 | Potentially Challenging |  |  | Auxiliary Building (PWR) | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) |  |  |  | Annunciator modules, alarms | 2/8/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal Suppression via CO2, | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 2/8/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  | Meets PC criteria OB3 (Page B-3 of EPRI 1025284) for damage beyond initial circuit card as the two adjacent cards were damaged | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 2/8/2011 | Potentially Challenging |  |  | 1 |  | 8 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful |  |  | 2/8/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2209 | 50926 | 2/12/2011 | Challenging |  | Switchgear Room | Other (Specify in comments) | Low Voltage Power System (600V and less) | Electrical panel | Electric bus bar or bus duct | 480V | AC |  | Transformers, shunt reactors | 2/12/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Explosion | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 20 | 20 | 5 ft vertical 2 ft horizontal Phase to phase fault | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 20 ft vertical 20 ft horizontal Smoke affected the | 5 ft vertical 2 ft horizontal When the metallic bu | 2/12/2011 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Fire Type Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 2/12/2011 | Challenging |  | 12:13:00 | 1 |  | 56 | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments)Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 2/12/2011 | Challenging | Startup | Unknown | 20 | 0 |  |  | Challenging
2210 | 50928 | 3/23/2011 | Potentially Challenging |  |  | Control building | No Industry Std. Name for this system | Other |  |  |  |  | Power Tools | 3/23/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/23/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/23/2011 | Potentially Challenging |  | 14:00:00 | 1 |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 3/23/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2211 | 50930 | 3/29/2011 | Potentially Challenging |  | Containment/Drywell | Reactor Building (BWR) | No Industry Std. Name for this system | Other | No breakdown |  |  |  | Vehicle | 3/29/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0.4 | 0.4 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0.4 ft vertical 0.4 ft horizontal Quick detection | 3/29/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/29/2011 | Potentially Challenging |  | 00:56:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/29/2011 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
2212 | 50931 | 5/1/2011 | Potentially Challenging |  |  | Reactor Building (BWR) | Control Rod Drive System | Electric Motor | MG set |  |  |  | Generators, inverters, motor generators | 5/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure |  | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/1/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  | Some uncertainity exists in classification if active intervention was involved "after securing the MG set the fire extinguished without applying any fire suppresant" | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 5/1/2011 | Potentially Challenging |  | 02:44:00 | 1 |  | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/1/2011 | Potentially Challenging | Cold Shutdown | Unknown | 0 | 0 |  |  | Challenging
2213 | 50935 | 6/7/2011 | Challenging |  | Switchgear Room | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Load center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 6/7/2011 | Challenging | Electrical arcing or sparks (non-HEAF) |  | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 12 | 12 | 3 ft vertical 3 ft horizontal Deenergized electric | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12 ft vertical 12 ft horizontal Cabinets and suppr | 6 ft vertical 6 ft horizontal Deenergized electric | 6/7/2011 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/7/2011 | Challenging |  | 09:30:00 | 1 |  | 223 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Gas Ionization | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 6/7/2011 | Challenging | Cold Shutdown | Unknown | 0 | 0 |  | Unusual Event | Challenging
2214 | 50936 | 6/25/2011 | Challenging |  |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 6/25/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Type not specified |  | Arc/electric discharge | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to the object of origin (localized/single subcomponent) | Yes collateral damage occurred | Yes | 4 | 2 | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal THE AREA EFFECTED BY | 0 ft vertical 0 ft horizontal | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 6/25/2011 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Collateral Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Suppression Method Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/25/2011 | Challenging |  | 07:38:00 | 1 |  | 37 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 6/25/2011 | Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event | Challenging
2215 | 50939 | 10/4/2011 | Potentially Challenging |  |  | Auxiliary Building (PWR) |  | Electrical panel | Inverter |  |  |  | Generators, inverters, motor generators | 10/4/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10/4/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/4/2011 | Potentially Challenging |  | 05:55:00 | 1 |  | 6 | Smoke detector | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 10/4/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2216 | 50942 | 11/1/2011 | Potentially Challenging |  |  | Turbine Building | Condensate System | Pumps | Electric motor driven pumps |  |  | 3000 | Motors (electric, hydraulic, pneumatic) | 11/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease |  | Other (specify) | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Separation distance | 0 ft vertical 0 ft horizontal None. No suppression | 0 ft vertical 0 ft horizontal None. | 0 ft vertical 0 ft horizontal Smoke spread from lo | 0 ft vertical 0 ft horizontal Design of motor bear | 11/1/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Smoldering Fire with Moderate Smoke or Temperature Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: Timeline uses known values: 631 minutes Not Challenging Evaluation: | 11/1/2011 | Potentially Challenging |  | 10:26:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/1/2011 | Potentially Challenging | Power Operation | Power Operation | 100 | 90 | Reduced Power |  | Challenging
2217 | 50944 | 11/16/2011 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC |  | Valves, dampers | 11/16/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/16/2011 | Potentially Challenging |  | NC |  |  | Other | Flash seen coming from motor control center. Listed fire type as arc/electrical discharge as that is what was observed. This may have defaulted to a NC, although appears this event is at least PC. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: No criteria met | 11/16/2011 | Potentially Challenging |  | 02:14:00 | 1 |  | 19 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/16/2011 | Potentially Challenging | Cold Shutdown | Cold Shutdown | 0 | 0 | None | Alert | Challenging
2218 | 50945 | 12/21/2011 | Potentially Challenging |  |  | Diesel Generator Building | [6 empty] | Electric heaters | 12/21/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 1 | 2 | 0 ft vertical 0 ft horizontal Fire extinguished wi | 0 ft vertical 0 ft horizontal Suppression system d | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal Very light smoke, no | 1 ft vertical 2 ft horizontal Fire extinguished wi | 12/21/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  | Does not meet T&M override because timeline is greater than 5 minutes. This was complicated by a screw lodged in the starter preventing the contacts from opening. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/21/2011 | Potentially Challenging |  | 10:02:00 | 1 |  | 10 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/21/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 |  |  | Challenging
2219 | 50946 | 1/23/2012 | Potentially Challenging |  | Containment/Drywell | Containment (PWR) | No Industry Std. Name for this system | Electrical panel | Other instrument/control cabinet |  |  |  | Crane, hoist, or lifting device | 1/23/2012 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) |  | Cellulosic materials including wood, paper or other solid transients | Multiple Bundles | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal steel cabinet | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal steel cabinet | 1/23/2012 | Potentially Challenging |  | NC |  |  | Other | There was electrical discharge which resulted in soot deposits and damage internal to cabinet, but self extinguished. Fire was self extinguished, but there was evidence of arcing and tentatively screened in. There are pictures in the cause analysis. | No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 1/23/2012 | Potentially Challenging |  | 17:50:00 | 1 |  | 29 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 1/23/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  | Unusual Event | Challenging
2220 | 50949 | 4/2/2012 | Potentially Challenging |  |  | Auxiliary Building (PWR) | CVC/Makeup and Purification System | Other |  |  |  |  | Pipes, fittings, rupture discs | 4/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) |  | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | No smoke present | Outside area, elevated temperatures only in the fire plume | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/2/2012 | Potentially Challenging |  | Challenging |  |  | Other | 3" flame in outside environment. Likely PC (not CH) | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 4/2/2012 | Potentially Challenging |  | 19:29:00 | 1 |  | 49 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/2/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Unusual Event | Challenging
2221 | 50950 | 5/21/2012 | Undetermined (PC‐CH) |  | Cable vault/tunnel area | Other (Specify in comments) | Medium Voltage Power System (601V to 35kV) | Cable/Wiring | No breakdown | 13 KV or gre | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 5/21/2012 | Undetermined (PC-CH) | Electrical arcing or sparks (non-HEAF) | Insulation | Thermoset | Single Cable | Arc/electric discharge | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 1 | 3 | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Three CO2 extinguish | 0 ft vertical 0 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Fault occurred in an | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w | 5/21/2012 | Undetermined (PC-CH) |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Collateral Damage Suppression Method and Smoke Condition Potentially Challenging Criteria: Heavy Smoke Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/21/2012 | Undetermined (PC-CH) |  | 14:57:00 | 1 |  | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 5/21/2012 | Undetermined (PC-CH) | Power Operation | Hot Shutdown | 100 | 0 | Turbine Trip |  | Challenging
2222 | 50951 | 5/24/2012 | Undetermined (NC‐PC) |  |  | Turbine Building | Feedwater System | Junction Boxes | No breakdown |  |  |  | Motors (electric, hydraulic, pneumatic) | 5/24/2012 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 5 | 3 | 5 ft vertical 3 ft horizontal Electrical fault occ | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 5 ft vertical 3 ft horizontal Electrical fault occ | 5 ft vertical 3 ft horizontal Electrical fault occ | 5/24/2012 | Undetermined (NC-PC) |  | Challenging |  |  |  |  | Challenging Criteria: Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 5/24/2012 | Undetermined (NC-PC) |  | 13:50:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/24/2012 | Undetermined (NC-PC) | Startup | Cold Shutdown | 33 | 0 | Scram |  | Not Challenging
2223 | 50952 | 6/21/2012 | Potentially Challenging |  |  | Turbine Building | Feedwater System | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors | 6/21/2012 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Fire not observed and fire type indeterminate from post‐inspection | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal Insulation was the o | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Detection and dispat | 6/21/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/21/2012 | Potentially Challenging |  | 14:51:00 | 1 |  | 17 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 6/21/2012 | Potentially Challenging | Power Operation | Power Operation | 87 | 62 | Reduced Power | Unusual Event | Challenging
2224 | 50956 | 10/22/2012 | Challenging |  |  | Service Water Pump house | Low Voltage Power System (600V and less) | Electrical panel | Motor control center | 600V | AC |  | Transformers, shunt reactors & Circuit breakers, contactors, motor controllers, manual switches | 10/22/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 | 3 ft vertical 3 ft horizontal Design of the electr | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal Design of the electr | 1 ft vertical 1 ft horizontal Design of the electr | 10/22/2012 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/22/2012 | Challenging |  | 18:46:00 | 1 |  | 22 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 10/22/2012 | Challenging | Power Operation | Power Operation | 100 | 100 | None | Unusual Event | Challenging
2225 | 50968 | 4/18/2012 | Potentially Challenging |  |  | Turbine Building | Hydrogen Supply System | Other |  |  |  |  | Control board/panel | 4/18/2012 | Potentially Challenging | Personnel error during test and maintenance activity | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/18/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  | Agree with PC. Fire was self extinguished but a significant flame of 4-6 feet was observed and had the potential to cause damage if secondary combustibles were nearby. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 4/18/2012 | Potentially Challenging |  | 13:35:00 | 1 |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/18/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2226 | 50969 | 11/11/2012 | Challenging |  |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil-filled Transformer | : Other (specif | AC | 345 | Transformers, shunt reactors | 11/11/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment | Ambient pressure, within a component | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/11/2012 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Fire Type Suppression Method Potentially Challenging Criteria: Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/11/2012 | Challenging |  | 03:56:00 | 1 |  | 162 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Thermal detector (e.g.,temperatur | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful |  |  | 11/11/2012 | Challenging | Power Operation | Hot Shutdown | 100 | 0 | Turbine Trip | Unusual Event | Challenging
2227 | 50977 | 1/8/2013 | Challenging |  |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors | 1/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil |  | Explosion | Outside area, smoke only in fire plume |  | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 40 | 0 | 40 ft vertical 0 ft horizontal Exterior fire | 0 ft vertical 0 ft horizontal None, due to suppres | 0 ft vertical 0 ft horizontal Contained at the tra | 0 ft vertical 0 ft horizontal No smoke damage | 40 ft vertical 0 ft horizontal Exterior Fire | 1/8/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Fire Type Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/8/2013 | Challenging |  | 16:40:00 | 1 |  | 16 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful |  |  | 1/8/2013 | Challenging | Power Operation | Unknown | 100 | 0 | Scram | Unusual Event | Challenging
2228 | 50982 | 12/20/2010 | Challenging |  |  | Turbine Building | Main Generator Output Power System | Electrical panel | Electric bus bar or bus duct |  |  |  | Generators, inverters, motor generators | 12/20/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 12/20/2010 | Challenging |  | Challenging |  |  |  | Challenging, but likely does not fit into an PRA bin. | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/20/2010 | Challenging |  | 00:45:00 | 1 |  | 15 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful |  |  | 12/20/2010 | Challenging | Power Operation | Unknown | 100 | 0 | Scram |  | Challenging
2229 | 50983 | 9/22/2010 | Challenging |  |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil-filled Transformer |  |  |  | Transformers, shunt reactors | 9/22/2010 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire team putting ou | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal Fire team putting ou | 9/22/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/22/2010 | Challenging |  | 21:35:00 | 1 |  | 19 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful | None |  | 9/22/2010 | Challenging | Unknown | Unknown | 0 | 0 | None | Unusual Event | Challenging
2230 | 50985 | 3/26/2012 | Potentially Challenging |  |  | Turbine Building |  | Other | No breakdown |  |  |  | Waste Bin | 3/26/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Unknown | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/26/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 3/26/2012 | Potentially Challenging |  | 22:45:00 | 1 |  | 58 | Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | [8 empty] | 3/26/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2231 | 50986 | 3/28/2010 | Challenging |  |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Pumps, eductors | 3/28/2010 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/28/2010 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- >=10 minutes Suppression Method Potentially Challenging Criteria: Fire Type Fire Suppression Method Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/28/2010 | Challenging |  | 18:18:00 | 1 |  | 184 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/28/2010 | Challenging | Power Operation | Unknown | 100 | 68 | Reduced Power |  | Challenging
2232 | 50992 | 11/17/2010 | Potentially Challenging |  |  | Service Water Pump house | No Industry Std. Name for this system | Other | [5 empty] | 11/17/2010 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/17/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  | Left as PC, but classification hinges on the fire type | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 11/17/2010 | Potentially Challenging |  | 11:00:00 | 3 |  | 0 | Very early smoke detection system (incipient detection) | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 11/17/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2233 | 50994 | 2/13/2013 | Potentially Challenging |  |  | Turbine Building | No Industry Std. Name for this system | Other | No breakdown |  |  |  | Transient Combustible | 2/13/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Acetylene |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 2/13/2013 | Potentially Challenging |  | Potentially Challenging |  |  | Other | Flame observed with personnel injury/burns. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 2/13/2013 | Potentially Challenging |  | 22:05:00 | 1 |  | 2 | Dedicated Fire Watch | [6 empty] | Initial Suppression Method Successful |  |  | 2/13/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2234 | 51002 | 11/10/2010 |  |  | Main Control Room | Control building | Reactor Coolant System | Electrical panel | Main control board (i.e., the main |  |  |  | Motors (electric, hydraulic, pneumatic) | 11/10/2010 | Not Challenging/Undeter | Personnel error during test and maintenance activity | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/10/2010 | Not Challenging/Undeter |  | Undetermined(NC-PC) |  |  | Test and Maintenance | Maintenance Activity Override for at power conditions- Reactor was in Mode 5 undergoing maintenance on a system required for power operations. Reactor coolant pump handswitch began to flame (candle size) when it was switched into the on position during PMT. The flame self extinguished or was blown out by operator in attendance and was limited to the switch. Switch is located on the main control board in the control room. The fire was due to a wiring error during maintenance. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 11/10/2010 | Not Challenging/Undeter |  | 13:58:00 | 1 |  | 1 | Plant employee | Unknown | Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/10/2010 | Not Challenging/Undeter | Refueling | Refueling | 0 | 0 | None
2235 | 51005 | 4/30/2010 | Potentially Challenging |  |  | Turbine Building | No Industry Std. Name for this system | Other |  |  |  |  | Transient Combustible | 4/30/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal No physical suppress | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal The Air Arc Machine | 4/30/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 4/30/2010 | Potentially Challenging |  | 15:35:00 | 1 |  | 4 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/30/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2236 | 51007 | 1/6/2013 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) |  |  |  | Crane, hoist, or lifting device | 1/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1/6/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/6/2013 | Potentially Challenging |  | 09:01:00 | 1 |  | 19 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Staff conducting test/maintenance on equipment of fire origin |  |  |  |  | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful | 1/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2237 | 51013 | 11/29/2010 | Undetermined (NC‐PC) |  |  | Turbine Building | No Industry Std. Name for this system | Other | No breakdown |  |  |  | Transient Combustible | 11/29/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) |  | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/29/2010 | Undetermined (NC-PC) |  | NC |  |  |  | Overrode severity algorithm as there was observed arcing "the collection of debris caused an arc to develop. The debris flashed and burnt rapidly and the fire was self extinguished" which is consistent with EPRI 1025284 Page 5-6 for exclusions for self-extinguished fires. This was a welding/grinding fire that caused a junction box arc. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 11/29/2010 | Undetermined (NC-PC) |  |  | 3 |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/29/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2238 | 51014 | 3/27/2012 | Undetermined (NC‐PC) |  |  |  | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 3/27/2012 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/27/2012 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/27/2012 | Undetermined (NC-PC) |  | 16:49:00 | 1 |  | 2 | Unknown | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/27/2012 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
2239 | 51026 | 3/30/2010 | Potentially Challenging |  |  | Other (Specify in comments) | General Ventillation Systems | Electric Motor | Fans |  |  |  | Blowers, compressors, fans, vacuum pumps, cooling units | 3/30/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 10 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal | 1 ft vertical 1 ft horizontal | 3/30/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/30/2010 | Potentially Challenging |  | 04:20:00 | 1 |  | 6 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/30/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2240 | 51027 | 5/24/2010 | Potentially Challenging |  |  | Reactor Building (BWR) | Fuel Pool Cooling and Purification System | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors | 5/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/24/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/24/2010 | Potentially Challenging |  |  | 2 | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful |  |  | 5/24/2010 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2241 | 51032 | 5/2/2010 | Undetermined (NC‐PC) |  |  | Turbine Building | Turbine Lube Oil System | Pumps |  |  |  |  | Motors (electric, hydraulic, pneumatic) | 5/2/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Arc/electric discharge | Unknown |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The motor casing con | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/2/2010 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  | Not clear this was a fire or pump internal arcing fault that stopped when pump tripped. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/2/2010 | Undetermined (NC-PC) |  |  | 1 |  | 525 | Staff conducting test/maintenance on equipment of fire origin | Unknown | [5 empty] | Initial Suppression Method Successful |  |  | 5/2/2010 | Undetermined (NC-PC) | Power Operation | Power Operation |  |  | None |  | Not Challenging
2242 | 51040 | 4/11/2012 | Challenging |  |  | Turbine Building | Condensate System | [5 empty] | Heat exchanger, condenser, steam generator | 4/11/2012 | Challenging | Hot work (cutting/welding/grinding/etc.) |  |  |  | Unknown | Unknown |  | Confined to part of room or area of origin |  |  | 30 | 10 | 30 ft vertical 10 ft horizontal Acetylene/oxygen b | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Contained mostly ins | 30 ft vertical 10 ft horizontal Damage was limited | 4/11/2012 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/11/2012 | Challenging |  | 18:10:00 | 1 |  | 37 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 4/11/2012 | Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2243 | 51044 | 3/11/2010 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply Building | Other | No breakdown |  |  |  | Room | 3/11/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/11/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/11/2010 | Potentially Challenging |  | 12:20:00 | 11 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Initial Suppression Method Successful |  |  |  |  | Initial Suppression Method Successful |  |  | 3/11/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2244 | 51048 | 3/24/2010 | Potentially Challenging |  |  | Reactor Building (BWR) | [6 empty] | Power Tools | 3/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient |  |  | Flaming combustion – internal to component | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/24/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/24/2010 | Potentially Challenging |  | 01:10:00 | 1 |  | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel Supply Removed,Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/24/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2245 | 51051 | 4/6/2011 | Undetermined (NC‐PC) |  |  | Turbine Building | Main Turbine System | [5 empty] | Transient Combustible | 4/6/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Unknown | Unknown |  | Unknown | Unknown | Unknown | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/6/2011 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/6/2011 | Undetermined (NC-PC) |  | 02:07:00 | 1 |  | 0 |  | Unknown | [5 empty] | Initial Suppression Method Successful |  |  | 4/6/2011 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
2246 | 51057 | 5/2/2011 | Potentially Challenging |  |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 480V | AC |  | Transformers, shunt reactors | 5/2/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Fire confined to tra | 5/2/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/2/2011 | Potentially Challenging |  | 09:54:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/2/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2247 | 51081 | 12/14/2010 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 12/14/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12/14/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/14/2010 | Potentially Challenging |  | 15:00:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments),Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/14/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 |  |  | Challenging
2248 | 51082 | 4/4/2011 | Undetermined (NC‐PC) |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Power Tools | 4/4/2011 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/4/2011 | Undetermined (NC-PC) |  | Potentially Challenging |  |  |  | Fire was apparently small, of unknown duration, and suppression method. May have self suppressed. Otherwise could be considered PC. | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/4/2011 | Undetermined (NC-PC) |  | 04:00:00 | 3 |  | 0 | Plant employee | Unknown | Unknown |  |  |  |  | Initial Suppression Method Successful |  |  | 4/4/2011 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2249 | 51085 | 4/27/2012 | Potentially Challenging |  | Switchgear Room | Turbine Building | DC Power System | Electrical panel | Load center | 250VDC | DC |  | Power Tools | 4/27/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/27/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/27/2012 | Potentially Challenging |  | 10:22:00 | 1 |  | 10 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/27/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2250 | 51088 | 4/5/2011 | Potentially Challenging |  |  | Control building | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators | 4/5/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/5/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  | PC since fixed fire suppression system actuated. Appears fire limited to T&M period since PMT resulted in fire due to wiring error. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/5/2011 | Potentially Challenging |  | 09:39:00 | 1 |  | 10 | Smoke detector, Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 4/5/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2251 | 51090 | 2/15/2013 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure | Low Voltage Power System, Class 1E | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 2/15/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 2/15/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 2/15/2013 | Potentially Challenging |  | 08:59:00 | 1 |  | 9 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 2/15/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2252 | 51092 | 3/20/2013 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Aux. Bldg. Environmental Control System | [5 empty] | Instrument controllers | 3/20/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/20/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  | UE, fire in the auxiliary building supply HVAC unit. A supply unit heater was operating outside of its intended design. Smoke detector activated the pre-action feature of the fixed suppression system but the sprinklers did not heat up enough to discharge. The fire self-extinguished when the unit was de-energized by a plant worker. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/20/2013 | Potentially Challenging |  | 02:12:00 | 1 |  | 48 | Smoke detector, Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/20/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2253 | 51093 | 1/17/2013 | Challenging |  |  | Main Transformer or Switch Yard | Switchyard System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Transformers, shunt reactors | 1/17/2013 | Challenging | Unknown | Liquid | Transformer Oil | Contained within component | Explosion | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin |  |  | 0 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 10 ft horizontal Off site fire depar | 0 ft vertical 0 ft horizontal | 1/17/2013 | Challenging |  | Challenging |  |  |  | Located outside the PA, but in the switchyard. | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Fire Type Extent of Fire Damage Suppression Method Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/17/2013 | Challenging |  | 14:25:00 | 1 |  | 34 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 1/17/2013 | Challenging | Power Operation | Power Operation | 0 | 0 | None |  | Challenging
2254 | 51109 | 10/15/2010 | Undetermined (NC‐PC) |  |  | Turbine Building | No Industry Std. Name for this system | [5 empty] | Transient Combustible | 10/15/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Unknown |  | Confined to the object of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10/15/2010 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  | Many fire event details missing, although fire appears insignificant and unlikely to be of any risk signficance. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/15/2010 | Undetermined (NC-PC) |  |  | 3 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown | [5 empty] | Initial Suppression Method Successful |  |  | 10/15/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2255 | 51111 | 11/2/2010 | Undetermined (NC‐PC) |  |  | Turbine Building | No Industry Std. Name for this system | [5 empty] | Transient Combustible | 11/2/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  |  | Unknown |  | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/2/2010 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/2/2010 | Undetermined (NC-PC) |  |  | 3 |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown |  |  |  |  | Initial Suppression Method Successful |  |  | 11/2/2010 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2256 | 51113 | 10/5/2010 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure | Heat Rejection System (Circulating Water) | Pumps | Electric motor driven pumps | 480V | AC |  | Motors (electric, hydraulic, pneumatic) | 10/5/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10/5/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/5/2010 | Potentially Challenging |  | 08:50:00 | 1 |  | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/5/2010 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2257 | 51117 | 3/11/2013 | Potentially Challenging |  |  | Containment (PWR) | No Industry Std. Name for this system | Other | No breakdown | 110V | AC |  | Power Tools | 3/11/2013 | Potentially Challenging | Personnel error during test and maintenance activity | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/11/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation: | 3/11/2013 | Potentially Challenging |  | 14:50:00 | 2 | 2 | 2 | Other plant personnel (in vicinity or passerby), Plan employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful |  |  | 3/11/2013 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2258 | 51118 | 4/12/2011 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Low Voltage Power System (600V and less) | Electrical panel | Other instrument/control cabinet |  |  |  | 12/31/2011 | 4/12/2011 | Potentially Challenging |  | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/12/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: Timeline uses known values: 4 minutes Not Challenging Evaluation: | 4/12/2011 | Potentially Challenging | 15:20:00 |  | 1 | 4 | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/12/2011 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2259 | 51125 | 12/31/2011 | Potentially Challenging |  |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors | 12/31/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12/31/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/31/2011 | Potentially Challenging |  | 13:25:00 | 1 |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/31/2011 | Potentially Challenging | Power Operation | Power Operation |  |  | None |  | Challenging
2260 | 51132 | 4/2/2012 | Potentially Challenging |  |  | Other (Specify in comments) | Fuel Pool Cooling and Purification System | Electrical panel | Other (specify in comments) |  |  |  | Pumps, eductors | 4/2/2012 | Potentially Challenging | Unknown | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal De-energized compone | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/2/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/2/2012 | Potentially Challenging |  | 16:03:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2261 | 51135 | 3/12/2013 | Undetermined (NC‐PC) |  |  | Other (Specify in comments) | Main/Reheat Steam System |  | No breakdown |  |  |  | Power Tools | 3/12/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/12/2013 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/12/2013 | Undetermined (NC-PC) |  | 10:55:00 | 1 |  | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/12/2013 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2262 | 51136 | 1/19/2011 | Potentially Challenging |  |  | Other (Specify in comments) | Fire Detection System | Other | No breakdown |  |  |  | Power Tools | 1/19/2011 | Potentially Challenging |  | Transient | Temporary electrical wiring or equipment | Single Cable |  | Outside area, smoke only in fire plume |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal isolated location | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1/19/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/19/2011 | Potentially Challenging |  |  | 1 |  | 163 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 1/19/2011 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2263 | 51140 | 11/4/2010 | Potentially Challenging |  |  | Service Water Pump house |  | Pumps | Diesel driven pumps |  |  |  | Pumps, eductors | 11/4/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 11/4/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/4/2010 | Potentially Challenging |  | 09:43:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/4/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2264 | 51146 | 4/3/2013 | Potentially Challenging |  |  | Control building | Low Voltage Power System (600V and less) | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators | 4/3/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Distance of transfor | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No smoke damage. | 0 ft vertical 0.3 ft horizontal Cabinet wall paint | 4/3/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: Timeline uses known values: 20 minutes Not Challenging Evaluation: | 4/3/2013 | Potentially Challenging | 06:32:00 | 07:00:00 | 1 | 20 | 20 | Smoke detector, Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/3/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2265 | 51152 | 4/11/2013 | Challenging |  |  | Turbine Building |  | Boilers | No breakdown |  |  |  | Floor/roof | 4/11/2013 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Other (Specify) |  | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 12 | 5 ft vertical 8 ft horizontal Fire Brigade respons | 30 ft vertical 0 ft horizontal Ground floor floor | 0 ft vertical 2 ft horizontal configuration and lo | 0 ft vertical 0 ft horizontal Origin of fire was o | 8 ft vertical 12 ft horizontal Fire Brigade respon | 4/11/2013 | Challenging |  | Challenging |  |  |  | This is a larger roof fire and associated with the auxiliary boiler building. Might be risk signficant. | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/11/2013 | Challenging |  | 14:55:00 | 1 |  | 113 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful |  |  | 4/11/2013 | Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2266 | 51153 | 1/28/2010 | Potentially Challenging |  |  | Turbine Building | [6 empty] | Transient Combustible | 1/28/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1/28/2010 | Potentially Challenging |  | This event involved poor housekeeping and was limited by the amount of transient combustible material, but could have been worse if additional materials were ignited. Took 9 minutes to extiguish, so PC not HW override seems appropriate. |  |  |  | Potentially Challenging | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/28/2010 | Potentially Challenging |  | 17:20:00 | 1 |  | 9 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | [5 empty] | Initial Suppression Method Successful |  |  | 1/28/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2267 | 51154 | 8/2/2012 | Potentially Challenging |  |  | Turbine Building | Hydrogen Supply System | [5 empty] | Valves, dampers | 8/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 8/2/2012 | Potentially Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Potentially Challenging Criteria: Fire Type First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 8/2/2012 | Potentially Challenging |  | 03:20:00 | 1 |  | 119 | Plant employee | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g valve turn off) |  |  |  |  | Initial Suppression Method Successful |  |  | 8/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2268 | 51157 | 9/20/2010 | Undetermined (NC‐PC) |  |  | Other (Specify in comments) | Yard Handling and Maintenance System | [5 empty] | Transient Combustible | 9/20/2010 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 9/20/2010 | Undetermined (NC-PC) |  | Potentially Challenging |  |  | Outside Protected Are | Generally cigarette butt fires in designated areas are NC. This is not a designated smoking area or butt can fire, but an "inappropriately discarded cigarette butt" per the report. Since the magnitude,and actual location are inconsequntial from a risk perspective, it was classified as Undetermined, i.e. it could be treated as PC or NC. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/20/2010 | Undetermined (NC-PC) |  | 12:00:00 | 1 |  | 0 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 9/20/2010 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2269 | 51158 | 10/4/2012 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 10/4/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10/4/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: Checking Timeline: No Known Time Line Values Unknowns other than time - None Not Challenging Evaluation: | 10/4/2012 | Potentially Challenging |  | 04:00:00 | 1 |  | 3 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered |  |  |  |  | Initial Suppression Method Successful |  |  | 10/4/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2270 | 51160 | 9/25/2010 | Challenging |  |  | Other (Specify in comments) | Hydrogen Supply System | [5 empty] | Pipes, fittings, rupture discs | 9/25/2010 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Ambient pressure, within a compartment | Flaming combustion – external to component | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 9/25/2010 | Challenging |  | Challenging |  |  |  | The location of the fire was not risk signficant, but the fire itself was fairly extensive, although easily extinguished without collateral damage to the area. It could have been more problematic if fire was located elsewhere, therefore CH classification is appropriate. | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation Extent of Fire Damage Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/25/2010 | Challenging |  | 09:35:00 | 1 |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 9/25/2010 | Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2271 | 51162 | 10/10/2010 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | [5 empty] | Transient Combustible | 10/10/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10/10/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation:Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/10/2010 | Potentially Challenging |  | 10:00:00 | 3 |  | 0 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/10/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2272 | 51164 | 9/19/2011 | Undetermined (NC‐PC) |  |  | Turbine Building | Yard Handling and Maintenance System |  | No breakdown |  |  |  | Transient Combustible | 9/19/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  |  | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 9/19/2011 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  | Probable event classifications: 9/19/2011 - NC (proposed) or U 9/20/2011 - PC (proposed) or U 9/20/2011 - NC (proposed) or U 9/23/2011 - NC (proposed) or U | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/19/2011 | Undetermined (NC-PC) |  | 20:00:00 | 3 |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 9/19/2011 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2273 | 51166 | 6/10/2012 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 6/10/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (Specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 6/10/2012 | Potentially Challenging |  | Potentially Challenging |  |  | Hot Work | No fire watch was stationed at the location, although fire watch did observe the fire and extinguish it. Also, fire produced flames 1-2 ft high which are relatively large for a hot work override to apply. | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/10/2012 | Potentially Challenging |  | 16:45:00 | 1 |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 6/10/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2274 | 51168 | 12/3/2012 | Undetermined (NC‐PC) |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 12/3/2012 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12/3/2012 | Undetermined (NC-PC) |  | Potentially Challenging |  |  | Hot Work | Appears to have been hot work error and roving fire watch detected fire, so hot work override does not apply. U(NC-PC) due to uncertainty about fire watch, | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH Determination; Extent Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/3/2012 | Undetermined (NC-PC) |  | 21:45:00 | 1 |  | 0 | Roving Firewatch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 12/3/2012 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2275 | 51171 | 7/13/2012 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 7/13/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/13/2012 | Potentially Challenging |  | Challenging |  |  | Other | Flaming combustion external to initiating component and fire damage to nearby combustibles; but was apparently self limited in extent (cords, bucket, light stick). The employee who detected the fire notified the fire brigade and then extinguished the fire. | Challenging Criteria: Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 7/13/2012 | Potentially Challenging |  | 09:35:00 | 3 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 7/13/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2276 | 51172 | 3/21/2013 | Potentially Challenging |  |  | Turbine Building | Condensate System | Electrical panel | Motor control center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 3/21/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 3/21/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/21/2013 | Potentially Challenging |  | 11:00:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/21/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2277 | 51176 | 5/4/2013 | Potentially Challenging |  |  | Reactor Building (BWR) | Control Rod Drive System | Pumps | Electric motor driven pumps |  |  |  | Governors, couplings, gear boxes | 5/4/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within reservoir | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/4/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  | May also be considered as NC since fire self extinguished after about 7 minutes. However, not clear if pump was turned off before self-extinguished. Also, flame was small (candle flame). | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 5/4/2013 | Potentially Challenging |  | 07:43:00 | 1 |  | 7 | Smoke detector | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/4/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2278 | 51180 | 5/16/2010 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Yard Handling and Maintenance System | Electrical panel | Other instrument/control cabinet |  |  |  | Transient Combustible | 5/16/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Flaming combustion – internal to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 5/16/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  | This is a small and inconsequential fire that seems to have very limited potential to propagate. However, it does not appear to meet any override criteria. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/16/2010 | Potentially Challenging |  | 16:05:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Air supply cut off (smothered, covered |  |  |  |  | Initial Suppression Method Successful |  |  | 5/16/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2279 | 51181 | 9/14/2010 | Potentially Challenging |  |  | Turbine Building | DC Power System | Outlets |  |  |  |  | Batteries, battery chargers | 9/14/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 9/14/2010 | Potentially Challenging |  | Undetermined(NC-PC) |  |  | Other | Battery was discovered arcing to a metal wall and giving off fumes. Battery charger was de-energized. Fire brigade stopped the arcing with a dry chemical extinguisher and moved the battery away from the wall. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/14/2010 | Potentially Challenging |  | 22:22:00 | 3 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 9/14/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2280 | 51184 | 12/2/2011 |  |  |  | Turbine Building | [7 empty] | 12/2/2011 | 12/2/2011 | Hot work (cutting/welding/grinding/etc.) | In_Situ | Structural component |  | Flaming combustion – external to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12/2/2011 | 12/2/2011 |  | Potentially Challenging |  |  | Hot Work | Hor work crew failed to follow area work prep requirements; unknown fire duration, unknown fire suppression. Because the fire was in the roof, it may be considered for NC by location. | Challenging Criteria: Suppression Method and first responder initial attack-- Unknown time entries for first responder time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/2/2011 | 12/2/2011 |  | 13:00:00 | 3 |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | [5 empty] | Initial Suppression Method Successful |  |  | 12/2/2011 | 12/2/2011 | Unknown | Unknown | 0 | 0 | None
2281 | 51186 | 4/20/2013 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | Other | No breakdown |  |  |  | Transient Combustible | 4/20/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (Specify) | Other (Specify) | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/20/2013 | Potentially Challenging |  | Challenging |  |  |  | A worker was welding in a confined space and ignited flammable gas which caused a flash fire. The fire brigade was dispatched but the flammable gas burned off and self extinguished. | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 4/20/2013 | Potentially Challenging |  | 10:00:00 | 1 |  | 0 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/20/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2282 | 51187 | 4/17/2013 | Challenging |  |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers |  | 13 KV or gre | AC |  | Transformers, shunt reactors | 4/17/2013 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Contained within component | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 1 | 2 | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 2 ft horizontal Suppression was conc | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 1 ft horizontal The fire was outside | 1 ft vertical 2 ft horizontal Cable was charred, b | 4/17/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Ignition Factor Extent of Fire Damage Collateral Damage Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/17/2013 | Challenging |  | 20:29:00 | 1 |  | 7 | Main control room staff (e.g.,control/instrumentation failures), Plant employee,Failed Equipment A | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel,Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/17/2013 | Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2283 | 51188 | 5/20/2013 | Undetermined (PC‐CH) |  |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Pumps, eductors | 5/20/2013 | Undetermined (PC-CH) | Mechanical equipment malfunction/failure | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 5/20/2013 | Undetermined (PC-CH) |  | Challenging |  |  |  | Turbine Aux Oil Pump motor tripped, motor windings were on fire. This resulted in plant shutdown because of the loss of the aux oil pump. Fire brigade extinguished the fire with several CO2 extinguishers. | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Suppression Method and Smoke Condition Potentially Challenging Criteria: Fire Type Heavy Smoke Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/20/2013 | Undetermined (PC-CH) |  | 03:50:00 | 1 |  | 27 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful |  |  | 5/20/2013 | Undetermined (PC-CH) | Startup | Hot Shutdown |  | 0 | Reduced Power |  | Challenging
2284 | 51190 | 4/2/2012 | Potentially Challenging |  | Battery Room |  | Instrument and Uninterruptible Power System | Electrical panel | Inverter | 110V | AC |  | Generators, inverters, motor generators | 4/2/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/2/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/2/2012 | Potentially Challenging |  | 06:24:00 | 1 |  | 9 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/2/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2285 | 51191 | 4/27/2013 | Potentially Challenging |  |  | Turbine Building |  | Generator | Main turbine generator |  |  |  | Transient Combustible | 4/27/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Transformer Oil |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 4/27/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/27/2013 | Potentially Challenging |  | 10:10:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/27/2013 | Potentially Challenging | Power Operation | Hot Shutdown |  | 0 | Scram |  | Challenging
2286 | 51193 | 5/21/2013 | Potentially Challenging |  |  | Radwaste Building | Administration Building | Other | No breakdown |  |  |  | Transient Combustible | 5/21/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Other (Specify) | Other (Specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 5/21/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 5/21/2013 | Potentially Challenging |  | 21:59:00 | 1 |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 5/21/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2287 | 51194 | 7/2/2013 | Challenging |  |  | Turbine Building | Low Voltage Power System (600V and less) | Electrical panel | Electric bus bar or bus duct | 13 KV or gre | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 7/2/2013 | Challenging | High Energy Arc Fault (HEAF) | In_Situ | Interior finish |  | Arc/electric discharge | No smoke present |  | Confined to the object of origin (broad/extensive damage) | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/2/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Ignition Factor Collateral Damage Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 7/2/2013 | Challenging |  | 20:26:00 | 1 |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 7/2/2013 | Challenging | Power Operation | Unknown | 100 | 60 | Reduced Power |  | Challenging
2288 | 51196 | 7/11/2013 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators | 7/11/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/11/2013 | Potentially Challenging |  | Potentially Challenging |  |  | Diesel Exhaust | Does not meet all diesel exhaust override conditions: flame size, length, oil soked insulation. Pic shows damage. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation: | 7/11/2013 | Potentially Challenging |  | 10:29:00 | 2 | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  | <5 minutes | Initial Suppression Method Successful |  |  | 7/11/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2289 | 51199 | 7/26/2013 | Challenging |  |  | Main Transformer or Switch Yard | Main Generator Output Power System | Transformers | Oil-filled Transformer | 13 KV or gre | AC |  | Generators, inverters, motor generators | 7/26/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 20 | 30 ft vertical 20 ft horizontal The arc flash thre | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal The arc flash threw | 30 ft vertical 20 ft horizontal Smoke was moderate | 30 ft vertical 20 ft horizontal The arc flash thre | 7/26/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 7/26/2013 | Challenging |  | 23:35:00 | 1 |  | 33 | Smoke detector, Other plant personnel (in vicinity or passerby), Failed Equipment Alarm (Tripped pum | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 7/26/2013 | Challenging | Power Operation | Unknown | 100 | 0 | Turbine Trip |  | Challenging
2290 | 51201 | 2013-08-08 | Challenging |  |  | Auxiliary Building (PWR) | Medium Voltage Power System (601V to 35kV) |  |  | 480V | AC |  | Transformers, shunt reactors | : 8/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Damage was confined | 0 ft vertical 0 ft horizontal Damage was confined | : 8/8/2013 | Challenging |  | Undetermined(NC-PC) |  |  | Other | Photos show signifcant electric arc/discharge damage. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 2 minutes Not Challenging Evaluation: | : 8/8/2013 | Challenging |  | 03:00:00 | 2 | 2 | 2 | Plant employee, Very early smoke detection system,(incipient detection), Main control room staff (e. | Plant area had installed detection which did not actuate, fire was detected visually or by other means – system failure indicated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful |  |  | : 8/8/2013 | Challenging | Power Operation | Power Operation | 100 | 92 | Reduced Power |  | Challenging
2291 | 51207 | 9/2/2013 | Potentially Challenging |  |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Turbines (steam, gas) | 9/2/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – external to component | Unknown |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 9/2/2013 | Potentially Challenging |  | Challenging |  |  |  | Smoke was coming from the A Main Feedwater Pump. AUO reported flames from the lagging on the turbine side of the pump. Oil soaked the lagging which ignited under operating heat. The fire brigade extinguished the fire with multiple fire extinguishers. Typical fire from oil soaked lagging. | Challenging Criteria: Suppression Method and fire brigade initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type Fire Suppression Method Fire Brigade and >=30 minutes Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values This Record Uses Estimated Time Line Values: 25 minutes | 9/2/2013 | Potentially Challenging |  | 19:22:00 | 2 | 25 | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers |  |  |  | 20 to <30 minu | Initial Suppression Method Successful |  |  | 9/2/2013 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2292 | 51209 | 7/31/2013 | Undetermined (NC‐PC) |  |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Electrical panel | Other (specify in comments) | 110V | AC |  | Transformers, shunt reactors | 7/31/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | In_Situ | Other (Specify) |  | Fire not observed and fire type indeterminate from post‐inspection | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 7/31/2013 | Undetermined (NC-PC) |  | NC |  |  | Other | Although apparently self extinguished, the nature and duration of the fire was not known. There was possible fire damage to wiring near the fire ignition source. Therefore, although fire was localized, some evidence of spreading occurred. Since the fire self extinguished without signficant spread, it could be PC or NC. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; 20 Suppression Method Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 7/31/2013 | Undetermined (NC-PC) |  | 13:02:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown,Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 7/31/2013 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2293 | 51216 | 1/3/2010 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure |  | Electrical panel | Other instrument/control cabinet |  |  |  | Bistable, switch (mechanical, electronic) | 1/3/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | [7 empty] | 1/3/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  | May also be considered as U(NC-PC) due to unknown fire size, but stated as small, limited damage, unknown time line, and single fire extinguisher used for suppression. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/3/2010 | Potentially Challenging |  |  | 3 |  |  | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 1/3/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2294 | 51219 | 2/12/2010 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators | 2/12/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 2/12/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 2/12/2010 | Potentially Challenging |  | 02:30:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 2/12/2010 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2295 | 51220 | 3/26/2010 | Undetermined (NC‐PC) |  |  | Turbine Building | No Industry Std. Name for this system | Other |  |  |  |  | Electric heaters | 3/26/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 3/26/2010 | Undetermined (NC-PC) |  | Potentially Challenging |  |  | Other | Event appears to be more smoldering and arcing which occurred under the purview of the dedicated fire watch and then fire brigade as the fire was extinguished by removing power. Small flame noted, associated with tape, and event suppression exceeded 5 min for hot work override. Thus could be PC. However, small flame was momentary and fire watch oversight could be considered fire control as the primary observations were smoke and some sparking. Thus NC is also considered. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/26/2010 | Undetermined (NC-PC) |  | 22:45:00 | 1 |  | 25 | Dedicated Fire Watch | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/26/2010 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2296 | 51221 | 7/20/2011 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Engines (gas, diesel) | 7/20/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 7/20/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 7/20/2011 | Potentially Challenging |  | 13:19:00 | 1 |  | 17 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 7/20/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2297 | 51222 | 10/12/2011 | Challenging |  | Cable vault/tunnel area | Turbine Building | Low Voltage Power System (600V and less) | Cable/Wiring |  |  |  |  | Electrical conductors, bus, cable, wire | 10/12/2011 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 10/12/2011 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Collateral Damage Potentially Challenging Criteria: Fire Type 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/12/2011 | Challenging |  | 05:30:00 | 1 |  | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/12/2011 | Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2298 | 51231 | 4/7/2014 | Undetermined (NC‐PC) |  |  | Other (Specify in comments) | Yard Handling and Maintenance System | Other |  |  |  |  | Vehicle | 4/7/2014 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 3 | 3 | 2 ft Vertical, 2 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 2 ft Vertical, 2 ft Horizontal | 3 ft Vertical, 3 ft Horizontal | 4/7/2014 | Undetermined (NC-PC) |  | Potentially Challenging |  |  |  | Somewhat limited applicability as a transient fire igntion source. U(NC-PC) due to uncertainty about applicability due to location. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/7/2014 | Undetermined (NC-PC) |  | 09:43:00 | 1 |  | 4 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/7/2014 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 |  |  | Not Challenging
2299 | 51254 | 10/13/2012 | Potentially Challenging |  |  | Turbine Building | Aux. Bldg. Environmental Control System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic) | 10/13/2012 | Potentially Challenging |  | In_Situ | Temporary thermal insulation materials |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Small fire involving motor windings no damage to other compo | 0 ft Vertical, 0 ft Horizontal Suppressed by opening breaker, no other actions required | 0 ft Vertical, 0 ft Horizontal No secondary ignition noted | 0 ft Vertical, 0 ft Horizontal Light smoke produced, ventilation in turbine building | 0 ft Vertical, 0 ft Horizontal No adjacent components exposed to heat. | 10/13/2012 | Potentially Challenging |  | Undetermined(NC-PC) |  |  |  | Fire lasted about 10 minutes and pump had to be replaced. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/13/2012 | Potentially Challenging |  | 14:15:00 | 1 |  | 10 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 10/13/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 |  |  | Challenging
2300 | 51256 | 6/13/2013 | Undetermined (NC‐PC) |  | Switchgear Room | Reactor Building (BWR) | Medium Voltage Power System, Class 1E | Electrical panel | Switchgear |  |  |  | Circuit breakers, contactors, motor controllers, manual switches | 6/13/2013 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 6/13/2013 | Undetermined (NC-PC) |  | NC |  |  |  | Extent of damage appears to be localized to single breaker due to arcing with no subsequent fire; could also be NC. Investigation revealed evidence of a significant arcing fault in the 13.8 kV Bus 11 cubicle. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 6/13/2013 | Undetermined (NC-PC) |  | 14:31:00 | 1 |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 6/13/2013 | Undetermined (NC-PC) | Cold Shutdown | Cold Shutdown | 0 | 0 | LOOP |  | Not Challenging
2301 | 51257 | 5/16/2011 | Potentially Challenging |  | Switchgear Room |  | Medium Voltage Power System (601V to 35kV) | Electrical panel | Motor control center |  |  |  | Circuit breakers, contactors, motor controllers, manual switches | 5/16/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 5/16/2011 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH and PC Determination; Smoke Condition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/16/2011 | Potentially Challenging |  | 10:00:00 | 3 |  |  |  | Unknown | [5 empty] | Initial Suppression Method Successful |  |  | 5/16/2011 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2302 | 51258 | 7/10/2013 | Challenging |  |  | Turbine Building | No Industry Std. Name for this system | Lighting Ballasts |  |  |  |  | Illumination source | 7/10/2013 | Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment | Type not specified | Flaming combustion – external to component | No smoke present |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 7/10/2013 | Challenging |  | Challenging |  |  |  | Meets definition of challenging, but was relatively small and inconsequential fire. | Challenging Criteria: Extent of Fire Damage Collateral Damage Potentially Challenging Criteria: Fire Type First Responder and >=30 minutes Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 7/10/2013 | Challenging |  | 01:00:00 | 1 |  | 60 | Plant employee | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 7/10/2013 | Challenging | Unknown | Unknown | 0 | 0 |  |  | Challenging
2303 | 51265 | 8/24/2012 | Potentially Challenging |  | Containment/Drywell | Containment (PWR) | Low Voltage Power System (600V and less) | Cable/Wiring |  |  |  |  | Electrical conductors, bus, cable, wire | 8/24/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 8/24/2012 | Potentially Challenging |  | Potentially Challenging |  |  | Meets definition of challenging, but was relatively small and inconsequential fire. |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 8/24/2012 | Potentially Challenging |  | 04:50:00 | 1 |  | 1 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful |  |  | 8/24/2012 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2304 | 51273 | 4/2/2013 | Undetermined (NC‐PC) |  |  | Main Transformer or Switch Yard | Medium Voltage Power System (601V to 35kV) | Transformers |  |  |  |  | Transformers, shunt reactors | 4/2/2013 | Undetermined (NC-PC) | Human Error | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 5 | 5 | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal No suppression required. Fire self-extinguished with loss of po | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 4/2/2013 | Undetermined (NC-PC) |  | NC |  |  |  | Arc flash large enough to burn employees in vicinity conducting maintenance activity: borderline PC or NC | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished | 4/2/2013 | Undetermined (NC-PC) |  | 17:07:00 | 1 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/2/2013 | Undetermined (NC-PC) | Power Operation | Power Operation | 100 | 100 | None |  | Not Challenging
2305 | 51274 | 12/9/2012 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Load center |  |  |  | 21 | 12/9/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 12/9/2012 | Potentially Challenging |  | Undetermined(NC-PC) |  |  |  | The extent of damage seems significant within the load center to be potentially damaging if not terminated in a timely manner. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/9/2012 | Potentially Challenging |  | 05:00:00 | 3 |  |  | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/9/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2306 | 51276 | 8/14/2013 | Potentially Challenging |  | Fuel handling area | Reactor Building (BWR) | [6 empty] | Reactor Building (BWR) | 8/14/2013 | Potentially Challenging | Human Error | Gas | Hydrogen | Ambient pressure, within a compartment | Explosion | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 8/14/2013 | Potentially Challenging |  | Challenging |  |  |  | Changed to PC from CH as magnitude of the "deflagration" was not sufficient to damage other equipment nearby. | Challenging Criteria: Fire Type Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 8/14/2013 | Potentially Challenging |  | 16:15:00 | 1 |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful |  |  | 8/14/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2307 | 51278 | 11/5/2013 | Challenging |  |  |  | Medium Voltage Power System, Class 1E | Cable/Wiring |  | 4KV | AC |  | Electrical conductors, bus, cable, wire | 11/5/2013 | Challenging | Electrical failure resulting in overheating materials | Insulation | Cable Tray Stack | Type not specified | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | Vertical Distance (ft): 3.00 | Vertical Distance (ft): 3.00 | Damage limited to |  |  | Vertical Distance (ft): 7.00; Horizontal Distance (ft): 80.00 | Vertical Distance (ft): 3.00; Horizontal Distance (ft): 5.0 | 11/5/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/5/2013 | Challenging |  | 17:48:00 | 1 |  | 42 | Sprinkler or fire-water system flow alarm | Plant area did not have installed detection capability | Automatic fixed - thermally actuated |  |  |  |  | Initial Suppression Method Successful |  |  | 11/5/2013 | Challenging | Power Operation | Unknown | 0 | 0 | Turbine Trip | Unusual Event | Challenging
2308 | 51280 | 12/21/2014 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure |  | Pumps |  |  |  |  | Electric heaters | 12/21/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Lube Oil or Grease | Other (Specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 12/21/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/21/2014 | Potentially Challenging |  | 09:15:00 | 3 |  |  | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/21/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2309 | 51287 | 10/6/2013 | Potentially Challenging |  |  | Main Transformer or Switch Yard | Switchyard System | Electrical panel | Other (specify in comments) |  |  |  | Control board/panel | 10/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 10/6/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  | T/M override does not appear to apply as testing was not PMT | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/6/2013 | Potentially Challenging |  | 16:00:00 | 1 |  | 3 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2310 | 51289 | 10/26/2013 | Potentially Challenging |  |  | Circulating Water Pump house/Intake Structure | [6 empty] | Electric heaters | 10/26/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In_Situ | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 10/26/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/26/2013 | Potentially Challenging |  | 08:15:00 | 1 |  | 6 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 10/26/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2311 | 51291 | 12/9/2013 | Challenging |  |  | Turbine Building | Main Generator Output Power System | Transformers | Other (Capacitor Voltage, Potential | 7KV | AC |  | Transformers, shunt reactors | 12/9/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume |  | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 50 | 20 | 50 ft Vertical, 20 ft Horizontal Transformer fire outdoors, concrete separation walls betwe | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal |  |  | 12/9/2013 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/9/2013 | Challenging |  | 07:48:00 | 1 |  | 89 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful |  |  | 12/9/2013 | Challenging | Power Operation | Unknown | 0 | 0 | Scram | Unusual Event | Challenging
2312 | 51293 | 11/6/2013 | Potentially Challenging |  |  | Turbine Building | [6 empty] | Room | 11/6/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 11/6/2013 | Potentially Challenging |  | Challenging |  |  |  | Because of the magnitude of the fire and possible time line, hot work override may not apply. However, the fire watch did see the fire at its start and extinguished it before the fire brigade arrived and declared to fire extinguished (10 min). PC classification due to limited CH potential. | Challenging Criteria: Suppression Method and first responder initial attack-- >=10 minutes Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/6/2013 | Potentially Challenging |  | 20:10:00 | 1 |  | 10 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 11/6/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2313 | 51295 | 11/1/2013 | Potentially Challenging |  |  | Turbine Building | Feedwater System | Pumps | Turbine-driven pump |  |  |  | Transient Combustible | 11/1/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Other (Specify) | Leak - Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 11/1/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/1/2013 | Potentially Challenging |  | 20:56:00 | 1 |  | 134 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | [5 empty] | Initial Suppression Method Successful |  |  | 11/1/2013 | Potentially Challenging | Power Operation | Unknown | 50 | 0 | Reduced Power |  | Challenging
2314 | 51296 | 11/30/2013 | Potentially Challenging |  |  | Turbine Building |  | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic) | 11/30/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 11/30/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  | Fire occurred during routine T/M, but not PMT required for T/M override | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 11/30/2013 | Potentially Challenging |  | 13:50:00 | 1 |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 11/30/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2315 | 51304 | 1/18/2014 | Potentially Challenging |  |  | Auxiliary Building (PWR) |  | Electrical panel | Inverter | 250VDC | DC | 50 | Generators, inverters, motor generators | 1/18/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Temporary thermal insulation materials |  | Fire not observed and fire type indeterminate from post‐inspection | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. no secondary i | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. No damage be | 1/18/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 1/18/2014 | Potentially Challenging |  | 03:45:00 | 1 |  | 26 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 1/18/2014 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | Entered an LCO | Unusual Event | Challenging
2316 | 51308 | 4/7/2012 | Potentially Challenging |  |  | Reactor Building (BWR) |  | Other |  |  |  |  | Crane, hoist, or lifting device | 4/7/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 4/7/2012 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/7/2012 | Potentially Challenging |  | 08:00:00 | 1 |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/7/2012 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2317 | 51309 | 3/7/2014 | Potentially Challenging |  |  |  |  | Electrical panel | Load center | 480V | AC |  | Circuit breakers, contactors, motor controllers, manual switches | 3/7/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 3/7/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  | The substation is panel located within the protected area. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 3/7/2014 | Potentially Challenging |  | 04:55:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/7/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2318 | 51310 | 4/17/2014 | Potentially Challenging |  |  | Turbine Building | Yard Handling and Maintenance System | Other |  |  |  |  | Transient Combustible | 4/17/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 4/17/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/17/2014 | Potentially Challenging |  | 11:00:00 | 1 |  | 2 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/17/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2319 | 51315 | 3/20/2014 | Potentially Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Generator | Class 1A emergency generator |  |  |  | Generators, inverters, motor generators | 3/20/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Lube Oil or Grease | Other (Specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 3/20/2014 | Potentially Challenging |  | Potentially Challenging |  |  | Test and Maintenance | Fire occurred during trouble shooting of components that had failed previously. T&M staff was fully prepared, small fire, detected and suppressed fire immediately. PC per NRC review: Known condition appears to be pre-existing to the M&T on 3/20/14. EDG was run previously with this condition; smoke observed. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 3/20/2014 | Potentially Challenging |  | 14:01:00 | 1 |  | 5 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/20/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None | Alert | Challenging
2320 | 51316 | 4/12/2014 | Potentially Challenging |  |  | Containment (PWR) | No Industry Std. Name for this system | Other |  |  |  |  | Power Tools | 4/12/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 4/12/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: Self extinguished Conflicting Data Entries Check Field 20.m | 4/12/2014 | Potentially Challenging |  | 22:00:00 | 1 |  | 1 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 4/12/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0 |  |  | Challenging
2321 | 51317 | 4/2/2014 | Challenging |  |  | Turbine Building | Instrument and Uninterruptible Power System | Cable/Wiring |  |  |  |  | Pipes, fittings, rupture discs | 4/2/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Single Cable Tray | Type not specified | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | -1 | -1 | 10 | 10 | 2 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 2 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 10 ft Vertical, 10 ft Horizontal fire suppression equipment put out fire quickly to prevent fu | 4 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 4/2/2014 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage Detection Method Suppression Method Potentially Challenging Criteria: Fire Type Heavy Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/2/2014 | Challenging |  | 12:47:00 | 1 |  | 91 | Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Automatic fixed - thermally actuated |  |  |  |  | Initial Suppression Method Successful |  |  | 4/2/2014 | Challenging | Startup | Hot Shutdown | 0 | 0 | Scram | Alert | Challenging
2322 | 51318 | 4/3/2014 | Potentially Challenging |  |  | Main Transformer or Switch Yard | Low Voltage Power System (600V and less) | Other |  | 480V | AC |  | Electronic power supply | 4/3/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal The 480VAC connector was located outside of the building. All | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 4/3/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: Suppression Method and fire brigade initial attack-- Unknown time entries for fire brigade time evaluation No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/3/2014 | Potentially Challenging |  | 13:55:00 | 1 |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/3/2014 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2323 | 51322 | 6/19/2014 | Undetermined (NC‐PC) |  |  | Diesel Generator Building | No Industry Std. Name for this system | Other |  |  |  |  | Crane, hoist, or lifting device | 6/19/2014 | Undetermined (NC-PC) |  | Transient | Other (Specify) |  | Flaming combustion – internal to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 6/19/2014 | Undetermined (NC-PC) |  | Potentially Challenging |  |  | Other | Not clear if fire occurred when equipment was powered up and if staff using eguipment detected and suppressed (removed power) fire. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Ignition Unknown CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 6/19/2014 | Undetermined (NC-PC) |  | 15:26:00 | 1 |  | 0 | Plant employee | Plant area did not have installed detection capability | [5 empty] | Initial Suppression Method Successful |  |  | 6/19/2014 | Undetermined (NC-PC) | Unknown | Unknown | 0 | 0 | None |  | Not Challenging
2324 | 51324 | 5/23/2014 | Potentially Challenging |  |  | Auxiliary Building (PWR) | Low Voltage Power System, Class 1E | Electrical panel | Inverter |  |  |  | Transformers, shunt reactors | 5/23/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  |  | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | -1 | -1 | 1 | 1 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 1 ft Horizontal Quick Fire brigade response. | 0.25 ft Vertical, 0 ft Horizontal Fire was limited to inside of the 3KI inverter. The metal cabi | 5/23/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 5/23/2014 | Potentially Challenging |  | 19:41:00 | 1 |  | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 5/23/2014 | Potentially Challenging | Power Operation | Power Operation | 100 | 100 | None |  | Challenging
2325 | 51328 | 7/27/2014 | Potentially Challenging |  |  | Service Water Pump house | Essential Service Water System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic) | 7/27/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 7/27/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: 2 of 3 Criteria; Detection, Power Effect, Time Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 7/27/2014 | Potentially Challenging |  | 12:44:00 | 1 |  | 15 | Smoke detector | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful |  |  | 7/27/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2326 | 51331 | 9/4/2014 | Potentially Challenging |  |  | Diesel Generator Building |  | Electrical panel | Other (specify in comments) |  |  |  | Control board/panel | 9/4/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 9/4/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  | Although fire occurred during trouble shooting with fire watch in attendance, conditions were such that fire could have occurred during other periods when maintenance was not being performed. The initial test was a performance test of Appendix R Isolation Sequence. This may or may not have been a maintenance test, but does not appear to be related to the specifics of the subsequent fire. | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/4/2014 | Potentially Challenging |  | 10:10:00 | 1 |  | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 9/4/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2327 | 51332 | 10/6/2014 | Challenging |  |  | Diesel Generator Building | Emergency Onsite Power Supply System | Electrical panel | Other instrument/control cabinet |  |  |  | Control board/panel | 10/6/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to part of room or area of origin | -1 | -1 | 8 | 3 | 1 ft Vertical, 1 ft Horizontal Fire immediately extinguished by site operator in room with po | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 8 ft Vertical, 3 ft Horizontal Fire initiated in closed electrical component control cabinet. S | 2 ft Vertical, 2 ft Horizontal Fire immediately extinguished by site operator in room with po | 10/6/2014 | Challenging |  | Challenging |  |  |  |  | Challenging Criteria: Extent of Fire Damage Potentially Challenging Criteria: Fire Type Power Supply removed and Moderate Smoke Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 10/6/2014 | Challenging |  | 13:26:00 | 1 |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 10/6/2014 | Challenging | Power Operation | Power Operation | 100 | 100 | Entered an LCO | Alert | Challenging
2328 | 51335 | 9/15/2014 | Potentially Challenging |  |  | Other (Specify in comments) | No Industry Std. Name for this system | Other |  |  |  |  | Manual Tools | 9/15/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Type not specified | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord | 9/15/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/15/2014 | Potentially Challenging |  | 19:36:00 | 1 |  | 3 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 9/15/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2329 | 51339 | 9/28/2014 | Potentially Challenging |  |  | Other (Specify in comments) | Containment Spray System | Pumps | Electric motor driven pumps |  |  |  | Motors (electric, hydraulic, pneumatic) | 9/28/2014 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 9/28/2014 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 9/28/2014 | Potentially Challenging |  | 15:45:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 9/28/2014 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2330 | 51354 | 3/28/2010 | Potentially Challenging |  |  | Turbine Building |  | Pumps | Electric motor driven pumps | 4KV | AC |  | Motors (electric, hydraulic, pneumatic) | 3/28/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 3/28/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/28/2010 | Potentially Challenging |  | 23:30:00 | 1 |  | 3 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful |  |  | 3/28/2010 | Potentially Challenging | Hot Shutdown | Hot Shutdown | 0 | 0 | None |  | Challenging
2331 | 51366 | 4/21/2010 | Potentially Challenging |  |  | Containment (PWR) |  | Other |  |  |  |  | Circuit breakers, contactors, motor controllers, manual switches | 4/21/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 4/21/2010 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 4/21/2010 | Potentially Challenging |  | 13:47:00 | 1 |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 4/21/2010 | Potentially Challenging | Refueling | Refueling | 0 | 0 | None |  | Challenging
2332 | 51374 | 3/1/2014 | Undetermined (NC‐PC) |  |  | Reactor Building (BWR) | No Industry Std. Name for this system | Electrical panel | Other (specify in comments) |  |  |  | Electronic power supply | 3/1/2014 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 3/1/2014 | Undetermined (NC-PC) |  | Undetermined(NC-PC) |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: No potentially challenging criteria met. Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 3/1/2014 | Undetermined (NC-PC) |  |  | 3 |  |  | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful |  |  | 3/1/2014 | Undetermined (NC-PC) | Refueling | Refueling | 0 | 0 | None |  | Not Challenging
2333 | 51377 | 12/12/2013 | Potentially Challenging |  |  | Other (Specify in comments) | Aux. Bldg. Environmental Control System | Electrical panel | Motor control center | 4KV | AC |  | Blowers, compressors, fans, vacuum pumps, cooling units | 12/12/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In_Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 12/12/2013 | Potentially Challenging |  | Potentially Challenging |  |  |  |  | Challenging Criteria: No challenging criteria met. Potentially Challenging Criteria: Fire Type Fire Suppression Method Undetermined; Check for Unknown Entries: CH Determination; Temperature Condition Unknown CH and PC Determination; Detection Unknown Checking Timeline: No Known Time Line Values Not Challenging Evaluation: | 12/12/2013 | Potentially Challenging |  | 14:16:00 | 1 |  | 2 | Plant employee | Plant area did not have installed detection capability | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful |  |  | 12/12/2013 | Potentially Challenging | Unknown | Unknown | 0 | 0 | None |  | Challenging
2334 | 506203 | [12 empty] | 3/27/2008 | Not Challenging | Electrical arcing or sparks (non-HEAF) | In_Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
2335
2336
2337
2338
2339
2340
2341
2342
2343
2344