## Sheet1
| FireID | Event Date_FEA | Disposition_FEA | Fire Cause | Combustible Group | Type | Form | Fire Type | Smoke | Temperature | Damage Extent | Collateral Damage | Collateral Damage.1 | Feet Above | Feet Laterally | Collateral Description | Suppression Effects | Evidence of secondary ignition | Smoke.1 | Heat Damage
0 | 1 | 12/12/2006 | Undetermined | High Energy Arc Fault | Transient | Temporary |  | Arc/electric discharge | Unknow | Unknow | Confined to the objective of origin | Yes
1 | 2 | 1/5/1999 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | Yes
2 | 3 | 1/14/1999 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No
3 | 4
4 | 5 | 5/18/1999 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the objective of origin | No
5 | 6 | 7/13/1999 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No
6 | 7 | 10/9/1999 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | Insulation | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
7 | 8 | 5/7/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
8 | 9 | 1/3/1990 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Not available | Yes
9 | 10
10 | 11 | 3/15/1990 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
11 | 12 | 3/30/1990 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
12 | 13 | 4/10/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
13 | 14 | 5/24/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No
14 | 15 | 5/27/1990 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
15 | 16 | 6/10/1990 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
16 | 17 | 6/28/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Not available | No
17 | 18 | 7/13/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
18 | 19 | 8/4/1990 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Interior finish |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
19 | 20 | 8/25/1990 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Not available | No
20 | 21 | 9/22/1990 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
21 | 22 | 12/3/1990 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | No
22 | 23 | 12/19/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
23 | 24 | 12/22/1990 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
24 | 25 | 1/11/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
25 | 26 | 2/14/1991 | Challenging | Misuse of heating devices | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
26 | 27 | 1/16/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume |  | Confined to the object of origin | No
27 | 28 | 1/23/1991 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
28 | 29 | 2/23/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of originn (broad/extensive damage) | No
29 | 30 | 4/29/1991 | Challenging | Electrical arcing or sparks (non‐HEAF) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | Yes
30 | 31 | 6/15/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
31 | 32 | 6/27/1991 | Potentially Challenging | Personnel error during test and maintenance activity | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
32 | 33 | 8/1/1991 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
33 | 34 | 8/11/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
34 | 35 | 11/2/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
35 | 36 | 11/9/1991 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | Yes
36 | 37 | 11/15/1991 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
37 | 38 | 3/21/1992 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes
38 | 39 | 5/3/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
39 | 40 | 5/22/1992 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
40 | 41 | 6/17/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
41 | 42 | 7/3/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
42 | 43 | 7/4/1992 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
43 | 44 | 7/13/1992 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
44 | 45 | 7/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
45 | 46 | 8/4/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
46 | 47 | 8/10/1992 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
47 | 48 | 9/4/1992 | Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
48 | 49 | 9/15/1992 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
49 | 50 | 11/24/1992 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Structural component |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
50 | 51 | 2/5/1993 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
51 | 52 | 6/19/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
52 | 53 | 7/27/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
53 | 54 | 8/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | laming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
54 | 55 | 10/13/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No
55 | 56 | 10/21/1993 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
56 | 57 | 11/2/1993 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
57 | 58 | 12/25/1993 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Pressurized in a container | Explosion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to part of room or area of origin | Yes
58 | 59 | 1/29/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
59 | 60 | 2/3/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Ambient pressure, within a component | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
60 | 61 | 4/3/1994 | Challenging | Electrical arcing or sparks (non‐HEAF) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
61 | 62 | 6/6/1994 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
62 | 63 | 6/15/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
63 | 64 | 6/1/1994 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
64 | 65 | 7/2/1994 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
65 | 66 | 7/11/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
66 | 67 | 7/29/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
67 | 68 | 8/10/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
68 | 69 | 8/29/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
69 | 70 | 10/26/1994 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
70 | 71 | 3/1/1995 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
71 | 72 | 4/14/1995 | Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
72 | 73 | 6/1/1995 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
73 | 74 | 6/10/1995 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | Yes
74 | 75 | 8/22/1995 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No
75 | 76 | 10/21/1995 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
76 | 77 | 12/10/1995 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
77 | 78 | 1/24/1996 | Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to the object of origin | No
78 | 79 | 2/5/1996 | Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
79 | 80 | 2/29/1996 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
80 | 81 | 3/25/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
81 | 82 | 3/27/1996 | Potentially Challenging | Unknown | Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
82 | 83 | 4/4/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
83 | 84 | 4/19/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
84 | 85 | 5/13/1996 | Not Challenging | Unknown | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
85 | 86 | 6/23/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | Yes
86 | 87 | 8/19/1996 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
87 | 88 | 10/5/1996 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
88 | 89 | 10/15/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
89 | 90 | 10/17/1996 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
90 | 91 | 11/19/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Unknown | No
91 | 92 | 11/22/1996 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
92 | 93 | 3/4/1997 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
93 | 94 | 8/1/1997 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Mixed | Other (Specify) | Flaming combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to the object of origin | No
94 | 95 | 10/9/1997 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
95 | 96 | 10/28/1997 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
96 | 97 | 6/10/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
97 | 98 | 10/8/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
98 | 99 | 10/10/1998 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
99 | 100 | 5/15/2000 | Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | Yes
100 | 101 | 9/3/2000 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
101 | 102 | 9/4/2000 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
102 | 103 | 9/22/2000 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
103 | 104 | 10/14/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
104 | 105 | 11/10/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
105 | 106 | 2/3/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
106 | 107 | 3/21/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Cleaning solvents or paint | Contained within component | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
107 | 108 | 4/6/2001 | Not Challenging | Unknown |  | Unknown |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to part of room or area of origin | No
108 | 109 | 4/24/2001 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
109 | 110 | 6/25/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
110 | 111 | 8/2/2001 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
111 | 112 | 8/3/2001 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
112 | 113 | 6/12/2002 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
113 | 114 | 8/21/2002 | Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
114 | 115 | 8/22/2002 | Challenging | Mechanical malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
115 | 116 | 10/3/2002 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
116 | 117 | 10/9/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
117 | 118 | 1/15/2003 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
118 | 119 | 3/18/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No
119 | 120 | 4/7/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | No damage | No
120 | 121 | 4/26/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
121 | 122 | 4/29/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
122 | 123 | 10/16/2003 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Not available | No
123 | 124 | 10/28/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
124 | 125 | 1/6/2004 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to part of room or area of origin | Yes
125 | 126 | 5/21/2004 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
126 | 127 | 6/18/2004 | Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
127 | 128 | 8/31/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
128 | 129 | 11/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Interior finish |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
129 | 130 | 12/14/2004 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | No damage | No
130 | 131 | 1/14/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
131 | 132 | 3/4/2005 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
132 | 133 | 5/4/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
133 | 134 | 6/27/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
134 | 135 | 8/25/2005 | otentially Challenging | Electrical Failure (overheating, spark, HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light – visibility reduced, but all areas of the space can be seen | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
135 | 136 | 10/25/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
136 | 137 | 10/29/2005 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No
137 | 138 | 2/11/2006 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Interior finish |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
138 | 139 | 2/24/2006 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Other (Specify) | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
139 | 140 | 3/20/2006 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
140 | 141 | 5/1/2006 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent） | No
141 | 142 | 5/24/2006 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
142 | 143 | 8/15/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to room of origin | No
143 | 144 | 10/30/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
144 | 145 | 11/11/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
145 | 146 | 2/27/2007 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Not available | No
146 | 147 | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
147 | 148 | 4/6/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition） | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage） | No
148 | 149 | 4/8/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
149 | 150 | 4/25/2007 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition) | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No
150 | 151 | 8/1/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | No
151 | 152 | 10/23/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | No
152 | 153 | 8/16/2008 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | Yes
153 | 154 | 9/20/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin
154 | 155 | 11/17/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | No damage | No
155 | 157 | 2/1/2009 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
156 | 158 | 6/26/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
157 | 159 | 1/16/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Not available | Yes
158 | 160 | 2/7/2009 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | Confined to fire rated compartment of origin | No
159 | 161 | 4/22/2009 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
160 | 162 | 8/5/2009 | Challenging | High Energy Arc Fault (HEAF) | Insulation | Type not specified | Single Cable Tray | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to floor of origin | No
161 | 163 | 10/12/2009 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
162 | 164 | 3/28/1990 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent） | No
163 | 168 | 11/13/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Mixed | Unknown | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
164 | 169 | 11/13/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent） | No
165 | 170 | 11/21/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | Yes
166 | 172 | 12/7/2003 | Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to room of origin | No
167 | 173 | 12/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Mixed | Single Cable | Overheating – no smoldering or flaming combustion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
168 | 174 | 12/30/2003 | Not Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
169 | 175 | 11/22/2009 | Challenging | Electrical malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | High – protective clothing needed for room entry | Confined to part of room or area of origin | No
170 | 176 | 12/12/2009 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
171 | 181 | 2/13/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage） | No
172 | 184 | 6/27/1997 | Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to room of origin | No
173 | 185 | 3/23/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
174 | 186 | 5/14/1998 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
175 | 187 | 8/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No
176 | 188 | 8/24/1999 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
177 | 189 | 10/14/1996 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to part of room or area of origin | No
178 | 190 | 3/18/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
179 | 191 | 11/11/1998 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
180 | 192 | 5/15/1999 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
181 | 193 | 7/31/1991 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
182 | 194 | 5/22/1990 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil | Contained within reservoir | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | Yes
183 | 195 | 3/21/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
184 | 199 | 1/22/1990 | Potentially Challenging |  | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
185 | 200 | 2/6/1990 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
186 | 201 | 3/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
187 | 202 | 3/23/1990 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
188 | 203 | 4/6/1990 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
189 | 204 | 4/9/1990 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Plastic Sheets |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
190 | 206 | 6/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
191 | 207 | 7/15/1990 | Undetermined (PC-CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
192 | 208 | 8/8/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
193 | 209 | 8/22/1990 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
194 | 210 | 10/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
195 | 211 | 11/2/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
196 | 212 | 12/5/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
197 | 214 | 3/8/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
198 | 215 | 3/11/1991 | Not Challenging |  | In‐Situ | Other (specify) |  | Flaming combustion – external to component |  |  | Confined to part of room or area of origin
199 | 216 | 7/12/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
200 | 217 | 7/19/1991 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
201 | 218 | 9/12/1991 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No
202 | 219 | 9/27/1991 | Undetermined (PC‐CH） | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
203 | 220 | 10/20/1991 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
204 | 221 | 10/23/1991 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
205 | 222 | 2/1/1992 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin | No
206 | 223 | 3/3/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
207 | 224 | 3/8/1992 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
208 | 225 | 3/23/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
209 | 226 | 4/17/1992 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
210 | 227 | 6/9/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
211 | 228 | 8/14/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
212 | 229 | 8/21/1992 | Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable Tray | Other (specify) | Unknown | Unknown | Confined to the object of origin | Yes
213 | 230 | 8/31/1992 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
214 | 231 | 10/22/1992 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
215 | 232 | 10/27/1992 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
216 | 233 | 11/29/1992 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
217 | 234 | 12/16/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
218 | 235 | 12/30/1992 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
219 | 236 | 1/6/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
220 | 237 | 3/19/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
221 | 238 | 4/1/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
222 | 239 | 7/14/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
223 | 240 | 7/19/1993 | Undetermined (PC‐CH） | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
224 | 241 | 11/3/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
225 | 242 | 11/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
226 | 243 | 12/1/1993 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
227 | 244 | 12/7/1993 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
228 | 245 | 12/16/1993 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
229 | 246 | 1/12/1994 | Challenging | Personnel error: Misuse of material ignited | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to room of origin | No
230 | 247 | 1/12/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
231 | 248 | 3/5/1994 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
232 | 249 | 3/7/1994 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
233 | 250 | 7/19/1994 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
234 | 251 | 10/11/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
235 | 252 | 3/18/1995 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
236 | 253 | 7/6/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
237 | 254 | 9/25/1995 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
238 | 255 | 11/19/1995 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin | No
239 | 256 | 7/22/1996 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
240 | 257 | 10/22/1997 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
241 | 258 | 11/3/1997 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | No
242 | 259 | 11/26/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
243 | 260 | 2/3/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
244 | 261 | 5/11/1998 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
245 | 262 | 2/19/1999 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
246 | 263 | 4/25/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
247 | 264 | 10/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Unknown | No
248 | 265 | 9/23/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
249 | 266 | 11/9/2006 | Potentially Challenging | Unknown | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
250 | 267 | 6/1/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
251 | 268 | 4/7/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
252 | 269 | 12/12/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
253 | 270 | 11/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
254 | 271 | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
255 | 272 | 4/17/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Contained within reservoir | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes
256 | 273 | 5/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
257 | 274 | 5/7/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
258 | 275 | 10/14/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
259 | 276 | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
260 | 277 | 11/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
261 | 278 | 1/5/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
262 | 280 | 11/19/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
263 | 282 | 4/23/2001 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
264 | 283 | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
265 | 284 | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
266 | 285 | 11/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Spill confined by curbs or other physical feat | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
267 | 286 | 4/20/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
268 | 287 | 8/10/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
269 | 288 | 10/10/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
270 | 289 | 5/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
271 | 290 | 8/22/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
272 | 292 | 10/8/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
273 | 293 | 10/14/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
274 | 294 | 10/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
275 | 295 | 10/22/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
276 | 296 | 10/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
277 | 297 | 11/30/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
278 | 298 | 12/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
279 | 299 | 3/4/2008 | Not Challenging | Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
280 | 300 | 3/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
281 | 302 | 12/21/1999 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
282 | 303 | 3/1/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
283 | 305 | 6/21/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
284 | 306 | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
285 | 307 | 10/17/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
286 | 308 | 10/14/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
287 | 309 | 10/23/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Single Cable | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
288 | 310 | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
289 | 311 | 12/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
290 | 312 | 10/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
291 | 313 | 11/9/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
292 | 314 | 2/10/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
293 | 316 | 8/17/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
294 | 317 | 9/27/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
295 | 318 | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
296 | 319 | 10/5/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
297 | 320 | 10/24/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
298 | 321 | 10/31/2000 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | In‐Situ | Other electrical or electronic equipment |  | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
299 | 322 | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
300 | 324 | 1/12/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
301 | 325 | 3/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
302 | 326 | 3/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
303 | 327 | 1/1/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
304 | 328 | 9/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
305 | 329 | 9/25/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
306 | 330 | 9/27/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
307 | 332 | 4/15/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
308 | 333 | 5/11/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
309 | 335 | 8/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
310 | 337 | 8/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
311 | 338 | 7/25/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
312 | 340 | 8/7/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
313 | 341 | 2/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
314 | 342 | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
315 | 343 | 11/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
316 | 344 | 10/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
317 | 345 | 4/25/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
318 | 346 | 3/1/2002 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
319 | 349 | 4/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
320 | 350 | 7/11/2002 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
321 | 351 | 9/26/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
322 | 352 | 2/28/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
323 | 353 | 1/21/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
324 | 354 | 10/1/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
325 | 355 | 3/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
326 | 356 | 4/19/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
327 | 357 | 1/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
328 | 358 | 5/2/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
329 | 359 | 3/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
330 | 360 | 7/25/2001 | Not Challenging | Mechanical equipment malfunction/failure |  |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
331 | 361 | 2/4/2002 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
332 | 362 | 4/16/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
333 | 363 | 5/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
334 | 364 | 10/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
335 | 365 | 8/7/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
336 | 366 | 1/25/2006 | Not Challenging | Personnel error: Misuse of heating devices | Liquid | Lube Oil or grease |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
337 | 367 | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
338 | 368 | 10/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
339 | 372 | 9/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
340 | 373 | 10/5/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
341 | 374 | 10/13/2009 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
342 | 375 | 10/15/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
343 | 376 | 6/5/2004 | Not Challenging |  | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
344 | 377 | 8/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
345 | 378 | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
346 | 379 | 10/2/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
347 | 380 | 10/29/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
348 | 381 | 3/6/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
349 | 384 | 3/23/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
350 | 385 | 4/14/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | Yes
351 | 386 | 6/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
352 | 387 | 7/24/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
353 | 388 | 7/25/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
354 | 389 | 10/17/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
355 | 390 | 10/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
356 | 392 | 10/30/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
357 | 393 | 10/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
358 | 394 | 2/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
359 | 397 | 5/2/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
360 | 398 | 7/7/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
361 | 399 | 12/24/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
362 | 400 | 3/28/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
363 | 401 | 6/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
364 | 404 | 6/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
365 | 405 | 8/13/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
366 | 406 | 6/12/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
367 | 407 | 12/1/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
368 | 408 | 6/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
369 | 409 | 9/21/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Other (specify) | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
370 | 410 | 7/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
371 | 411 | 3/8/2001 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
372 | 412 | 7/15/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
373 | 416 | 10/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
374 | 418 | 10/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
375 | 419 | 4/5/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
376 | 420 | 6/24/2001 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
377 | 421 | 7/1/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
378 | 422 | 3/7/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
379 | 423 | 6/23/2003 | Undetermined (PC‐CH) | Unknown | In‐Situ | Structural component |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
380 | 424 | 3/10/2005 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
381 | 426 | 9/17/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
382 | 427 | 2/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
383 | 428 | 9/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  |  | Unknown | Unknown | Confined to the object of origin | No
384 | 429 | 3/12/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
385 | 430 | 10/10/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
386 | 431 | 4/3/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
387 | 436 | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
388 | 437 | 2/3/2001 | Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | High – protective clothing needed for room entry | Confined to room of origin | Yes
389 | 438 | 6/24/2001 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to structure of origin | Yes
390 | 439 | 10/2/2002 | Not Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a component | Explosion | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
391 | 440 | 1/2/2003 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
392 | 441 | 11/23/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
393 | 442 | 2/4/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
394 | 443 | 3/3/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
395 | 444 | 6/28/2004 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | Yes
396 | 445 | 8/30/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
397 | 446 | 10/5/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
398 | 447 | 10/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
399 | 448 | 11/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
400 | 449 | 12/8/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
401 | 450 | 12/13/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
402 | 451 | 12/13/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
403 | 452 | 12/18/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
404 | 453 | 6/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
405 | 454 | 6/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
406 | 455 | 6/6/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
407 | 456 | 7/7/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
408 | 457 | 2/17/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
409 | 458 | 5/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
410 | 459 | 5/10/2006 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
411 | 460 | 9/7/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
412 | 461 | 10/12/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
413 | 462 | 10/18/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
414 | 463 | 11/1/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
415 | 464 | 12/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
416 | 465 | 1/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
417 | 466 | 2/2/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
418 | 467 | 2/13/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
419 | 468 | 2/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
420 | 469 | 3/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
421 | 470 | 6/29/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
422 | 471 | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
423 | 472 | 7/17/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
424 | 473 | 8/4/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
425 | 474 | 8/21/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin
426 | 475 | 9/27/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
427 | 476 | 12/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
428 | 477 | 2/23/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No
429 | 478 | 3/30/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
430 | 479 | 3/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
431 | 480 | 4/7/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
432 | 481 | 6/29/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
433 | 482 | 2/8/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
434 | 483 | 11/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
435 | 484 | 11/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
436 | 485 | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
437 | 486 | 8/27/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
438 | 487 | 1/13/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
439 | 488 | 10/16/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
440 | 491 | 4/12/2000 | Undetermined (NC‐PC) | Unknown | In‐Situ | Structural component |  |  | Unknown | Unknown | Unknown
441 | 492 | 10/19/2000 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
442 | 494 | 3/8/2000 | Undetermined(NC‐PC) | Unknown | In‐Situ | Structuralcomponen |  |  | Unknown | Unknown | Unknown | No
443 | 495 | 3/20/2003 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  |  | Unknown | Unknown | Unknown | No
444 | 496 | 5/19/2002 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specif |  | Flamingcombustion–internaltocomponent | Unknown | Unknown | Unknown | No
445 | 497 | 8/14/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipmen |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
446 | 498 | 12/19/2000 | Undetermined(PC‐CH) | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
447 | 499 | 12/17/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
448 | 500 | 3/12/2001 | Undetermined(PC‐CH) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Unknown | Unknown | Unknown | Unknown
449 | 501 | 1/24/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent |  | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
450 | 502 | 11/18/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Transient | Temporaryelectricalwiringorequipment |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
451 | 503 | 5/14/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
452 | 504 | 10/9/2002 | Undetermined(PC‐CH) | Unknown | Unknown | Unknown |  | Unknown | Unknown | Unknown | Unknown
453 | 505 | 9/13/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
454 | 506 | 9/12/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin | No
455 | 508 | 3/14/2005 | NotChallenging |  |  |  |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
456 | 509 | 1/19/2005 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
457 | 511 | 7/16/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
458 | 512 | 7/20/2005 | NotChallenging |  | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
459 | 513 | 11/18/2005 | Undetermined(NC‐PC) |  | In‐Situ | Thermalinsulationmaterials |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
460 | 514 | 4/27/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion
461 | 515 | 10/5/2005 | Undetermined(PC‐CH) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
462 | 516 | 10/25/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
463 | 517 | 3/23/2006 | Undetermined(PC‐CH) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
464 | 518 | 3/30/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
465 | 519 | 5/4/2007 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  |  | Unknown | Unknown | Confinedtotheobjectoforigin | No
466 | 520 | 6/6/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
467 | 521 | 12/17/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
468 | 522 | 9/19/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
469 | 523 | 9/27/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
470 | 524 | 10/11/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
471 | 526 | 1/30/2009 | Undetermined(NC‐PC) | Unknown | In‐Situ | Other(specify) |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
472 | 527 | 11/10/2009 | Undetermined(NC‐PC) | Mechanicalequipmentmalfunction/failure | In‐Situ | Structuralcomponent |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
473 | 529 | 11/28/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent) | No
474 | 530 | 3/5/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
475 | 531 | 8/24/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin | No
476 | 533 | 1/27/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
477 | 534 | 4/10/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
478 | 535 | 6/16/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  |  | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
479 | 536 | 8/24/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation
480 | 537 | 10/13/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
481 | 538 | 10/20/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
482 | 539 | 10/23/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
483 | 540 | 10/23/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
484 | 541 | 10/24/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
485 | 542 | 3/4/2000 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Thermalinsulationmaterials |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
486 | 543 | 8/27/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
487 | 544 | 12/13/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
488 | 545 | 6/5/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
489 | 546 | 10/9/2002 | NotChallenging |  | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
490 | 547 | 11/5/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
491 | 548 | 11/13/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Unkno |  |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Unknown | Unknown | Confinedtotheobjectoforigin
492 | 549 | 7/16/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
493 | 550 | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtotheobjectoforigin
494 | 551 | 2/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
495 | 552 | 7/31/2003 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
496 | 553 | 6/24/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
497 | 554 | 6/2/2005 | Undetermined(NC‐PC) | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
498 | 555 | 7/27/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
499 | 556 | 10/14/2005 | NotChallenging |  | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | : Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
500 | 557 | 11/2/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
501 | 558 | 12/13/2005 | PotentiallyChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
502 | 559 | 9/12/2006 | Undetermined(NC‐PC | Unknown | Unknown |  |  |  | Unknown | Unknown | Unknown
503 | 560 | 5/20/2006 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplumt | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
504 | 561 | 1/3/2005 | NotChallenging | Unknown | In‐Situ | Other(specify) |  | NoFire‐Falseactuationofdetectiondevice | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
505 | 562 | 10/9/2006 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  |  | Unknown | Unknown | Confinedtotheobjectoforigin
506 | 563 | 10/18/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
507 | 564 | 3/13/2007 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
508 | 565 | 4/25/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
509 | 566 | 7/2/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
510 | 567 | 7/31/2007 | Undetermined(NC‐PC) | Arc/electricdischarge | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
511 | 568 | 1/12/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
512 | 569 | 5/15/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
513 | 570 | 6/3/2008 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Structuralcomponent |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
514 | 571 | 9/29/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
515 | 572 | 12/23/2008 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
516 | 573 | 1/29/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
517 | 575 | 5/18/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
518 | 576 | 8/31/2009 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
519 | 577 | 9/16/2002 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
520 | 578 | 11/8/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
521 | 579 | 3/23/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
522 | 580 | 1/6/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Otherelectricalorelectronicequipment |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
523 | 581 | 4/17/2002 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
524 | 582 | 9/3/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
525 | 584 | 10/8/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Nodamage
526 | 585 | 12/10/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
527 | 586 | 5/5/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
528 | 587 | 5/13/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Transient | Otherelectricalorelectronicequipment |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
529 | 588 | 11/30/2006 | Challenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Thermoset | SingleCable | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
530 | 590 | 2/20/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
531 | 591 | 7/19/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
532 | 592 | 6/11/2009 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
533 | 593 | 10/16/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
534 | 594 | 1/28/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
535 | 595 | 2/13/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
536 | 596 | 6/13/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
537 | 597 | 7/22/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
538 | 598 | 10/12/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
539 | 599 |  | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire Temperature: | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
540 | 600 | 1/17/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
541 | 601 | 10/28/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
542 | 602 | 9/29/2006 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
543 | 603 | 11/14/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
544 | 604 | 9/8/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
545 | 605 | 9/14/2001 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
546 | 606 | 10/31/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
547 | 607 | 11/13/2008 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
548 | 609 |  | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
549 | 10273 | 10/18/2000 | NotChallenging | Personnelerrorduringtestandmaintenanceactivity | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
550 | 10274 | 10/21/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ |  |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
551 | 10276 | 12/15/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
552 | 10277 | 12/22/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Smolderingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
553 | 10278 | 4/4/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
554 | 10279 | 4/14/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
555 | 10280 | 4/17/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
556 | 10282 | 8/12/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | NoFire‐Falseactuationofdetectiondevice | Unknown | Unknown | Confinedtotheobjectoforigin
557 | 10283 | 2/10/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
558 | 10284 | 3/10/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
559 | 10285 | 4/7/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
560 | 10286 | 5/10/2004 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
561 | 10287 | 5/19/2004 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
562 | 10288 | 5/22/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
563 | 10289 | 5/28/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
564 | 10290 | 6/3/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
565 | 10291 | 9/18/2004 | Undetermined(PC‐CH) | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
566 | 10292 | 1/13/2005 | NotChallenging | Mechanicalequipmentmalfunction/failure | Insulation | Otherelectricalorelectronicequipment | Other(Specify) | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
567 | 10293 | 8/16/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
568 | 10294 | 10/9/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
569 | 10295 | 10/18/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
570 | 10296 | 8/21/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
571 | 10297 | 12/14/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
572 | 10298 | 2/12/2009 | NotChallenging | Unknown | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
573 | 10299 | 2/19/2009 | NotChallenging | Mechanicalequipmentmalfunction/failure | Gas | Hydrogen | Jetfromapressurizedsource | NoFire‐Falseactuationofdetectiondevice | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown
574 | 10300 | 6/25/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
575 | 10302 | 3/10/2000 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
576 | 10303 | 5/18/2001 | NotChallenging | Suspicious | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
577 | 10304 | 4/8/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
578 | 10305 | 10/25/2001 | NotChallenging | Electricalarcingorsparks(non‐HEAF) |  |  |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
579 | 10307 | 10/3/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
580 | 10308 | 9/19/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
581 | 10309 | 4/18/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
582 | 10310 | 1/29/2007 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
583 | 10311 | 1/9/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
584 | 10312 | 2/9/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio FireTypeUnknown: | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
585 | 10313 | 4/3/2009 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
586 | 10315 | 10/18/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
587 | 10316 | 11/22/2002 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
588 | 10317 | 9/23/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
589 | 10318 | 10/16/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
590 | 10319 | 1/7/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
591 | 10320 | 5/25/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
592 | 10321 | 6/1/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
593 | 10322 | 12/10/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown
594 | 10323 | 12/11/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
595 | 10324 | 12/30/200 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
596 | 10326 | 1/24/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
597 | 10327 | 6/21/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
598 | 10328 | 7/17/2007 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Liquid | Other(specify) | Other(specify) | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
599 | 10329 | 9/22/2008 | NotChallenging | Unknown | Unknown |  |  | Other(specify) | Unknown | Unknown | Unknown
600 | 10330 | 9/23/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
601 | 10331 | 3/24/2009 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
602 | 10334 | 3/30/2000 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
603 | 10336 | 10/2/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
604 | 10337 | 10/11/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
605 | 10338 | 9/13/2001 | Undetermined(PC‐CH) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
606 | 10339 | 8/16/2004 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
607 | 10341 | 5/21/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
608 | 10343 | 8/25/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
609 | 10344 | 10/1/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
610 | 10345 | 1/25/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
611 | 10349 | 9/24/2007 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
612 | 10350 | 1/21/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
613 | 10352 | 12/11/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
614 | 10353 | 1/5/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
615 | 10354 | 7/2/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Gas | Other(specify) | Pressurizedinacontainer | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
616 | 10355 | 4/26/2008 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
617 | 10356 | 10/3/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
618 | 10357 | 7/1/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
619 | 10358 | 7/3/2002 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
620 | 10359 | 11/16/2000 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
621 | 10360 | 10/13/2000 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
622 | 10361 | 5/5/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
623 | 10362 | 10/28/2006 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
624 | 10363 | 11/5/2009 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–externaltocomponent | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
625 | 10364 | 6/30/2005 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
626 | 10365 | 8/22/2008 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | Unknown |  |  | Arc/electricdischarge | Unknown | Unknown | Confinedtotheobjectoforigin
627 | 10367 | 10/22/2000 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
628 | 10368 | 6/28/2004 | Undetermined(NC‐PC) | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
629 | 10369 | 10/4/2002 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
630 | 10370 | 4/11/2008 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
631 | 10371 | 10/20/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
632 | 10372 | 10/22/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
633 | 10373 | 4/14/2005 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
634 | 10374 | 7/11/2003 | PotentiallyChallenging | Flamingcombustion–externaltocomponent | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
635 | 10376 | 3/23/2004 | Challenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
636 | 10377 | 3/10/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Thermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
637 | 10378 | 3/18/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
638 | 10379 | 3/22/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
639 | 10380 | 9/23/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
640 | 10381 | 10/24/2000 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
641 | 10382 | 3/20/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
642 | 10383 | 4/3/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
643 | 10384 | 6/26/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
644 | 10385 | 2/12/2002 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
645 | 10386 | 3/1/2003 | Undetermined(NC‐PC) | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
646 | 10387 | 3/4/2003 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
647 | 10389 | 9/8/2003 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
648 | 10392 | 4/5/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
649 | 10393 | 11/7/2004 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
650 | 10394 | 2/22/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage)
651 | 10395 | 7/13/2005 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
652 | 10396 | 7/14/2005 | NotChallenging | Unkno | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
653 | 10397 | 10/12/2005 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Structuralcomponent |  | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
654 | 10399 | 1/31/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
655 | 10401 | 5/9/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient
656 | 10402 | 6/27/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Overheating–nosmolderingorflamingcombustion | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
657 | 10403 | 10/31/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
658 | 10404 | 12/5/2006 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
659 | 10405 | 1/20/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Unknown | Confinedtotheobjectoforigin
660 | 10406 | 5/5/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
661 | 10407 | 6/3/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
662 | 10409 | 12/12/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
663 | 10410 | 2/13/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
664 | 10411 | 3/8/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
665 | 10412 | 2/17/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
666 | 10413 | 5/17/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Nosmokepresent | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
667 | 10414 | 8/31/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | SingleCable | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
668 | 10416 | 4/1/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
669 | 10417 | 4/17/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
670 | 10418 | 2/15/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
671 | 10419 | 4/12/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
672 | 10420 | 4/17/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
673 | 10421 | 6/20/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
674 | 10422 | 8/25/2008 | NotChallenging | Unknown | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
675 | 10423 | 9/3/2008 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
676 | 10424 | 10/19/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
677 | 10425 | 11/6/2009 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
678 | 10426 | 4/29/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
679 | 10427 | 5/3/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
680 | 10428 | 6/1/2000 | NotChallenging | Mechanicalequipmentmalfunction/failure | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
681 | 10429 | 9/21/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
682 | 10430 | 12/21/2000 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
683 | 10432 | 10/22/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
684 | 10433 | 12/10/2003 | NotChallenging | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
685 | 10434 | 5/7/2004 | NotChallenging | :Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
686 | 10435 | 7/8/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
687 | 10436 | 8/11/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
688 | 10437 | 5/9/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | NoFire‐Falseactuationofdetectiondevice | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
689 | 10441 | 3/4/2009 | PotentiallyChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
690 | 10442 | 3/9/2009 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtotheobjectoforigin
691 | 10443 | 7/25/2009 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
692 | 10444 | 10/13/2009 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
693 | 10445 | 2/7/2000 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
694 | 10446 | 4/11/2000 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
695 | 10447 | 3/9/2000 | Undetermined(NC‐PC) | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
696 | 10448 | 10/23/2001 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
697 | 10449 | 5/17/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
698 | 10450 | 6/19/2001 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | Cleaningsolventsorpaint | Unconfinedspill | Flamingcombustion–externaltocomponent | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
699 | 10451 | 6/5/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Unknown
700 | 10452 | 9/17/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
701 | 10453 | 11/20/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
702 | 10454 | 2/17/2003 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
703 | 10455 | 3/22/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
704 | 10456 | 7/19/2002 | PotentiallyChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
705 | 10457 | 10/22/2002 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Unknown |  |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
706 | 10458 | 1/7/2003 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Liquid | Other(specify) | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
707 | 10459 | 2/7/2003 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
708 | 10460 | 4/9/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
709 | 10461 | 3/6/2003 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Firenotobservedandfiretypeindeterminatefrompost‐inspectio | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
710 | 10462 | 2/5/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
711 | 10463 | 3/1/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
712 | 10464 | 3/30/2005 | Challenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Containedwithinreservoir | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Unknown | Confinedtotheobjectoforigin
713 | 10465 | 9/30/2004 | NotChallenging | Unknown | Unknown |  |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
714 | 10466 | 8/31/2005 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | In‐Situ |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
715 | 10467 | 4/7/2005 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
716 | 10468 | 10/27/2005 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Structuralcomponent |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
717 | 10469 | 3/23/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
718 | 10470 | 5/5/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | re: Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
719 | 10471 | 12/26/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
720 | 10472 | 9/25/2007 | Challenging | HighEnergyArcFault(HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Explosion | Unknown | Unknown | Confinedtotheobjectoforigin
721 | 10473 | 1/23/2007 | NotChallenging | Unknown | In‐Situ | Other(specify) |  | Other(specify) | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Unknown
722 | 10474 | 2/23/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
723 | 10476 | 4/10/2007 | PotentiallyChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
724 | 10477 | 6/7/2007 | PotentiallyChallenging | Unknown | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
725 | 10478 | 7/10/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
726 | 10479 | 7/23/2008 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
727 | 10480 | 7/23/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
728 | 10482 | 10/22/2006 | Undetermined(NC‐PC) | Unknown | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
729 | 10483 | 4/10/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
730 | 10484 | 4/16/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
731 | 10485 | 4/21/2007 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
732 | 10486 | 7/28/2007 | NotChallenging | Mechanicalequipmentmalfunction/failure | In‐Situ | Other(specify) |  | Mechanicalequipmentmalfunction/failure | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
733 | 10487 | 9/4/2007 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtopartofroomorareaoforigin
734 | 10488 | 9/24/2007 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
735 | 10489 | 4/6/2008 | Challenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | Other(specify) | Spillconfinedbycurbsorotherphysicalfeat | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
736 | 10490 | 4/9/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Insulation | Typenotspecified | Unknown | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
737 | 10491 | 4/29/2008 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
738 | 10492 | 9/30/2008 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(broad/extensivedamage)
739 | 10493 | 10/23/2008 | NotChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Other(specify) |  | Arc/electricdischarge | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
740 | 10496 | 5/14/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
741 | 10497 | 7/31/2009 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
742 | 10498 | 9/26/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
743 | 10499 | 10/16/2009 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Overheating–nosmolderingorflamingcombustion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
744 | 10504 | 3/15/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
745 | 10505 | 3/16/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
746 | 10507 | 3/14/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
747 | 10508 | 3/28/2001 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Unknown | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
748 | 10509 | 4/1/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
749 | 10510 | 4/10/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
750 | 10512 | 6/22/2001 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
751 | 10513 | 8/20/2001 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
752 | 10514 | 8/26/2001 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
753 | 10515 | 9/30/2001 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
754 | 10516 | 11/20/2001 | PotentiallyChallenging | Electricalarcingorsparks(non‐HEAF) | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
755 | 10517 | 8/5/2002 | NotChallenging | Unknown | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
756 | 10518 | 8/26/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin
757 | 10519 | 9/25/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
758 | 10520 | 11/26/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Structuralcomponent |  | Flamingcombustion–externaltocomponent | Unknown | Unknown | Confinedtopartofroomorareaoforigin
759 | 10521 | 9/10/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
760 | 10522 | 11/2/2003 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
761 | 10523 | 11/9/2003 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
762 | 10524 | 1/7/2004 | PotentiallyChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
763 | 10525 | 5/10/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
764 | 10526 | 5/30/2004 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Liquid | LubeOilorgrease | Leak‐OilsoakedInsulation | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
765 | 10528 | 9/8/2004 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
766 | 10529 | 1/25/2006 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
767 | 10530 | 3/15/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
768 | 10531 | 3/31/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
769 | 10532 | 6/28/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
770 | 10533 | 2/1/2001 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
771 | 10534 | 3/21/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Unknown |  |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
772 | 10535 | 3/31/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
773 | 10536 | 12/12/2002 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
774 | 10537 | 2/17/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
775 | 10538 | 4/1/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
776 | 10539 | 1/19/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
777 | 10540 | 2/4/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Extendedbeyondstructureoforigin
778 | 10541 | 3/24/2001 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
779 | 10542 | 7/9/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
780 | 10543 | 9/3/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
781 | 10544 | 1/17/2003 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
782 | 10545 | 5/9/2002 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
783 | 10546 | 3/15/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
784 | 10547 | 1/22/2004 | NotChallenging |  | Insulation | Typenotspecified | SingleCable | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
785 | 10548 | 6/25/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
786 | 10549 | 10/8/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
787 | 10550 | 9/3/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
788 | 10551 | 7/14/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
789 | 10552 | 7/8/2003 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
790 | 10553 | 4/17/2000 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
791 | 10554 | 5/3/2004 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
792 | 10555 | 5/5/2004 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
793 | 10556 | 5/11/2004 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient(Gas) | Other(specify) | Pressurizedinacontainer | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
794 | 10557 | 1/13/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
795 | 10558 | 1/19/2005 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Liquid | LubeOilorgrease | Containedwithincomponent | Flamingcombustion–internaltocomponent | Moderatesmokecomingformignitionsource‐visibilitysignificantlyreducedinvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
796 | 10559 | 3/7/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
797 | 10560 | 3/29/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
798 | 10561 | 4/4/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
799 | 10562 | 5/23/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
800 | 10563 | 7/11/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
801 | 10564 | 8/10/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
802 | 10565 | 8/15/2005 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | In‐Situ | Other(specify) |  | Flamingcombustion–externaltocomponent | Outsidearea,smokeonlyinfireplume | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
803 | 10566 | 9/15/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
804 | 10567 | 12/19/2005 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
805 | 10568 | 1/12/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Temporarythermalinsulationmaterials |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
806 | 10569 | 2/8/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Unknown | Other(specify) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
807 | 10570 | 2/13/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Liquid | LubeOilorgrease | Unconfinedspill | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
808 | 10571 | 3/5/2006 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
809 | 10572 | 4/13/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtopartofroomorareaoforigin
810 | 10573 | 7/5/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
811 | 10574 | 7/17/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
812 | 10575 | 7/18/2006 | NotChallenging | OverheatedMaterial(lubeoil,pumppacking,thermalinsulation,etc.) | Transient | Other(specify) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
813 | 10576 | 7/26/2006 | PotentiallyChallenging | Mechanicalequipmentmalfunction/failure | Gas | Hydrogen | Other(specify) | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
814 | 10577 | 10/28/2006 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | Insulation | Typenotspecified | MultipleCablesNotInTrayorBundle | Overheating–nosmolderingorflamingcombustion | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
815 | 10579 | 4/4/2008 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Cellulosicmaterialsincludingwood,paperorothersolidtransients |  | Flamingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
816 | 10580 | 4/26/2008 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
817 | 10581 | 11/19/2008 | NotChallenging | Other(otherpersonnelerror,naturaleffect,etc.specifyincomments) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
818 | 10582 | 12/9/2005 | Undetermined(NC‐PC) | Hotwork(cutting/welding/grinding/etc.) | Transient | Trash(i.e.,solidrefusecollectedfordisposal) |  | Smolderingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Nodamage
819 | 10583 | 9/1/2006 | NotChallenging | Hotwork(cutting/welding/grinding/etc.) | In‐Situ | Other(specify) |  | Smolderingcombustion–externaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin
820 | 10584 | 7/27/2008 | NotChallenging | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Explosion | Outsidearea,smokeonlyinfireplume | Outsidearea,elevatedtemperaturesonlyinthefireplume | Confinedtotheobjectoforigin(localized/singlesubcomponent)
821 | 10585 | 4/24/2003 | Undetermined(NC‐PC) | Electricalfailureresultinginoverheatingmaterials | In‐Situ | Otherelectricalorelectronicequipment |  | Flamingcombustion–internaltocomponent | Lightsmokecomingfromignitionsource‐minorornovisibilityreductioninvicinityoffire | Noneorinsignificant–temperatureatorclosetoambient | Confinedtotheobjectoforigin(localized/singlesubcomponent)
822 | 10586 | 1/19/2000 | : Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
823 | 10587 | 8/10/2000 | Not Challenging | Not Challenging | Gas | Hydrogen | Pressurized in a container | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
824 | 10588 | 11/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
825 | 10589 | 2/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient (Liquid) | Fuel Oil | Unconfined spill | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
826 | 10590 | 10/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume |  | No
827 | 10591 | 10/8/2002 | Not Challenging | vElectrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
828 | 10592 | 1/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
829 | 10593 | 7/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
830 | 10594 | 1/25/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
831 | 10595 | 2/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
832 | 10596 | 11/4/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
833 | 10598 | 1/3/2006 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
834 | 10599 | 3/25/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
835 | 10600 | 2/18/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
836 | 10601 | 2/16/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
837 | 10602 | 2/13/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (specify) | Other (specify) | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
838 | 10604 | 5/14/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
839 | 10605 | 1/31/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
840 | 10606 | 5/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Other (specify) | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
841 | 10607 | 12/27/2004 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to componen | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | High – protective clothing needed for room entry | Confined to part of room or area of origin | Yes
842 | 10609 | 9/7/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
843 | 10611 | 8/20/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
844 | 10614 | 2/25/2004 | Undetermined (NC‐PC) FireID: 10614 | [5 empty] | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still
845 | 10615 | 10/15/2005 | Undetermined (NC‐PC) | [5 empty] | possible with SCBA
846 | 10617 | 2/14/2003 | Undetermined (NC‐PC) | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Hydrogen | Ambient pressure, within a compartment | Explosion | Unknown | Unknown | Unknown
847 | 10618 | 2/15/2000 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
848 | 10619 | 5/24/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
849 | 10620 | 8/9/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
850 | 10621 | 8/22/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | No damage | No
851 | 10622 | 6/25/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
852 | 10623 | 8/8/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
853 | 10624 | 10/26/2001 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Extended beyond structure of origin | No
854 | 10625 | 9/28/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
855 | 10626 | 12/11/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
856 | 10627 | 12/12/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
857 | 10628 | 12/30/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
858 | 10630 | 6/6/2007 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Flaming combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
859 | 10631 | 11/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
860 | 10632 | 3/3/2000 | Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
861 | 10633 | 3/7/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
862 | 10636 | 9/26/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable Tray | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
863 | 10638 | 3/5/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
864 | 10639 | 2/16/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
865 | 10641 | 3/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Flaming combustion – internal to component | Flaming combustion – internal to component | Confined to the object of origin | No
866 | 10642 | 3/14/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
867 | 10643 | 5/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
868 | 10644 | 11/3/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
869 | 10645 | 4/11/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
870 | 10646 | 7/17/2003 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
871 | 10647 | 8/22/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
872 | 10648 | 3/12/2004 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
873 | 10649 | 3/15/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
874 | 10650 | 3/20/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
875 | 10652 | 3/10/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
876 | 10653 | 4/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
877 | 10654 | 2/5/2007 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
878 | 10656 | 2/22/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
879 | 10657 | 6/29/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
880 | 10658 | 12/29/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
881 | 10660 | 11/6/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
882 | 10664 | 10/2/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
883 | 10665 | 11/3/2000 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
884 | 10666 | 4/18/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
885 | 10667 | 4/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
886 | 10668 | 4/22/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
887 | 10669 | 5/20/2001 | Not Challenging | Mechanical equipment malfunction/failure | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
888 | 10670 | 6/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
889 | 10671 | 6/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
890 | 10672 | 6/26/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
891 | 10673 | 9/4/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
892 | 10674 | 12/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
893 | 10675 | 12/31/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
894 | 10676 | 3/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
895 | 10677 | 4/4/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
896 | 10678 | 5/29/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
897 | 10679 | 1/9/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
898 | 10680 | 7/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
899 | 10681 | 11/12/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Other (specify) | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
900 | 10682 | 4/2/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
901 | 10683 | 4/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
902 | 10684 | 4/6/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
903 | 10685 | 4/11/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
904 | 10686 | 4/13/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
905 | 10687 | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
906 | 10688 | 10/31/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
907 | 10689 | 1/26/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
908 | 10690 | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | n‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
909 | 10691 | 2/25/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
910 | 10693 | 3/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
911 | 10694 | 7/10/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
912 | 10695 | 7/27/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
913 | 10696 | 8/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
914 | 10697 | 2/25/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
915 | 10698 | 4/18/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
916 | 10699 | 4/24/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | n‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
917 | 10700 | 7/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient
918 | 10701 | 8/25/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
919 | 10702 | 2/8/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
920 | 10703 | 11/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
921 | 10704 | 3/28/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
922 | 10705 | 12/3/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
923 | 10706 | 12/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
924 | 10707 | 8/8/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
925 | 10708 | 9/22/2004 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
926 | 10709 | 2/1/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
927 | 10710 | 11/21/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
928 | 10711 | 1/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
929 | 10712 | 10/8/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
930 | 10713 | 3/25/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
931 | 10715 | 2/5/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
932 | 10716 | 7/26/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
933 | 10717 | 4/12/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
934 | 10718 | 5/20/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
935 | 10719 | 6/1/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Hydrogen | Ambient pressure, within a component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
936 | 10720 | 4/8/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
937 | 10721 | 8/26/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
938 | 10722 | 9/3/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
939 | 10723 | 10/4/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
940 | 10724 | 10/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
941 | 10725 | 10/29/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
942 | 10726 | 11/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
943 | 10727 | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
944 | 10728 | 8/23/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
945 | 10729 | 4/3/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Lube Oil or grease | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
946 | 10730 | 3/16/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
947 | 10731 | 6/27/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
948 | 10732 | 4/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Other (specify) | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
949 | 10733 | 4/7/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Unknown | Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
950 | 10734 | 4/27/2004 | Not Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
951 | 10735 | 4/28/2006 | Not Challenging | Unknown | In‐Situ | Other (specify) |  | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
952 | 10736 | 12/6/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
953 | 10737 | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
954 | 10738 | 8/22/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin | No
955 | 10739 | 4/24/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
956 | 10740 | 10/8/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
957 | 10741 | 9/21/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
958 | 10742 | 4/11/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
959 | 10743 | 4/19/2001 | Unknown | In‐Situ | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | Unknown | Confined to the object of origin | No
960 | 10744 | 8/17/2001 | Not Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
961 | 10745 | 7/25/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
962 | 10746 | 5/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
963 | 10747 | 1/15/1999 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Insulation | Type not specified | Unknown | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
964 | 10748 | 5/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
965 | 10749 | 9/10/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
966 | 10750 | 2/28/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
967 | 10751 | 1/28/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
968 | 20264 | 1/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
969 | 20265 | 2/2/1990 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No
970 | 20266 | 2/19/1990 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | No damage | No
971 | 20267 | 3/12/1990 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
972 | 20268 | 4/19/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No
973 | 20269 | 4/30/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
974 | 20270 | 6/7/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No
975 | 20271 | 7/9/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
976 | 20272 | 9/10/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
977 | 20273 | 9/18/1990 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
978 | 20274 | 10/9/1990 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
979 | 20275 | 10/11/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
980 | 20276 | 10/12/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
981 | 20277 | 11/16/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (specify |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
982 | 20278 | 11/24/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
983 | 20279 | 11/28/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
984 | 20280 | 12/5/1990 | Undetermined (PC‐CH) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
985 | 20281 | 6/24/1991 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No
986 | 20282 | 9/17/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
987 | 20283 | 10/3/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
988 | 20284 | 10/14/1991 | Undetermined (NC‐PC) | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
989 | 20285 | 10/25/1991 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
990 | 20286 | 1/23/1992 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
991 | 20287 | 2/29/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
992 | 20288 | 3/9/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | No damage | No
993 | 20289 | 3/16/1992 | Undetermined (NC‐PC) | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Unknown | No
994 | 20290 | 4/26/1992 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Unknown | Unknown | No damage | No
995 | 20291 | 4/28/1992 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
996 | 20292 | 6/25/1992 | Undetermined (NC‐PC) | Personnel error: Misuse of material ignited | Gas | Hydrogen | Jet from a pressurized source | Other (specify) | Unknown | Unknown | Unknown | No
997 | 20293 | 9/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
998 | 20294 | 10/5/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
999 | 20295 | 10/12/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1000 | 20296 | 10/23/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1001 | 20297 | 11/17/1992 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1002 | 20298 | 1/11/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1003 | 20299 | 3/9/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1004 | 20300 | 3/30/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Insulation | Type not specified | Unknown | Unknown | Unknown | Unknown | Confined to the object of origin | No
1005 | 20301 | 4/13/1993 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1006 | 20302 | 7/25/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1007 | 20303 | 10/14/1993 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1008 | 20304 | 11/2/1993 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1009 | 20305 | 11/18/1993 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1010 | 20306 | 12/30/1993 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1011 | 20307 | 1/25/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1012 | 20308 | 3/9/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1013 | 20309 | 3/11/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1014 | 20310 | 3/26/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1015 | 20311 | 4/4/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1016 | 20312 | 7/27/1994 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify | Unknown | Unknown | Unknown | No
1017 | 20313 | 9/29/1994 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Other (specify | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1018 | 20314 | 12/19/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1019 | 20315 | 2/20/1995 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1020 | 20316 | 2/24/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1021 | 20317 | 4/10/1995 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Unknown | No
1022 | 20318 | 8/9/1995 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1023 | 20319 | 8/15/1995 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
1024 | 20320 | 3/21/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1025 | 20321 | 7/10/1996 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1026 | 20322 | 9/13/1996 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
1027 | 20323 | 1/8/1997 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
1028 | 20324 | 8/12/1997 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Insulation | Type not specified | Unknown | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1029 | 20325 | 1/16/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1030 | 20326 | 10/12/1998 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1031 | 20327 | 11/2/1998 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1032 | 20328 | 5/6/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
1033 | 20329 | 9/1/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1034 | 20330 | 10/3/1999 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
1035 | 20331 | 11/4/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1036 | 20332 | 12/14/1999 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1037 | 20333 | 1/12/1990 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1038 | 20334 | 2/20/1990 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Unknown | No
1039 | 20335 | 4/13/1990 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Other (specify) | Unknown | Unknown | No damage | No
1040 | 20336 | 2/14/1991 | Undetermined (NC‐PC) | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1041 | 20337 | 4/21/1991 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Other (specify) | Unknown | Unknown | No damage | No
1042 | 20338 | 10/11/1991 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Unknown | No
1043 | 20339 | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1044 | 20340 | 12/1/1992 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Unknown | Unknown | Unknown | Confined to the object of origin | No
1045 | 20341 | 3/31/1993 | Undetermined (NC‐PC) | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) |  | Other (specify) | Unknown | Unknown | Unknown | No
1046 | 20342 | 4/30/1993 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Other (specify) | Unknown | Unknown | Unknown | No
1047 | 20343 | 8/13/1993 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Other (specify) | Unknown | Unknown | No damage | No
1048 | 20344 | 2/20/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
1049 | 20345 | 3/28/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No
1050 | 20346 | 3/30/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to part of room or area of origin | No
1051 | 20347 | 4/15/1994 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1052 | 20348 | 4/16/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown | Unknown | Unknown | No
1053 | 20349 | 4/23/1994 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1054 | 20350 | 6/9/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to the object of origin | No
1055 | 20351 | 6/21/1994 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1056 | 20352 | 6/23/1994 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Confined to the object of origin (localized/single subcomponent) | No
1057 | 20353 | 7/13/1994 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1058 | 20354 | 10/8/1994 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Bundle | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1059 | 20355 | 10/31/1994 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1060 | 20356 | 2/19/1995 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No
1061 | 20357 | 5/24/1995 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin | No
1062 | 20358 | 1/23/1996 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1063 | 20359 | 3/3/1996 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Other (specify) | Unknown | Unknown | Confined to part of room or area of origin | No
1064 | 20360 | 5/25/1996 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Unknown | Unknown | Unknown | Confined to fire rated compartment of origin | No
1065 | 20361 | 1/7/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Unknown | No
1066 | 20362 | 3/2/1997 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1067 | 20363 | 7/27/1997 | Not Evaluated | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Unknown | No
1068 | 20364 | 12/4/1997 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
1069 | 20365 | 1/13/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Interior finish |  | Unknown | Unknown | Unknown | Unknown | No
1070 | 20366 | 2/6/1998 | Undetermined (NC‐PC) | Unknown | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Other (specify) | Unknown | Unknown | Unknown | No
1071 | 20367 | 2/24/1998 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Leak ‐ Oil soaked Insulation | Unknown | Unknown | Unknown | Unknown | No
1072 | 20368 | 6/7/1998 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1073 | 20369 | 6/14/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify | Unknown | Unknown | Unknown | No
1074 | 20370 | 7/1/1998 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1075 | 20371 | 9/9/1998 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Unknown | [6 empty] | No
1076 | 20372 | 11/23/1998 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1077 | 20373 | 3/16/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Unknown | No
1078 | 20374 | 3/19/1999 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1079 | 20375 | 3/29/1999 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1080 | 20376 | 7/29/1999 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1081 | 20377 | 2/8/2000 | Challenging | Personnel error: Misuse of heating devices | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
1082 | 20378 | 2/25/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
1083 | 20379 | 6/20/2000 | Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1084 | 20380 | 8/16/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1085 | 20381 | 10/17/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1086 | 20382 | 10/23/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1087 | 20383 | 11/5/2000 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1088 | 20385 | 12/27/2000 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | Insulation | Type not specified | Unknown | Other (specify) | Unknown | Unknown | Confined to the object of origin | No
1089 | 30265 | 8/5/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1090 | 30266 | 1/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1091 | 30268 | 8/9/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1092 | 30269 | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Fire not observed and fire type indeterminate from post‐inspectio | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1093 | 30270 | 3/16/2003 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1094 | 30271 | 9/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1095 | 30272 | 7/9/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1096 | 30275 | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Liquid | Transformer Oil |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1097 | 30276 | 7/24/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1098 | 30277 | 12/3/2007 | Potentially Challenging | Unknown | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1099 | 30278 | 10/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1100 | 30279 | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1101 | 30281 | 6/5/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1102 | 30282 | 11/26/2001 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1103 | 30283 | 3/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1104 | 30284 | 3/12/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1105 | 30285 | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1106 | 30286 | 6/18/2009 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Unknown | No
1107 | 30287 | 10/1/2009 | Potentially Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
1108 | 30288 | 4/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1109 | 30289 | 7/8/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
1110 | 30290 | 1/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1111 | 30291 | 3/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1112 | 30292 | 6/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1113 | 30293 | 8/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1114 | 30294 | 11/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1115 | 30295 | 3/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1116 | 30296 | 11/22/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
1117 | 30297 | 8/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1118 | 30298 | 4/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1119 | 30299 | 4/25/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1120 | 30300 | 5/13/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1121 | 30301 | 6/7/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1122 | 30302 | 1/26/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1123 | 30303 | 6/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1124 | 30304 | 11/29/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1125 | 30305 | 12/14/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ |  |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1126 | 30306 | 1/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1127 | 30307 | 3/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1128 | 30308 | 4/3/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1129 | 30309 | 7/21/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1130 | 30310 | 9/7/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1131 | 30311 | 9/24/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1132 | 30312 | 3/29/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1133 | 30313 | 11/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1134 | 30314 | 12/19/2001 | Undetermined (PC‐CH | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
1135 | 30316 | 3/16/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1136 | 30317 | 4/18/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1137 | 30318 | 5/16/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Fuel Oil |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1138 | 30319 | 7/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1139 | 30320 | 5/8/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1140 | 30321 | 11/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1141 | 30322 | 10/28/2006 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1142 | 30323 | 12/9/2006 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1143 | 30324 | 1/11/2007 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1144 | 30325 | 11/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1145 | 30326 | 5/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1146 | 30327 | 3/6/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | n‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1147 | 30330 | 4/30/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1148 | 30331 | 10/12/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1149 | 30332 | 4/6/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1150 | 30333 | 7/31/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient (Liquid) | Cleaning solvents or paint | Contained within reservoir | : Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1151 | 30334 | 9/27/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1152 | 30335 | 1/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1153 | 30338 | 3/30/2006 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1154 | 30339 | 6/21/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1155 | 30340 | 11/10/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1156 | 30341 | 1/2/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1157 | 30342 | 2/11/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Other (other personnel error, natural effect, etc. specify in comments) | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1158 | 30343 | 5/3/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1159 | 30344 | 1/23/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1160 | 30345 | 8/29/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1161 | 30346 | 10/22/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1162 | 30347 | 3/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1163 | 30348 | 11/22/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1164 | 30350 | 7/26/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1165 | 30351 | 5/14/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1166 | 30354 | 2/8/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic euiment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes
1167 | 30355 | 2/17/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1168 | 30356 | 11/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1169 | 30357 | 6/20/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1170 | 30358 | 8/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | Other electrical or electronic equipment | In‐Situ |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1171 | 30359 | 1/10/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1172 | 30360 | 4/21/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1173 | 30361 | 4/11/2001 | Potentially Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1174 | 30362 | 12/16/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1175 | 30363 | 5/5/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1176 | 30364 | 5/26/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1177 | 30365 | 9/8/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1178 | 30366 | 12/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1179 | 30367 | 3/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1180 | 30368 | 7/6/2004 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Structural component |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1181 | 30369 | 10/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1182 | 30370 | 10/31/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1183 | 30371 | 11/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
1184 | 30372 | 11/18/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1185 | 30373 | 11/20/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1186 | 30374 | 11/30/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1187 | 30375 | 5/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1188 | 30376 | 10/14/2007 | Not Challenging | Not Challenging | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1189 | 30377 | 11/3/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1190 | 30378 | 11/6/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1191 | 30379 | 11/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1192 | 30380 | 12/17/2007 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1193 | 30381 | 4/7/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1194 | 30382 | 5/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1195 | 30383 | 2/11/2009 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1196 | 30384 | 10/18/2000 | Not Challenging | Not Challenging | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1197 | 30385 | 10/27/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Mixed | Other (Specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1198 | 30386 | 5/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1199 | 30387 | 5/24/2001 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1200 | 30388 | 4/6/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1201 | 30389 | 10/18/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Contained within component | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1202 | 30390 | 5/7/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1203 | 30391 | 11/13/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1204 | 30392 | 3/20/2000 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1205 | 30393 | 3/24/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1206 | 30394 | 2/2/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1207 | 30395 | 3/21/2004 | Undetermined (PC‐CH) | Hot work (cutting/welding/grinding/etc.) | Hot work (cutting/welding/grinding/etc.) | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1208 | 30396 | 3/22/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1209 | 30397 | 4/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1210 | 30398 | 10/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1211 | 30400 | 9/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1212 | 30401 | 2/6/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1213 | 30402 | 4/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1214 | 30403 | 9/24/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1215 | 30404 | 4/21/2009 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1216 | 30405 | 10/26/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown |  |  | Arc/electric discharge | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
1217 | 30407 | 4/30/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1218 | 30408 | 3/19/2001 | Potentially Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1219 | 30409 | 8/21/2000 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1220 | 30410 | 10/25/2000 | Potentially Challenging | Unknown | In‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1221 | 30411 | 3/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1222 | 30412 | 4/25/2002 | Potentially Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1223 | 30413 | 4/25/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1224 | 30414 | 3/28/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1225 | 30415 | 4/29/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1226 | 30416 | 4/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1227 | 30417 | 3/20/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1228 | 30418 | 3/18/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1229 | 30419 | 10/4/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1230 | 30420 | 3/18/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1231 | 30421 | 3/5/2002 | Undetermined (NC‐PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin | No
1232 | 30422 | 11/27/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Confined to the object of origin (localized/single subcomponent) | No
1233 | 30423 | 3/17/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1234 | 30424 | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1235 | 30425 | 10/7/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1236 | 30426 | 10/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (broad/extensive damage) | No
1237 | 30429 | 5/6/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1238 | 30430 | 1/13/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1239 | 30431 | 6/18/2006 | Not Challenging | Unknown | Unknown |  |  | No Fire ‐ False actuation of detection device | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
1240 | 30433 | 6/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1241 | 30434 | 8/12/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1242 | 30435 | 8/16/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1243 | 30436 | 9/30/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1244 | 30437 | 10/6/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1245 | 30438 | 5/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1246 | 30439 | 3/21/2008 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1247 | 30440 | 10/26/2005 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1248 | 30441 | 9/5/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1249 | 30442 | 9/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1250 | 30443 | 12/31/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1251 | 30444 | 3/13/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1252 | 30445 | 10/18/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1253 | 30446 | 4/1/2003 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Unknown | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1254 | 30447 | 7/11/2004 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1255 | 30449 | 10/8/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1256 | 30452 | 8/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1257 | 30453 | 1/30/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Contained within component | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1258 | 30454 | 6/22/2009 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1259 | 30455 | 3/14/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1260 | 30456 | 3/7/2001 | Potentially Challenging | Potentially Challenging | Unknown |  |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1261 | 30457 | 10/24/2006 | Undetermined (NC‐PC) |  | Transient (Gas) | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1262 | 30458 | 1/18/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1263 | 30459 | 3/9/2003 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1264 | 30460 | 3/18/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1265 | 30461 | 3/23/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1266 | 30462 | 5/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1267 | 30463 | 10/28/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1268 | 30464 | 9/23/2008 | Not Challenging | Unknown | In‐Situ | Structural component |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1269 | 30465 | 9/24/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1270 | 30469 | 11/11/2007 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1271 | 30471 | 4/4/2008 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1272 | 30472 | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1273 | 30473 | 9/20/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1274 | 30474 | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
1275 | 30475 | 4/26/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1276 | 30476 | 10/12/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1277 | 30478 | 9/9/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1278 | 30479 | 9/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1279 | 30480 | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1280 | 30481 | 9/25/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Cleaning solvents or paint | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1281 | 30482 | 10/5/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
1282 | 30483 | 10/9/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
1283 | 30485 | 9/17/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1284 | 30487 | 12/4/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Gas | Other (specify) | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1285 | 30489 | 10/5/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1286 | 30493 | 7/24/2008 | Challenging | Electrical failure resulting in overheating materials | Liquid | Transformer Oil | Unconfined spill | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
1287 | 30498 | 6/21/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
1288 | 30500 | 5/29/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1289 | 30502 | 10/8/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1290 | 30503 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Liquid | Lube Oil or grease | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1291 | 30504 | 3/17/2002 | Not Challenging | : Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1292 | 30505 | 3/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1293 | 30506 | 12/17/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1294 | 30507 | 7/26/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1295 | 30508 | 3/26/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1296 | 30509 | 8/11/2009 | Not Challenging | False actuation of detector, no ignition or overheat condition |  |  |  | No Fire ‐ False actuation of detection device |  |  | : No damage | No
1297 | 30510 | 1/17/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1298 | 30511 | 1/23/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1299 | 30512 | 2/15/2006 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1300 | 30513 | 5/27/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1301 | 30514 | 3/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Other electrical or electronic equipment | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1302 | 30516 | 6/25/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1303 | 30517 | 7/29/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
1304 | 30519 | 1/5/2009 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
1305 | 30520 | 3/1/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1306 | 30521 | 9/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1307 | 30522 | 9/12/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1308 | 30523 | 9/14/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1309 | 30524 | 12/14/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin | No
1310 | 30525 | 3/7/2001 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1311 | 30526 | 6/12/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) | Pressurized in a container | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1312 | 30527 | 2/1/2002 | Not Challenging | Unknown | In‐Situ | Structural component |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1313 | 30528 | 2/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1314 | 30529 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1315 | 30530 | 3/23/2002 | Not Challenging | Unknown | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1316 | 30531 | 4/17/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1317 | 30532 | 6/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
1318 | 30533 | 2/10/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1319 | 30534 | 3/4/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1320 | 30535 | 4/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1321 | 30536 | 9/13/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) |  |  |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1322 | 30537 | 6/15/2005 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1323 | 30538 | 1/23/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1324 | 30539 | 2/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component |  |  | Confined to the object of origin | No
1325 | 30540 | 5/2/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1326 | 30541 | 7/6/2005 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1327 | 30542 | 7/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1328 | 30543 | 8/24/2005 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1329 | 30544 | 10/4/2005 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1330 | 30545 | 1/16/2006 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
1331 | 30546 | 4/26/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1332 | 30547 | 4/19/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1333 | 30548 | 7/24/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1334 | 30549 | 9/5/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component |  |  | Confined to the object of origin | No
1335 | 30550 | 10/5/2006 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1336 | 30551 | 10/20/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1337 | 30552 | 5/8/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1338 | 30553 | 8/28/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1339 | 30554 | 10/17/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1340 | 30555 | 4/1/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1341 | 30556 | 4/4/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1342 | 30557 | 4/30/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1343 | 30558 | 10/20/2008 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Unknown | No
1344 | 30559 | 11/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1345 | 30560 | 2/4/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1346 | 30561 | 4/3/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1347 | 30562 | 3/17/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1348 | 30563 | 3/9/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1349 | 30564 | 11/18/2003 | Not Challenging | Unknown | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
1350 | 30565 | 2/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | No damage | No
1351 | 30566 | 9/11/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1352 | 30567 | 10/17/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1353 | 30568 | 1/19/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1354 | 30569 | 10/16/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1355 | 30570 | 3/28/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
1356 | 30571 | 1/12/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  |  | No
1357 | 30572 | 5/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1358 | 30573 | 6/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Flaming combustion – external to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1359 | 30574 | 11/2/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin | No
1360 | 30576 | 8/15/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Unknown | No
1361 | 30577 | 3/3/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1362 | 30578 | 2/27/2003 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin | No
1363 | 30579 | 6/6/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1364 | 30580 | 6/21/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1365 | 30581 | 6/19/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to componen | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1366 | 30582 | 6/7/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to componen | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | No damage | No
1367 | 30583 | 6/30/2003 | Not Challenging | Unknown | Unknown |  |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
1368 | 30584 | 5/24/2001 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1369 | 30585 | 5/3/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1370 | 30586 | 1/11/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
1371 | 30587 | 3/4/2009 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No
1372 | 30588 | 5/14/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1373 | 30589 | 10/11/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1374 | 30590 | 12/22/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1375 | 30591 | 10/17/2005 | Not Challenging | Personnel error: Misuse of heating devices | Unknown |  |  | Other (specify) | Unknown | Unknown | Unknown | No
1376 | 30593 | 2/7/2008 | Undetermined (PC‐CH) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1377 | 30594 | 6/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
1378 | 30595 | 10/10/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1379 | 30596 | 10/17/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1380 | 30597 | 2/5/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Hydrogen |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1381 | 30598 | 11/20/2009 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1382 | 30599 | 3/23/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1383 | 30600 | 11/9/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1384 | 30601 | 9/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1385 | 30602 | 5/19/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1386 | 30603 | 1/13/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1387 | 30604 | 5/28/2005 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1388 | 30605 | 9/19/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1389 | 30606 | 12/19/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1390 | 30607 | 3/20/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1391 | 30608 | 1/10/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
1392 | 30609 | 4/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1393 | 30610 | 7/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Confined to the object of origin | No
1394 | 30693 | 2/3/2004 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1395 | 30694 | 8/10/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | Unknown | No damage | No
1396 | 30695 | 9/21/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Jet from a pressurized source | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No
1397 | 30696 | 9/26/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1398 | 30697 | 9/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1399 | 30698 | 2/22/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1400 | 30699 | 3/7/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1401 | 30700 | 4/19/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1402 | 30701 | 8/13/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Smoldering combustion – internal to component | None or insignificant – temperature at or close to ambient | No damage | No
1403 | 30702 | 9/11/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1404 | 30703 | 10/2/2007 | Not Challenging | Other (personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1405 | 30704 | 10/17/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1406 | 30705 | 9/20/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1407 | 30706 | 9/20/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1408 | 30707 | 10/1/2000 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1409 | 30708 | 2/6/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1410 | 30709 | 7/13/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1411 | 30710 | 9/19/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Moderate – temperature increase detectable, protective clothing not needed for room entry | No damage | No
1412 | 30711 | 11/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | No damage |  | Smoldering combustion – internal to component |  |  | Confined to the object of origin | No
1413 | 30712 | 4/24/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1414 | 30713 | 4/29/2002 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1415 | 30716 | 9/2/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1416 | 30717 | 12/10/2002 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1417 | 30718 | 4/15/2003 | Undetermined (NC‐PC) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1418 | 30719 | 6/11/2003 | Undetermined (PC‐CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1419 | 30720 | 7/2/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient (Liquid) | Fuel Oil | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1420 | 30721 | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Other (specify) | Other (specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1421 | 30722 | 10/19/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | Unknown | Confined to the object of origin | No
1422 | 30723 | 11/3/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1423 | 30724 | 11/3/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1424 | 30725 | 4/12/2000 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
1425 | 30726 | 5/19/2000 | Not Challenging | Transient | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1426 | 30727 | 10/30/2000 | Potentially Challenging | Trash (i.e., solid refuse collected for disposal) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1427 | 30728 | 12/21/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1428 | 30729 | 12/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1429 | 30730 | 3/5/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin | No
1430 | 30731 | 3/19/2001 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component |  |  | No damage | No
1431 | 30732 | 12/3/2001 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1432 | 30733 | 6/27/2002 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown | No
1433 | 30734 | 8/26/2002 | Potentially Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1434 | 30735 | 3/4/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify |  | Flaming combustion – internal to component | Unknown | Unknown | No damage | No
1435 | 30736 | 3/13/2003 | Undetermined (PC‐CH) | Unknown | Unknown |  | Unknown | Flaming combustion – internal to component | Unknown | Unknown | Unknown | No
1436 | 30737 | 5/12/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1437 | 30738 | 9/23/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | In‐Situ |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | Outside area, smoke only in fire plume | No
1438 | 30739 | 3/29/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component |  | None or insignificant – temperature at or close to ambient | No damage | No
1439 | 30740 | 2/6/2004 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | No damage | No
1440 | 30741 | 3/24/2004 | Not Challenging | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1441 | 30742 | 4/15/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1442 | 30743 | 4/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1443 | 30744 | Hot work (cutting/welding/grinding/etc.) | Not Challenging | Unknown | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1444 | 30745 | 10/10/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1445 | 30746 | 10/28/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1446 | 30747 | 11/6/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1447 | 30748 | 11/27/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1448 | 30749 | 1/9/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1449 | 30750 | 5/9/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1450 | 30751 | 3/28/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1451 | 30752 | 4/3/2007 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within reservoir | Flaming combustion – external to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1452 | 30753 | 5/16/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1453 | 30754 | 2/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1454 | 30755 | 4/7/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1455 | 30756 | 11/23/2008 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Hot work (cutting/welding/grinding/etc.) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1456 | 30757 | 8/24/2009 | Undetermined (NC‐PC) | Unknown | Transient | Hot work (cutting/welding/grinding/etc.) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1457 | 30758 | 9/3/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1458 | 40730 | 10/27/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1459 | 40731 | 2/13/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1460 | 40732 | 3/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1461 | 40733 | 3/14/2001 | Potentially Challenging | Unknown | Unknown | Hydrogen | Other (specify) | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1462 | 40734 | 3/19/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1463 | 40735 | 4/4/2001 | Potentially Challenging | Unknown | Gas | Hydrogen | Confined liquid spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1464 | 40736 | 4/15/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1465 | 40737 | 4/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | Liquid | Liquid | Other (specify) | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1466 | 40738 | 6/5/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1467 | 40739 | 7/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1468 | 40740 | 3/3/2003 | Not Challenging | Unknown | Unknown |  |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1469 | 40741 | Confined to the object of origin | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1470 | 40742 | 7/7/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Hot work (cutting/welding/grinding/etc.) |  | Smoldering combustion – internal to componen | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1471 | 40743 | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Hot work (cutting/welding/grinding/etc.) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1472 | 40744 | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Hot work (cutting/welding/grinding/etc.) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1473 | 40745 | 10/20/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | None or insignificant – temperature at or close to ambient | No
1474 | 40746 | 8/15/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1475 | 40747 | 4/17/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1476 | 40748 | 11/28/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1477 | 40749 | 6/13/2008 | Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | High – protective clothing needed for room entry | Confined to room of origin | No
1478 | 40750 | 11/16/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1479 | 50356 | 1/11/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1480 | 50357 | 3/21/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1481 | 50358 | 6/1/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1482 | 50359 | 8/24/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1483 | 50360 | 12/20/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1484 | 50361 | 4/11/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1485 | 50362 | 7/16/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1486 | 50364 | 10/4/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1487 | 50365 | 3/4/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1488 | 50366 | 3/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified | Unknown | No Fire ‐ False actuation of detection device | Unknown | Unknown | Confined to the object of origin | No
1489 | 50367 | 3/14/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1490 | 50368 | 6/6/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1491 | 50369 | 8/14/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1492 | 50370 | 10/23/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1493 | 50371 | 11/1/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1494 | 50372 | 5/9/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1495 | 50373 | 10/7/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1496 | 50374 | 4/22/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1497 | 50375 | 9/30/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1498 | 50376 | 9/30/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1499 | 50377 | 7/2/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1500 | 50378 | 7/27/2005 | Other electrical or electronic equipment | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1501 | 50379 | 2/24/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1502 | 50380 | 8/31/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1503 | 50381 | 12/14/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1504 | 50382 | 1/29/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Confined to the object of origin (localized/single subcomponent) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1505 | 50383 | 3/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1506 | 50384 | 3/22/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1507 | 50385 | 5/30/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1508 | 50387 | 3/29/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1509 | 50388 | 6/8/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1510 | 50389 | 6/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1511 | 50390 | 10/1/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1512 | 50391 | 7/2/2009 | Not Challenging | Unknown | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1513 | 50392 | 8/13/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1514 | 50393 | 10/17/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1515 | 50394 | 4/21/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1516 | 50395 | 4/16/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1517 | 50396 | 5/1/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1518 | 50397 | 1/13/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1519 | 50398 | 12/2/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify) |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1520 | 50399 | 2/26/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1521 | 50400 | 8/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1522 | 50401 | 10/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1523 | 50402 | 11/8/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1524 | 50403 | 11/8/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) | Other (specify) | Pressurized spray | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1525 | 50404 | 11/25/2005 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1526 | 50405 | 3/4/2006 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1527 | 50406 | 8/21/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1528 | 50407 | 3/11/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1529 | 50409 | 10/5/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Unknown |  |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Unknown | No
1530 | 50410 | 9/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1531 | 50411 | 7/9/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | Mechanical equipment malfunction/failure | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1532 | 50423 | 2/28/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1533 | 50424 | 3/15/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1534 | 50425 | 3/16/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1535 | 50426 | 5/2/2000 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Other (specify) | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1536 | 50427 | 8/19/2000 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1537 | 50428 | 9/20/2000 | Not Challenging | Unknown | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1538 | 50429 | 3/19/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1539 | 50430 | 2/18/2000 | Not Challenging | Mechanical equipment malfunction/failure | 3/19/2001 | Structural component |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1540 | 50432 | 3/19/2001 | Not Challenging | Electrical failure resulting in overheating materials | 3/19/2002 | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1541 | 50433 | 8/17/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1542 | 50434 | 10/28/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1543 | 50435 | 7/22/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1544 | 50436 | 8/12/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1545 | 50438 | 1/7/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1546 | 50439 | 3/3/2003 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1547 | 50440 | 10/13/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin | No
1548 | 50441 | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1549 | 50442 | 11/8/2004 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Other (specify) | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1550 | 50443 | 3/20/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Unknown |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1551 | 50444 | 4/27/2005 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1552 | 50445 | 4/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1553 | 50446 | 7/14/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1554 | 50447 | 9/14/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1555 | 50448 | 10/11/2005 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1556 | 50449 | 2/21/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1557 | 50450 | 2/28/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1558 | 50451 | 7/15/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1559 | 50452 | 8/18/2006 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1560 | 50453 | 8/22/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1561 | 50454 | 11/8/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1562 | 50455 | 11/30/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1563 | 50456 | 2/15/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1564 | 50457 | 7/28/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume
1565 | 50458 | 8/15/2007 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1566 | 50459 | 2/8/2008 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1567 | 50460 | 4/16/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1568 | 50461 | 4/24/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1569 | 50462 | 6/12/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1570 | 50463 | 4/11/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1571 | 50464 | 4/26/2000 | Not Challenging | Personnel error: Misuse of heating devices | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1572 | 50466 | 2/4/2005 | Not Challenging | Electrical failure resulting in overheating materials | Liquid | Lube Oil or grease | Contained within reservoir | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1573 | 50467 | 2/4/2006 | Undetermined (NC‐PC) | Unknown | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1574 | 50468 | 11/2/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1575 | 50469 | 7/28/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1576 | 50470 | 11/19/2008 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1577 | 50471 | 12/2/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1578 | 50472 | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1579 | 50473 | 6/26/2000 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1580 | 50474 | 8/29/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1581 | 50475 | 10/11/2000 | Undetermined (PC‐CH) |  | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Unknown
1582 | 50476 | 12/19/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1583 | 50477 | 3/18/2000 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Liquid) | Other (specify) | Contained within reservoir | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1584 | 50478 | 3/19/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1585 | 50479 | 3/22/2000 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1586 | 50480 | 4/7/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1587 | 50481 | 11/4/2006 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | Unknown | No damage | No
1588 | 50482 | 3/8/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin | No
1589 | 50483 | 3/11/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1590 | 50484 | 3/23/2008 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Other (specify | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1591 | 50486 | 4/20/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Other (specify) | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1592 | 50487 | 3/6/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1593 | 50488 | 5/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1594 | 50489 | 8/30/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1595 | 50490 | 9/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1596 | 50491 | 10/16/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1597 | 50492 | 11/2/2009 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1598 | 50494 | 2/5/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Flaming combustion – external to component |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1599 | 50495 | 11/11/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1600 | 50496 | 1/21/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Thermal insulation materials |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1601 | 50497 | 8/15/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1602 | 50499 | 4/1/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1603 | 50501 | : 11/6/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1604 | 50502 | 10/16/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1605 | 50503 | : 6/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : No damage | No
1606 | 50504 | : 5/20/2002 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Structural component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire |  | Unknown | : Confined to the object of origin (localized/single subcomponent) | No
1607 | 50506 | 12/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Single Cable | : Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1608 | 50507 | 11/15/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1609 | 50508 | 11/26/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | : Confined to the object of origin (localized/single subcomponent) | No
1610 | 50510 | 4/19/2000 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1611 | 50511 | : 5/15/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) |  | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1612 | 50512 | 5/31/2000 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1613 | 50513 | 8/27/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Other electrical or electronic equipment | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1614 | 50514 | 4/29/2009 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1615 | 50515 | 11/30/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | Flaming combustion – external to component |  | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1616 | 50516 | 10/5/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1617 | 50517 | 10/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1618 | 50518 | 11/18/2001 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Smoldering combustion – external to component | Smoldering combustion – external to component | Confined to the object of origin (localized/single subcomponent) | No
1619 | 50519 | 10/19/2009 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1620 | 50520 | 12/7/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1621 | 50521 | 2/1/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1622 | 50522 | 9/8/2003 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | : Arc/electric discharge | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1623 | 50523 | 9/19/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1624 | 50524 | 1/23/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1625 | 50525 | 12/18/2009 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1626 | 50526 | 12/7/2006 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | In‐Situ |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1627 | 50527 | 6/23/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1628 | 50528 | 6/19/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1629 | 50529 | 3/31/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1630 | 50530 | 10/21/2008 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1631 | 50534 | 1/7/2002 | Not Evaluated | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1632 | 50535 | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1633 | 50536 | 3/21/2002 | Not Evaluated | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1634 | 50537 | 3/23/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Interior finish |  | Fire not observed and fire type indeterminate from post‐inspectio | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1635 | 50538 | 3/27/2002 | Not Evaluated | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Other (specify) | Pressurized in a container | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1636 | 50539 | 5/22/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1637 | 50540 | 5/25/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1638 | 50541 | 4/6/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1639 | 50542 | 7/30/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1640 | 50543 | 3/27/2001 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1641 | 50545 | 9/18/2003 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Other (specify) |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1642 | 50546 | 12/1/2004 | Not Challenging | Unknown | Unknown |  |  | Other (specify) | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1643 | 50547 | 4/4/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1644 | 50548 | 6/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1645 | 50549 | 1/21/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1646 | 50550 | 6/9/2007 | Not Challenging | Electrical failure resulting in overheating materials | Unknown |  |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1647 | 50551 | 10/6/2008 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1648 | 50552 | 3/23/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1649 | 50553 | 5/2/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1650 | 50554 | 5/19/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1651 | 50555 | : 6/25/2003 | Not Challenging | Unknown | Unknown |  |  | Unknown | Unknown | Unknown | Unknown | No
1652 | 50556 | 2/25/2005 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Flaming combustion – external to component | No smoke present | Unknown | Confined to the object of origin (broad/extensive damage) | No
1653 | 50557 | 1/16/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1654 | 50558 | 1/2/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1655 | 50562 | 5/28/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1656 | 50563 | 11/16/2005 | Undetermined (PC‐CH) | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1657 | 50564 | 1/15/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1658 | 50565 | 8/26/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1659 | 50566 | 9/17/2008 | Not Challenging | High Energy Arc Fault (HEAF) | In‐Situ | Other electrical or electronic equipment |  | Explosion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1660 | 50569 | 3/24/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1661 | 50570 | 6/21/2004 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1662 | 50571 | 7/22/2004 | Not Challengin | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1663 | 50572 | 10/8/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1664 | 50573 | 8/24/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Other (specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1665 | 50574 | 9/16/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1666 | 50575 | 9/14/2007 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1667 | 50576 | 9/17/2004 | Not Challenging | Personnel error during test and maintenance activity | Transient (Liquid) | Other (specify) | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1668 | 50577 | 10/23/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1669 | 50578 | 11/23/2004 | Not Challenging |  | Liquid | Lube Oil or grease | Other (specify) | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | onfined to the object of origin (localized/single subcomponent) | No
1670 | 50579 | 5/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1671 | 50580 | 10/9/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to part of room or area of origin | No
1672 | 50581 | 6/24/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No
1673 | 50582 | 8/22/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within component | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No
1674 | 50583 | 9/3/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1675 | 50584 | 6/27/2005 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment |  | verheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1676 | 50585 | 10/8/2009 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1677 | 50586 | 9/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage) | No
1678 | 50587 | 2/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1679 | 50588 | 2/4/2006 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  | Overheating – no smoldering or flaming combustion | Confined to the object of origin (localized/single subcomponent | No
1680 | 50589 | 4/15/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Unknown | No
1681 | 50590 | 5/6/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1682 | 50591 | 5/29/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1683 | 50592 | 7/11/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1684 | 50593 | 10/4/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1685 | 50594 | 10/5/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1686 | 50595 | 10/28/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1687 | 50596 | 1/5/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1688 | 50597 | 12/18/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify) |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1689 | 50598 | 3/10/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion |  |  |  | No
1690 | 50599 | 3/31/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Single Cable | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1691 | 50600 | 12/2/2008 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1692 | 50601 | 8/30/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1693 | 50603 | 2/24/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1694 | 50604 | 11/27/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Structural component |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1695 | 50605 | 10/4/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to part of room or area of origin | No
1696 | 50606 | 10/8/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1697 | 50607 | 3/1/1997 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1698 | 50608 | 5/28/1997 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | Electrical arcing or sparks (non‐HEAF) | Transient |  | Temporary electrical wiring or equipment | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No
1699 | 50609 | 11/23/2000 | Not Evaluated | Mechanical equipment malfunction/failure | In‐Situ | Structural component |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1700 | 50610 | 5/30/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1701 | 50611 | 3/19/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Transient | Other (specify |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1702 | 50612 | 10/21/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1703 | 50613 | 7/3/2003 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1704 | 50614 | 3/9/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1705 | 50615 | 3/11/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1706 | 50616 | 3/21/2004 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Unknown | Unknown | Unknown | No
1707 | 50617 | 3/29/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1708 | 50618 | 9/14/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1709 | 50619 | 2/8/2006 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1710 | 506203 | 3/27/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1711 | 50621 | 9/11/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1712 | 50622 | 11/8/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1713 | 50623 | 12/15/2000 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1714 | 50624 | 5/14/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1715 | 50625 | 1/8/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets | Other (Specify) | Smoldering combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1716 | 50627 | 3/24/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Insulation | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
1717 | 50628 | 3/9/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1718 | 50629 | 10/16/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1719 | 50630 | 10/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1720 | 50631 | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1721 | 50632 | 10/27/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1722 | 50633 | 11/12/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients Form N |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1723 | 50634 | 3/6/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1724 | 50635 | 12/12/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1725 | 50636 | 2/10/2001 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment | Other (Specify) | Overheating – no smoldering or flaming combustion | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1726 | 50637 | 4/18/2001 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1727 | 50638 | 5/14/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1728 | 50639 | 11/10/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1729 | 50640 | 12/23/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1730 | 50641 | 3/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Pressurized in a container | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1731 | 50642 | 4/16/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1732 | 50643 | 4/18/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1733 | 50644 | 6/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1734 | 50645 | 12/23/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1735 | 50646 | 3/7/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1736 | 50647 | 8/12/2003 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipmentOther electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1737 | 50648 | 12/2/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
1738 | 50649 | 4/22/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Single Cable | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1739 | 50650 | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (specify) | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1740 | 50650 | 9/26/2003 | Not Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1741 | 50651 | 10/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Cleaning solvents or paint |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1742 | 50652 | 3/18/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1743 | 50653 | 10/4/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1744 | 50654 | 9/24/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1745 | 50655 | 12/4/2007 | Undetermined (NC‐PC) | Mechanical equipment malfunction/failure | In‐Situ | Other (specify |  | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1746 | 50656 | 8/18/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1747 | 50657 | 3/2/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1748 | 50658 | 4/24/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1749 | 50659 | 8/11/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1750 | 50660 | 9/24/2000 | Not Challenging | Personnel error: Misuse of heating devices | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1751 | 50661 | 4/25/2001 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Other (specify |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1752 | 50662 | 6/5/2001 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1753 | 50663 | 8/12/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1754 | 50664 | 6/29/2001 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1755 | 50665 | 9/17/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | In‐Situ |  | Other (specify | Overheating – no smoldering or flaming combustion | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1756 | 50666 | 3/22/2005 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1757 | 50667 | 3/28/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1758 | 50668 | 4/16/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1759 | 50669 | 1/3/2002 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1760 | 50670 | 10/12/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1761 | 50671 | 10/20/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1762 | 50672 | 4/5/2002 | Not Evaluated | In‐Situ | Other electrical or electronic equipment | Fire not observed and fire type indeterminate from post‐inspecti |  | Unknown | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1763 | 50673 | 4/5/2002 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | Unknown | Confined to part of room or area of origin | No
1764 | 50674 | 9/23/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1765 | 50675 | 8/12/2002 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1766 | 50676 | 11/29/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1767 | 50677 | 9/24/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Other (specify |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1768 | 50678 | 3/28/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1769 | 50679 | 10/4/2002 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Leak ‐ Oil soaked Insulation | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1770 | 50680 | 8/24/2006 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1771 | 50681 | 11/22/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1772 | 50682 | 4/10/2007 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1773 | 50683 | 5/18/2004 | Not Evaluated | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1774 | 50684 | 3/8/2007 | Not Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other (specify |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1775 | 50685 | 3/30/2007 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | No damage | No
1776 | 50686 | 4/4/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1777 | 50687 | 7/23/2007 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1778 | 50688 | 5/28/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1779 | 50689 | 10/17/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient (Gas) |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1780 | 50690 | 10/24/2005 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials | Contained within reservoir | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1781 | 50691 | 2/15/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Unconfined spill | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1782 | 50692 | 3/24/2008 | Not Evaluated | Personnel error: Misuse of heating devices | Liquid | Other (specify | Unconfined spill | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1783 | 50693 | 10/13/2008 | Not Evaluated | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1784 | 50694 | 10/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Liquid | Lube Oil or grease |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1785 | 50696 | 4/21/2008 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1786 | 50697 | 7/16/2008 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1787 | 50698 | 3/17/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1788 | 50699 | 4/7/2000 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (broad/extensive damage) | No
1789 | 50700 | 5/13/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1790 | 50701 | 5/24/2000 | Not Challenging | High Energy Arc Fault (HEAF | In‐Situ | Other electrical or electronic equipment |  | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1791 | 50702 | 6/25/2000 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  |  | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1792 | 50703 | 8/22/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin | No
1793 | 50704 | 12/22/2000 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1794 | 50705 | 4/15/2001 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1795 | 50706 | 4/17/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
1796 | 50707 | 4/25/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1797 | 50708 | 5/17/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1798 | 50709 | 10/26/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1799 | 50710 | 11/19/2001 | Not Challenging | False actuation of detector, no ignition or overheat condition | Unknown |  | Leak ‐ Oil soaked Insulation | Unknown | Unknown | Unknown | No Fire ‐ False actuation of detection device | No
1800 | 50711 | 11/20/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1801 | 50712 | 12/14/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1802 | 50713 | 1/1/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1803 | 50714 | 1/9/2002 | Not Challenging |  | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1804 | 50715 | 1/16/2002 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1805 | 50716 | 1/24/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1806 | 50717 | 5/21/2002 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin | No
1807 | 50718 | 3/20/2003 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1808 | 50719 | 8/1/2003 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1809 | 50720 | 8/4/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Structural component |  | Flaming combustion – external to component | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Confined to the object of origin (localized/single subcomponent) | No
1810 | 50721 | 8/13/2003 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In‐Situ | Other (specify |  | Overheating – no smoldering or flaming combustion | No smoke present | Unknown | Confined to the object of origin (localized/single subcomponent | No
1811 | 50722 | 10/10/2003 | Not Challenging | Unknown | Overheating – no smoldering or flaming combustion |  |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No
1812 | 50723 | 1/8/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment | Other (specify) | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
1813 | 50724 | 3/5/2004 | Not Challenging | Unknown | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1814 | 50725 | 3/10/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc | Liquid | Lube Oil or grease |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1815 | 50726 | 10/14/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1816 | 50728 | 1/20/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other (specify |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
1817 | 50729 | 4/4/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF |  |  |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1818 | 50730 | 3/1/2006 | Not Challenging | Unknown |  |  | Other (Specify) | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Unknown | No
1819 | 50731 | 2/11/2005 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | Transient | Other (specify |  | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1820 | 50732 | 11/7/2002 | Undetermined (NC‐PC | Mechanical equipment malfunction/failure | Insulation | Type not specified |  | Smoldering combustion – internal to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1821 | 50733 | 4/23/2004 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1822 | 50735 | 4/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1823 | 50736 | 4/10/2007 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent | No
1824 | 50738 | 3/13/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other (specify) |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1825 | 50739 | 3/28/2001 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | Leak ‐ Oil soaked Insulation | Overheating – no smoldering or flaming combustion | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1826 | 50740 | 5/16/2000 | Undetermined (NC‐PC) | Electrical failure resulting in overheating materials | In‐Situ | Other (specify | Single Cable | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1827 | 50741 | 9/18/2000 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1828 | 50742 | 10/4/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Insulation | Type not specified |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1829 | 50743 | 7/17/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other (specify |  | Other (specify | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1830 | 50744 | 8/3/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other (specify |  | Flaming combustion – internal to component | Unknown | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1831 | 50745 | 9/22/2009 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1832 | 50747 | 2/9/2007 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1833 | 50748 | 9/22/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1834 | 50749 | 10/28/2008 | Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to part of room or area of origin | Yes
1835 | 50750 | 1/10/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc | In‐Situ | Thermal insulation materials |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1836 | 50751 | 11/17/2008 | Not Challenging | Unknown | Overheating – no smoldering or flaming combustion |  |  | Overheating – no or flaming combustion | Unknown | Unknown | Unknown | No
1837 | 50753 | 12/11/2009 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1838 | 50754 | 1/23/2009 | Potentially Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
1839 | 50756 | 9/21/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1840 | 50757 | 9/7/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1841 | 50758 | 6/14/2004 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage) | No
1842 | 50759 | 7/29/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1843 | 50760 | 11/8/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1844 | 50761 | 1/25/2008 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1845 | 50762 | 10/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Other (specify |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1846 | 50763 | 11/14/2008 | Undetermined (NC‐PC) | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1847 | 50764 | 1/14/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1848 | 50765 | 10/12/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post‐inspectio | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent) | No
1849 | 50766 | 8/18/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | Spill confined by curbs or other physical feat | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1850 | 50767 | 6/1/2001 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1851 | 50768 | 1/1/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1852 | 50769 | 12/6/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1853 | 50770 | 1/30/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1854 | 50771 | 5/6/2003 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1855 | 50772 | 7/2/2003 | Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Severe smoke coming from source ‐ visibility near zero in small room, severe degredation of visibility for relatively large room, room entry would require full turn out gear | Severe – room entry not possible without venting or mitigation | Confined to room of origin
1856 | 50773 | 9/11/2003 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1857 | 50774 | 1/7/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1858 | 50775 | 2/13/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1859 | 50777 | 8/5/2004 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In‐Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1860 | 50778 | 10/11/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1861 | 50779 | 10/25/2004 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage) | No
1862 | 50780 | 1/6/2005 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1863 | 50781 | 3/10/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1864 | 50782 | 3/11/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1865 | 50783 | 6/27/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1866 | 50784 | 11/20/2005 | Undetermined (NC‐PC | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1867 | 50785 | 12/3/2005 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment | N/A | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1868 | 50786 | 3/10/2006 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1869 | 50787 | 1/4/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid |  | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1870 | 50788 | 3/8/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1871 | 50789 | 3/4/2007 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1872 | 50790 | 6/7/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1873 | 50791 | 10/25/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1874 | 50792 | 11/6/2007 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1875 | 50793 | 11/18/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1876 | 50794 | 3/4/2009 | Not Challenging | Mechanical equipment malfunction/failure | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1877 | 50795 | 7/12/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1878 | 50796 | 11/4/2009 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1879 | 50797 | 11/8/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1880 | 50798 | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1881 | 50799 | 12/12/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1882 | 50803 | 12/1/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1883 | 50804 | 1/13/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
1884 | 50805 | 2/12/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1885 | 50806 | 8/30/2004 | Not Challenging | Electrical failure resulting in overheating materials | Transient | Other (specify |  | Unknown | Outside area, smoke only in fire plume | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1886 | 50807 | 8/24/2007 | Not Challenging | Personnel error during test and maintenance activity | Transient (Gas | Other (specify |  | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1887 | 50808 | 3/21/2006 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Other (specify |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1888 | 50809 | 11/9/2000 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1889 | 50810 | 6/25/2000 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1890 | 50811 | 1/9/2001 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1891 | 50812 | 6/11/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1892 | 50813 | 9/3/2002 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1893 | 50814 | 5/31/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1894 | 50815 | 5/19/2005 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other (specify) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1895 | 50816 | 11/16/2005 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1896 | 50817 | 2/13/2006 | Not Challenging | Other (other personnel error, natural effect, etc. specify in comments | Gas | Hydrogen | Pressurized in a container | No Fire ‐ False actuation of detection device | No smoke present | None or insignificant – temperature at or close to ambient | Confined to structure of origin | No
1897 | 50818 | 3/21/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1898 | 50819 | 6/13/2008 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | No damageNone or insignificant – temperature at or close to ambient | No damage | No
1899 | 50820 | 10/23/2008 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent) | No
1900 | 50821 | 10/30/2008 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1901 | 50822 | 11/7/2008 | Not Challenging | Personnel error during test and maintenance activity | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Moderate – temperature increase detectable, protective clothing not needed for room entry | Confined to the object of origin (localized/single subcomponent | No
1902 | 50823 | 4/9/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1903 | 50824 | 9/13/2009 | Not Challenging | Mechanical equipment malfunction/failure | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1904 | 50825 | 10/1/2009 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
1905 | 50826 | 12/9/2009 | Not Challenging | Personnel error: Misuse of heating devices | In‐Situ | Other electrical or electronic equipment |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient |  | No
1906 | 50827 | 4/27/2002 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak ‐ Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source ‐ visibility significantly reduced in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1907 | 50828 | 10/2/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1908 | 50829 | 9/11/2004 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Heavy smoke coming from ignition source ‐ smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is still possible with SCBA | Unknown | Confined to the object of origin (broad/extensive damage | No
1909 | 50833 | 9/23/2008 | Potentially Challenging | Personnel error: Misuse of material ignited | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1910 | 50834 | 9/24/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1911 | 50835 | 10/1/2009 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc. | In‐Situ | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1912 | 50837 | 7/9/2001 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Unknown | No
1913 | 50838 | 11/19/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Plastic Sheets |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1914 | 50839 | 11/26/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1915 | 50840 | 11/28/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1916 | 50841 | 11/29/2001 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1917 | 50842 | 8/23/2002 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1918 | 50843 | 3/22/2003 | Not Evaluated | Unknown | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1919 | 50844 | 7/24/2003 | Not Evaluated | Personnel error during test and maintenance activity | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1920 | 50845 | 12/13/2003 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown | Unknown | Unknown | No
1921 | 50846 | 1/24/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1922 | 50847 | 1/27/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1923 | 50848 | 1/30/2005 | Not Evaluated | Unknown | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1924 | 50849 | 3/8/2005 | Not Evaluated | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1925 | 50850 | 4/1/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1926 | 50851 | 4/27/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other (specify |  | Flaming combustion – external to component | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
1927 | 50852 | 5/25/2005 | Not Evaluated | Electrical arcing or sparks (non‐HEAF) | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (broad/extensive damage | No
1928 | 50853 | 11/28/2005 | Not Evaluated | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1929 | 50854 | 9/18/2006 | Not Evaluated | Personnel error: Misuse of heating devices | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1930 | 50855 | 4/26/2008 | Not Evaluated | Hot work (cutting/welding/grinding/etc. | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1931 | 50856 | 1/31/2008 | Not Evaluated | Electrical arcing or sparks (non‐HEAF | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1932 | 50857 | 11/6/2009 | Not Evaluated | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1933 | 50860 | 12/14/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal |  | Unknown | Unknown | Unknown | Confined to the object of origin (broad/extensive damage | No
1934 | 50861 | 12/20/2004 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1935 | 50862 | 2/9/2006 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Overheating – no smoldering or flaming combustion | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (broad/extensive damage | No
1936 | 50863 | 9/30/2008 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1937 | 50864 | 9/24/2009 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1938 | 50865 | 1/31/2000 | Not Challenging | Personnel error: Misuse of material ignited | Transient (Gas |  |  | Flaming combustion – external to component | No smoke present | None or insignificant – temperature at or close to ambient | No damage | No
1939 | 50866 | 3/28/2001 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1940 | 50867 | 10/31/2000 | Not Challenging | Electrical arcing or sparks (non‐HEAF | Transient | Cellulosic materials including wood, paper or other solid transients |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1941 | 50868 | 7/3/2001 | Not Challenging | Unknown | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | Unknown | Unknown | No damage | No
1942 | 50869 | 10/25/2001 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other electrical or electronic equipment |  | Unknown | Unknown | Unknown | Confined to the object of origin (localized/single subcomponent | No
1943 | 50870 | 1/8/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1944 | 50872 | 3/31/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1945 | 50873 | 5/9/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | In‐Situ | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1946 | 50874 | 7/12/2002 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1947 | 50875 | 11/10/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1948 | 50876 | 11/13/2002 | Potentially Challenging | Electrical arcing or sparks (non‐HEAF) | Insulation | Type not specified | Unknown | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1949 | 50878 | 11/12/2002 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1950 | 50879 | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1951 | 50880 | 11/15/2002 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1952 | 50881 | 12/31/2002 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown | Unknown | Unknown | No
1953 | 50882 | 1/20/2003 | Not Challenging | Electrical arcing or sparks (non‐HEAF | In‐Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1954 | 50883 | 4/18/2003 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1955 | 50884 | 2/23/2004 | Undetermined (NC‐PC | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or other solid transients |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1956 | 50885 | 6/17/2003 | Not Challenging | Personnel error: Misuse of material ignited | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1957 | 50886 | 2/27/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1958 | 50887 | 3/7/2004 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1959 | 50888 | 7/16/2004 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1960 | 50889 | 3/22/2005 | Not Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Unknown | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1961 | 50890 | 4/3/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient (Gas |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1962 | 50891 | 4/8/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambien | Confined to the object of origin (localized/single subcomponent | No
1963 | 50892 | 4/12/2005 | Not Challenging | Hot work (cutting/welding/grinding/etc. | Transient | Other (specify | Jet from a pressurized source | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1964 | 50893 | 12/2/2005 | Potentially Challenging | Electrical failure resulting in overheating materials | In‐Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1965 | 50894 | 3/12/2006 | Not Challenging | Unknown | Gas | Hydrogen |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1966 | 50895 | 5/13/2007 | Potentially Challenging | Unknown |  |  |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | No damage | No
1967 | 50896 | 5/13/2007 | Undetermined (NC‐PC) | Hot work (cutting/welding/grinding/etc | Transient | Other (specify | Leak ‐ Oil soaked Insulation | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1968 | 50897 | 12/22/2007 | Not Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent | No
1969 | 50899 | 10/27/2008 | Challenging | Explosion (hydrogen gas ignition, fuel vapor ignition, other volatile fluid vapor ignition) | Gas | Other (specify | Other (specify | Explosion | Unknown | Unknown | Unknown | No
1970 | 50900 | 5/1/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal |  | Smoldering combustion – external to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1971 | 50901 | 8/28/2009 | Not Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Smoldering combustion – internal to component | Light smoke coming from ignition source ‐ minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No
1972 | 50907 | 1/9/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Lube Oil or Grease | Contained within component | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished | 0 ft Vertical, 0 ft Horizontal extinguished
1973 | 50908 | 1/20/2010 | Challenging | Mechanical equipment malfunction/failure |  |  |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume |  | Confined to room of origin |  |  | 10 | 10 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal Damage was limited t | 0 ft Vertical, 0 ft Horizontal | 10 ft vertical 10 ft horizontal Damage was limited | 2 ft vertical 2 ft horizontal Fuel Supply - Lube O
1974 | 50909 | 3/7/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Insulation | Type not specified | Single Cable Tray | Explosion | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1975 | 50910 | 3/28/2010 | Challenging | High Energy Arc Fault (HEAF) | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to structure of origin |  |  | 25 | 25 | 25 ft Vertical, 25 ft Horizontal extinguishment | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal spacial separation | 25 ft vertical 25 ft horizontal extinguishment | 25 ft vertical 25 ft horizontal extinguishment
1976 | 50911 | 4/18/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 |  | 3 | 3
1977 | 50912 | 5/5/2010 | Challenging | Electrical arcing or sparks (non-HEAF) | Gas | Hydrogen | Ambient pressure, within a component |  | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1978 | 50913 | 5/12/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1979 | 50914 | 6/8/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire was extinguished promptly. | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe | 0 ft vertical 0 ft horizontal Fire was extinguishe
1980 | 50916 | 7/13/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1981 | 50917 | 7/13/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1982 | 50919 | 8/22/2010 | Undetermined (PC-CH) | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In-Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal The fire was extinguished using a dry chemical extinguisher and | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Proper fire fighting | 0 ft vertical 0 ft horizontal The fire was extingu
1983 | 50921 | 10/11/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage due to fire. | 0 ft vertical 0 ft horizontal Fire was promptly ex | 0 ft vertical 0 ft horizontal No evidence of secon | 0 ft vertical 0 ft horizontal No smoke damage | 0 ft vertical 0 ft horizontal Fire was extinguishe
1984 | 50922 | 11/7/2010 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Contained within component | Explosion | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1985 | 50923 | 12/19/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal Power to the heater | 0 ft vertical 0 ft horizontal No suppression was u | 0 ft vertical 0 ft horizontal There was no evidenc | 1 ft vertical 1 ft horizontal Power to the heater | 1 ft vertical 1 ft horizontal Power to the heater
1986 | 50925 | 2/8/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal Suppression via CO2, | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Unit 1 Equipment | 0 ft vertical 0 ft horizontal The Unit 1 Equipment
1987 | 50926 | 2/12/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Explosion | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 20 | 20 | 5 ft vertical 2 ft horizontal Phase to phase fault | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 20 ft vertical 20 ft horizontal Smoke affected the | 5 ft vertical 2 ft horizontal When the metallic bu
1988 | 50928 | 3/23/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1989 | 50930 | 3/29/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0.4 | 0.4 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0.4 ft vertical 0.4 ft horizontal Quick detection
1990 | 50931 | 5/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure |  | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1991 | 50935 | 6/7/2011 | Challenging | Electrical arcing or sparks (non-HEAF) |  | Other electrical or electronic equipment |  | Arc/electric discharge | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 12 | 12 | 3 ft vertical 3 ft horizontal Deenergized electric | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 12 ft vertical 12 ft horizontal Cabinets and suppr | 6 ft vertical 6 ft horizontal Deenergized electric
1992 | 50936 | 6/25/2011 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Type not specified |  | Arc/electric discharge | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to the object of origin (localized/single subcomponent) | Yes collateral damage occurred | Yes | 4 | 2 | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal THE AREA EFFECTED BY | 0 ft vertical 0 ft horizontal | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE | 4 ft vertical 2 ft horizontal ISOLATION TO THE BRE
1993 | 50939 | 10/4/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1994 | 50942 | 11/1/2011 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or grease |  | Other (specify) | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Separation distance | 0 ft vertical 0 ft horizontal None. No suppression | 0 ft vertical 0 ft horizontal None. | 0 ft vertical 0 ft horizontal Smoke spread from lo | 0 ft vertical 0 ft horizontal Design of motor bear
1995 | 50944 | 11/16/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1996 | 50945 | 12/21/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) |  | Type not specified |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 1 | 2 | 0 ft vertical 0 ft horizontal Fire extinguished wi | 0 ft vertical 0 ft horizontal Suppression system d | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal Very light smoke, no | 1 ft vertical 2 ft horizontal Fire extinguished wi
1997 | 50946 | 1/23/2012 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) |  | Cellulosic materials including wood, paper or ot | NA, Insulation Multiple Bundles | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 1 | 1 | 1 ft vertical 1 ft horizontal steel cabinet | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal steel cabinet
1998 | 50949 | 4/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) |  | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | No smoke present | Outside area, elevated temperatures only in the fire plume | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
1999 | 50950 | 5/21/2012 | Undetermined (PC-CH) | Electrical arcing or sparks (non-HEAF) | Insulation | Thermoset | Single Cable | Arc/electric discharge | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 1 | 3 | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Three CO2 extinguish | 0 ft vertical 0 ft horizontal Cable is IEEE 383; w | 0 ft vertical 0 ft horizontal Fault occurred in an | 1 ft vertical 3 ft horizontal Cable is IEEE 383; w
2000 | 50951 | 5/24/2012 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 5 | 3 | 5 ft vertical 3 ft horizontal Electrical fault occ | 0 ft vertical 0 ft horizontal N/A | 0 ft vertical 0 ft horizontal N/A | 5 ft vertical 3 ft horizontal Electrical fault occ | 5 ft vertical 3 ft horizontal Electrical fault occ
2001 | 50952 | 6/21/2012 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation | Fire not observed and fire type indeterminate from post-inspection | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal Insulation was the o | 0 ft vertical 0 ft horizontal Response and extingu | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Detection and dispat
2002 | 50956 | 10/22/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Type not specified | Multiple Cables Not In Tray or Bundle | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 3 | 3 | 3 ft vertical 3 ft horizontal Design of the electr | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 1 ft vertical 1 ft horizontal Design of the electr | 1 ft vertical 1 ft horizontal Design of the electr
2003 | 50968 | 4/18/2012 | Potentially Challenging | Personnel error during test and maintenance activity | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2004 | 50969 | 11/11/2012 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment | Ambient pressure, within a component | Explosion | Outside area, smoke only in fire plume | Outside area, elevated temperatures only in the fire plume | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2005 | 50977 | 1/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | Liquid | Transformer Oil | Contained within | Explosion | Outside area, smoke only in fire plume |  | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 40 | 0 | 40 ft vertical 0 ft horizontal Exterior fire | 0 ft vertical 0 ft horizontal None, due to suppres | 0 ft vertical 0 ft horizontal Contained at the tra | 0 ft vertical 0 ft horizontal No smoke damage | 40 ft vertical 0 ft horizontal Exterior Fire
2006 | 50982 | 12/20/2010 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None | 0 ft vertical 0 ft horizontal None
2007 | 50983 | 9/22/2010 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other (specify) |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire team putting ou | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal NA | 0 ft vertical 0 ft horizontal Fire team putting ou
2008 | 50985 | 3/26/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Unknown | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2009 | 50986 | 3/28/2010 | Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2010 | 50992 | 11/17/2010 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2011 | 50994 | 2/13/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Acetylene |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2012 | 51002 | 11/10/2010 | Not Challenging/Undeter | Personnel error during test and maintenance activity | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2013 | 51005 | 4/30/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal No physical suppress | 0 ft vertical 0 ft horizontal No secondary ignitio | 0 ft vertical 0 ft horizontal The Air Arc Machine | 0 ft vertical 0 ft horizontal The Air Arc Machine
2014 | 51007 | 1/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2015 | 51013 | 11/29/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) |  | Other electrical or electronic equipment |  | Arc/electric discharge | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2016 | 51014 | 3/27/2012 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Temporary electrical wiring or equipment |  | Unknown | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2017 | 51026 | 3/30/2010 | Potentially Challenging | Mechanical equipment malfunction/failure | In Situ | Other (specify) |  | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 10 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 10 ft vertical 10 ft horizontal | 1 ft vertical 1 ft horizontal
2018 | 51027 | 5/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified | Other (Specify | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire | Unknown | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2019 | 51032 | 5/2/2010 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In Situ | Other (specify) |  | Arc/electric discharge | Unknown |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal The motor casing con | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2020 | 51040 | 4/11/2012 | Challenging | Hot work (cutting/welding/grinding/etc.) |  |  |  | Unknown | Unknown |  | Confined to part of room or area of origin |  |  | 30 | 10 | 30 ft vertical 10 ft horizontal Acetylene/oxygen b | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Contained mostly ins | 30 ft vertical 10 ft horizontal Damage was limited
2021 | 51044 | 3/11/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Fuel Oil |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2022 | 51048 | 3/24/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient |  |  | Flaming combustion – internal to component | Unknown |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2023 | 51051 | 4/6/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Unknown | Unknown |  | Unknown | Unknown | Unknown | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2024 | 51057 | 5/2/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Fire confined to tra
2025 | 51081 | 12/14/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2026 | 51082 | 4/4/2011 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2027 | 51085 | 4/27/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2028 | 51088 | 4/5/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2029 | 51090 | 2/15/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2030 | 51092 | 3/20/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Type not specified |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2031 | 51093 | 1/17/2013 | Challenging | Unknown | Liquid | Transformer Oil | Contained within component | Explosion | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin |  |  | 0 | 10 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 10 ft horizontal Off site fire depar | 0 ft vertical 0 ft horizontal
2032 | 51109 | 10/15/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or ot |  | Smoldering combustion – internal to component | Unknown |  | Confined to the object of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2033 | 51111 | 11/2/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  |  | Unknown |  | Unknown |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2034 | 51113 | 10/5/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2035 | 51117 | 3/11/2013 | Potentially Challenging | Personnel error during test and maintenance activity | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2036 | 51118 | 4/12/2011 | Potentially Challenging |  | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Unknown |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2037 | 51125 | 12/31/2011 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other (specify) |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2038 | 51132 | 4/2/2012 | Potentially Challenging | Unknown | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal De-energized compone | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2039 | 51135 | 3/12/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | nsulation | Type not specified | Single Cable | Smoldering combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2040 | 51136 | 1/19/2011 | Potentially Challenging |  | Transient | Temporary electrical wiring or equipment | Single Cable |  | Outside area, smoke only in fire plume |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal isolated location | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2041 | 51140 | 11/4/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak - Oil soaked | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2042 | 51146 | 4/3/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Distance of transfor | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No suppression actio | 0 ft vertical 0 ft horizontal No smoke damage. | 0 ft vertical 0.3 ft horizontal Cabinet wall paint
2043 | 51152 | 4/11/2013 | Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In-Situ | Other (specify) |  | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 12 | 5 ft vertical 8 ft horizontal Fire Brigade respons | 30 ft vertical 0 ft horizontal Ground floor floor | 0 ft vertical 2 ft horizontal configuration and lo | 0 ft vertical 0 ft horizontal Origin of fire was o | 8 ft vertical 12 ft horizontal Fire Brigade respon
2044 | 51153 | 1/28/2010 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or ot |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2045 | 51154 | 8/2/2012 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Gas | Hydrogen | Jet from a pressurized source | Flaming combustion – external to component | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2046 | 51157 | 9/20/2010 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Cellulosic materials including wood, paper or ot |  | Flaming combustion – internal to component | Outside area, smoke only in fire plume |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2047 | 51158 | 10/4/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  | Flaming combustion – internal to component | No smoke present | None or insignificant – temperature at or close to ambient | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2048 | 51160 | 9/25/2010 | Challenging | Mechanical equipment malfunction/failure | Gas | Hydrogen | Ambient pressure, within a compartment | Flaming combustion – external to component | Outside area, smoke only in fire plume |  | Confined to part of room or area of origin | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2049 | 51162 | 10/10/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In-Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2050 | 51164 | 9/19/2011 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Other (specify) |  |  | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2051 | 51166 | 6/10/2012 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Other Transient Combustible (specify) |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2052 | 51168 | 12/3/2012 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Cellulosic materials including wood, paper or ot |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Unknown | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2053 | 51171 | 7/13/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2054 | 51172 | 3/21/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2055 | 51176 | 5/4/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within reservoir | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2056 | 51180 | 5/16/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other (specify) |  | Flaming combustion – internal to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished | 0 ft vertical 0 ft horizontal extinguished
2057 | 51181 | 9/14/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2058 | 51184 | 12/2/2011 | 12/2/2011 | Hot work (cutting/welding/grinding/etc.) | In-Situ | Structural component |  | Flaming combustion – external to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2059 | 51186 | 4/20/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Gas | Other (specify) | Other (specify) | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2060 | 51187 | 4/17/2013 | Challenging | High Energy Arc Fault (HEAF) | Liquid | Transformer Oil | Contained within component | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 1 | 2 | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 2 ft horizontal Suppression was conc | 1 ft vertical 1 ft horizontal Cable attached to ca | 1 ft vertical 1 ft horizontal The fire was outside | 1 ft vertical 2 ft horizontal Cable was charred, b
2061 | 51188 | 5/20/2013 | Undetermined (PC-CH) | Mechanical equipment malfunction/failure | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished. | 0 ft vertical 0 ft horizontal Fire extinguished.
2062 | 51190 | 4/2/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2063 | 51191 | 4/27/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Transformer Oil |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal Fire extinguished | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2064 | 51193 | 5/21/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Other (specify) | Other (specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2065 | 51194 | 7/2/2013 | Challenging | High Energy Arc Fault (HEAF) | In-Situ | Interior finish |  | Arc/electric discharge | No smoke present |  | Confined to the object of origin (broad/extensive damage) | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2066 | 51196 | 7/11/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or Grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2067 | 51199 | 7/26/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 30 | 20 | 30 ft vertical 20 ft horizontal The arc flash thre | 0 ft vertical 0 ft horizontal No collateral damage | 0 ft vertical 0 ft horizontal The arc flash threw | 30 ft vertical 20 ft horizontal Smoke was moderate | 30 ft vertical 20 ft horizontal The arc flash thre
2068 | 51201 | : 8/8/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) |  |  | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal Damage was confined | 0 ft vertical 0 ft horizontal Damage was confined
2069 | 51207 | 9/2/2013 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Contained within component | Flaming combustion – external to component | Unknown |  | Confined to original component did not affect external components (however fire had external flames | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2070 | 51209 | 7/31/2013 | Undetermined (NC-PC) | Electrical failure resulting in overheating materials | In-Situ | Other (specify) |  | Fire not observed and fire type indeterminate from post-inspection | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal | 0 ft vertical 0 ft horizontal
2071 | 51216 | 1/3/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No
2072 | 51219 | 2/12/2010 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | Liquid | Lube Oil or grease | Leak - Oil soaked Insulation | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2073 | 51220 | 3/26/2010 | Undetermined (NC-PC) | Hot work (cutting/welding/grinding/etc.) | Transient | Temporary thermal insulation materials |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2074 | 51221 | 7/20/2011 | Potentially Challenging | Overheated Material (lube oil, pump packing, thermal insulation, etc.) | In-Situ | Thermal insulation materials |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2075 | 51222 | 10/12/2011 | Challenging | Electrical failure resulting in overheating materials | Transient | Thermal insulation materials |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2076 | 51231 | 4/7/2014 | Undetermined (NC-PC) | Other (other personnel error, natural effect, etc. specify in comments) | Transient | Other (Specify) |  | Flaming combustion – internal to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 3 | 3 | 2 ft Vertical, 2 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 2 ft Vertical, 2 ft Horizontal | 3 ft Vertical, 3 ft Horizontal
2077 | 51254 | 10/13/2012 | Potentially Challenging |  | In-Situ | Thermal insulation materials |  | Fire not observed and fire type indeterminate from post-inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Small fire involving motor windings no damage to other compo | 0 ft Vertical, 0 ft Horizontal Suppressed by opening breaker, no other actions required | 0 ft Vertical, 0 ft Horizontal No secondary ignition noted | 0 ft Vertical, 0 ft Horizontal Light smoke produced, ventilation in turbine building | 0 ft Vertical, 0 ft Horizontal No adjacent components exposed to heat.
2078 | 51256 | 6/13/2013 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2079 | 51257 | 5/16/2011 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Unknown |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2080 | 51258 | 7/10/2013 | Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment | Type not specified | Flaming combustion – external to component | No smoke present |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2081 | 51265 | 8/24/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2082 | 51273 | 4/2/2013 | Undetermined (NC-PC) | Human Error | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | No smoke present |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 5 | 5 | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal No suppression required. Fire self-extinguished with loss of po | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h | 0 ft Vertical, 0 ft Horizontal | 5 ft Vertical, 5 ft Horizontal Arc flash occurred with no other combustibles in area except h
2083 | 51274 | 12/9/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post-inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2084 | 51276 | 8/14/2013 | Potentially Challenging | Human Error | Gas | Hydrogen | Ambient pressure, within a compartment | Explosion | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2085 | 51278 | 11/5/2013 | Challenging | Electrical failure resulting in overheating materials | Insulation | Cable Tray Stack | Type not specified | Arc/electric discharge | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to part of room or area of origin | Yes collateral damage occurred | Yes | Vertical Distance (ft): 3.00 | Vertical Distance (ft): 3.00 | Damage limited to |  |  | Vertical Distance (ft): 7.00; Horizontal Distance (ft): 80.00 | Vertical Distance (ft): 3.00; Horizontal Distance (ft): 5.0
2086 | 51280 | 12/21/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Lube Oil or Grease | Other (specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2087 | 51287 | 10/6/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2088 | 51289 | 10/26/2013 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | In-Situ | Thermal insulation materials |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire. | 0 ft Vertical, 0 ft Horizontal No other flammable items were in the area of the fire.
2089 | 51291 | 12/9/2013 | Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Arc/electric discharge | Outside area, smoke only in fire plume |  | Extended beyond structure of origin | Yes collateral damage occurred | Yes | 50 | 20 | 50 ft Vertical, 20 ft Horizontal Transformer fire outdoors, concrete separation walls betwe | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2090 | 51293 | 11/6/2013 | Potentially Challenging | Hot work (cutting/welding/grinding/etc.) | Transient | Trash (i.e., solid refuse collected for disposal) |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti | 0 ft Vertical, 0 ft Horizontal Hot Work Fire Watch detected the Fire, stopped Hot Work Acti
2091 | 51295 | 11/1/2013 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Other (specify) | Leak - Oil soaked Insulation | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2092 | 51296 | 11/30/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2093 | 51304 | 1/18/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Thermal insulation materials |  | Fire not observed and fire type indeterminate from post-inspection | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. no secondary i | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal Damage contained to the inverter transformer. No damage be
2094 | 51308 | 4/7/2012 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2095 | 51309 | 3/7/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Multiple Cables Not In Tray or Bundle | Type not specified | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2096 | 51310 | 4/17/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | No smoke present |  | Confined to the object of origin (localized/single subcomponent) | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2097 | 51315 | 3/20/2014 | Potentially Challenging | Other (other personnel error, natural effect, etc. specify in comments) | Liquid | Lube Oil or Grease | Other (specify) | Flaming combustion – internal to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2098 | 51316 | 4/12/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2099 | 51317 | 4/2/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | Insulation | Single Cable Tray | Type not specified | Flaming combustion – external to component | Heavy smoke coming from ignition source - smoke obscures vicinity of fire such that it is difficult to locate the origin of the fire, room entry is stil |  | Confined to part of room or area of origin | -1 | -1 | 10 | 10 | 2 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 2 ft Horizontal fire suppression equipment put out fire quickly to prevent furth | 10 ft Vertical, 10 ft Horizontal fire suppression equipment put out fire quickly to prevent fu | 4 ft Vertical, 5 ft Horizontal fire suppression equipment put out fire quickly to prevent furth
2100 | 51318 | 4/3/2014 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w | 0 ft Vertical, 0 ft Horizontal The 480VAC connector was located outside of the building. All | 0 ft Vertical, 0 ft Horizontal A craftsman saw the arc and notified a project team member w
2101 | 51322 | 6/19/2014 | Undetermined (NC-PC) |  | Transient | Other (specify) |  | Flaming combustion – internal to component | No smoke present |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2102 | 51324 | 5/23/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  |  | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | -1 | -1 | 1 | 1 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 1 ft Vertical, 1 ft Horizontal Quick Fire brigade response. | 0.25 ft Vertical, 0 ft Horizontal Fire was limited to inside of the 3KI inverter. The metal cabi
2103 | 51328 | 7/27/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Fire not observed and fire type indeterminate from post-inspection | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2104 | 51331 | 9/4/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | In Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (localized/single subcomponent) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da | 0 ft Vertical, 0 ft Horizontal Fire Watch and Fire extiguisher. Only the lockout relay was da
2105 | 51332 | 10/6/2014 | Challenging | Electrical arcing or sparks (non-HEAF) | In Situ | Other electrical or electronic equipment |  | Flaming combustion – external to component | Moderate smoke coming form ignition source - visibility significantly reduced in vicinity of fire |  | Confined to part of room or area of origin | -1 | -1 | 8 | 3 | 1 ft Vertical, 1 ft Horizontal Fire immediately extinguished by site operator in room with po | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 8 ft Vertical, 3 ft Horizontal Fire initiated in closed electrical component control cabinet. S | 2 ft Vertical, 2 ft Horizontal Fire immediately extinguished by site operator in room with po
2106 | 51335 | 9/15/2014 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment | Type not specified | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No collateral damage, breaker tripped and limited to extension | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord | 0 ft Vertical, 0 ft Horizontal No heat damage, breaker tripped and limited to extension cord
2107 | 51339 | 9/28/2014 | Potentially Challenging | Mechanical equipment malfunction/failure | Liquid | Lube Oil or Grease | Contained within component | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to original component did not affect external components (however fire had external flames | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off | 0 ft Vertical, 0 ft Horizontal Fire self-extinguished once the pump was turned off
2108 | 51354 | 3/28/2010 | Potentially Challenging | Electrical arcing or sparks (non-HEAF) | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | 0 | 0 | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal NONE | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2109 | 51366 | 4/21/2010 | Potentially Challenging | Electrical failure resulting in overheating materials | Transient | Temporary electrical wiring or equipment |  | Flaming combustion – external to component | Very light smoke (detectable odor no visibility reduction) |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2110 | 51374 | 3/1/2014 | Undetermined (NC-PC) | Electrical arcing or sparks (non-HEAF) | Transient | Temporary electrical wiring or equipment |  | Arc/electric discharge | Very light smoke (detectable odor no visibility reduction) |  | Confined to object of origin (component) do not result in flames or heat output external to the comp | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal
2111 | 51377 | 12/12/2013 | Potentially Challenging | Electrical failure resulting in overheating materials | In-Situ | Other electrical or electronic equipment |  | Flaming combustion – internal to component | Light smoke coming from ignition source - minor or no visibility reduction in vicinity of fire |  | Confined to the object of origin (broad/extensive damage) | No there was no collateral damage | No | 0 | 0 | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal | 0 ft Vertical, 0 ft Horizontal