## Sheet1
| FireID | Event Date_FTS | Disposition_FTS | Ignition | Discovery | Duration Certainty | Duration | Suppression Time | Detection Method | Detection Performance | Suppression Method | Suppression Agent | Unnamed: 12 | Unnamed: 13 | Estimated Duration | Suppression Agent Portable | Suppression Agent Other | Unnamed: 14
0 | 1 | 12/12/2006 | Undetermined | 13:22:00 | 13:22:00 | Known | 34 | 34 | Failed Equipment Alarm | Unknow | Unknow | Portable
1 | 2 | 1/5/1999 | Not Challenging | 13:11:00 | 13:11:00 | Known | 14 | 14 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknow | Hose stream or hose reel | Portable
2 | 3 | 1/14/1999 | Challenging | 12:56:00 | 12:56:00 | Known | 409 | 409 | Other plant personnel (in vicinity or passerby） | Plant area did not have installed detection capability | Hose stream or hose reel | Portable
3 | 5 | 5/18/1999 | Not Evaluated | 18:32:00 | 18:32:00 | Known | 173 | 173 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
4 | 6 | 7/13/1999 | Potentially Challenging | 13:00:00 |  | Known | 40 | 40 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water
5 | 7 | 10/9/1999 | Undetermined (NC‐PC) | 23:25:00 | 23:25:00 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
6 | 8 | 5/7/2000 | Potentially Challenging | 07:50:00 | 07:57:00 | Known | 37 | 37 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknow | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
7 | 9 | 1/3/1990 | Undetermined (PC‐CH) | 07:45:00 |  | Known | 13 | 13 | Unknown | Unknown | Unknown | Portable
8 | 11 | 3/15/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
9 | 12 | 3/30/1990 | Not Challenging | 03:41:00 | 03:41:00 | Known | 3 | 3 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher Other (specify in comments) | Portable: CO2
10 | 13 | 4/10/1990 | Potentially Challenging | 05:41:00 |  | Known | 9 | 9 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2
11 | 14 | 5/24/1990 | Potentially Challenging | 03:15:00 | 03:23:00 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable
12 | 15 | 5/27/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Single Portable fire extinguisher | Portable: CO2
13 | 16 | 6/10/1990 | Not Challenging | 13:31:00 |  | Known | 8624 | 8624 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Other (specify in comments) | Portable
14 | 17 | 6/28/1990 | Potentially Challenging | 03:01:00 | 03:01:00 | Known | 29 | 29 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
15 | 18 | 7/13/1990 | Potentially Challenging | 13:10:00 | 13:25:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Unknown | Portable
16 | 19 | 8/4/1990 | Challenging | 17:09:00 | 17:09:00 | Known | 19 | 19 | Unknown | Unknown | Fixed suppression system ‐ deluge (automatic) | Portable
17 | 20 | 8/25/1990 | Challenging | 18:02:00 |  | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
18 | 21 | 9/22/1990 | Challenging | 21:51:00 |  | Known | 29 | 29 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Portable,Other: Water
19 | 22 | 12/3/1990 | Challenging | 04:29:00 |  | Known | 76 | 76 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel Multiple portable fire extinguishers | Portable: Dry Chemical,Other: Water
20 | 23 | 12/19/1990 | Undetermined (PC‐CH) | 12:20:00 |  | Known | 40 | 40 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means–no indication of system failure | Single Portable fire extinguisher Other (specify in comments) | Portable: Dry Chemical
21 | 24 | 12/22/1990 | Undetermined (PC‐CH) | 07:45:00 |  | Known | 120 | 120 | Dedicated Fire Watch | Unknown | Unknown | Portable
22 | 25 | 1/11/1991 | Undetermined (PC‐CH) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
23 | 26 | 2/14/1991 | Challenging | 21:45:00 | 21:45:00 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Single Portable fire extinguisher | Portable: Halon，Other: Water
24 | 27 | 1/16/1991 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
25 | 28 | 1/23/1991 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable
26 | 29 | 2/23/1991 | Potentially Challenging | 00:50:00 | 00:52:00 | Known | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
27 | 30 | 4/29/1991 | Challenging | 18:42:00 |  | Known | 200 | 200 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression ‐ manually actuated,Fixed suppression system ‐ deluge (automatic),Fuel supply removed,Supervised burn out | Other: Water
28 | 31 | 6/15/1991 | Undetermined (NC‐PC) | 23:50:00 |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
29 | 32 | 6/27/1991 | Potentially Challenging | 21:15:00 | 21:15:00 | Known | 28 | 28 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable
30 | 33 | 8/1/1991 | Potentially Challenging | 19:31:00 | 19:31:00 | Known | 183 | 183 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
31 | 34 | 8/11/1991 | Potentially Challenging | 08:55:00 | 08:55:00 | Known | 11 | 11 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel Multiple portable fire extinguishers | Portable: CO2,Other: Water
32 | 35 | 11/2/1991 | Not Challenging |  | 21:39:00 | Estimated | 46 | 46 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Portable
33 | 36 | 11/9/1991 | Not Challenging | 11:22:00 | 11:22:00 | Known | 15 | 15 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated, Hose stream or hose reel, Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water
34 | 37 | 11/15/1991 | Not Challenging | 09:28:00 |  | Known | 34 | 34 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
35 | 38 | 3/21/1992 | Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
36 | 39 | 5/3/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
37 | 40 | 5/22/1992 | Not Challenging |  |  | Estimated | 85 | 85 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Other (specify in comments) | Portable
38 | 41 | 6/17/1992 | Potentially Challenging | 15:26:00 | 15:26:00 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
39 | 42 | 7/3/1992 | Potentially Challenging | 10:29:00 |  | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable
40 | 43 | 7/4/1992 | Challenging |  | 01:50:00 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
41 | 44 | 7/13/1992 | Challenging | 19:10:00 | 19:10:00 | Estimated | 13 | 13 | Unknown | Unknown | Hose stream or hose reel, Multiple portable fire extinguishers,Other (specify in comments) | Portable: CO2,Other: Water
42 | 45 | 7/29/1992 | Potentially Challenging | 04:15:00 |  | Known | 16 | 16 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: CO2
43 | 46 | 8/4/1992 | Potentially Challenging | 05:52:00 | 05:52:00 | Known | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable
44 | 47 | 8/10/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable
45 | 48 | 9/4/1992 | Challenging | 02:14:00 | 02:14:00 | Known | 27 | 27 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers,Power Supply Removed | Portable: Dry Chemical,Other: Water
46 | 49 | 9/15/1992 | Challenging | 02:43:00 | 02:43:00 | Known | 77 | 77 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel, Single portable fire extinguishers | Portable: CO2,Other: AFFF foam
47 | 50 | 11/24/1992 | Potentially Challenging | 02:18:00 | 02:18:00 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
48 | 51 | 2/5/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed | Portable
49 | 52 | 6/19/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown | Portable
50 | 53 | 7/27/1993 | Not Challenging |  |  | Known | 0 | 0 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Other (specify in comments) | Portable
51 | 54 | 8/16/1993 | Not Challenging | 15:09:00 | 15:09:00 | Known | 1 | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
52 | 55 | 10/13/1993 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemica
53 | 56 | 10/21/1993 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable
54 | 57 | 11/2/1993 | Not Challenging | 13:00:00 | 13:00:00 | Known | 14 | 14 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
55 | 58 | 12/25/1993 | Challenging | 13:52:00 | 13:52:00 | Known | 210 | 210 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified, Multiple portable fire extinguishers | Portable: CO2,Other: Water
56 | 59 | 1/29/1994 | Challenging | 06:54:00 |  | Known | 20 | 20 | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
57 | 60 | 2/3/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention) | Portable
58 | 61 | 4/3/1994 | Challenging | 06:18:00 | 06:18:00 | Known | 167 | 167 | ailed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression ‐ manually actuated, Hose stream or hose reel | Other: Water
59 | 62 | 6/6/1994 | Not Challenging | 11:41:00 | 11:41:00 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention | Portable
60 | 63 | 6/15/1994 | Potentially Challenging |  | 01:40:00 | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
61 | 64 | 6/1/1994 | Challenging | 14:55:00 |  | Known | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
62 | 65 | 7/2/1994 | Challenging | 11:44:00 | 11:44:00 | Known | 31 | 31 | Fire Watch | Unknown | Hose stream or hose reel,Portable manual system (e.g. CO2 cart),Multiple portable fire extinguishers | Portable: Dry Chemical,Other: CO2
63 | 66 | 7/11/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
64 | 67 | 7/29/1994 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
65 | 68 | 8/10/1994 | Undetermined (PC‐CH) | 13:30:00 |  | Known | 30 | 30 | Fire Watch | Unknown | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water
66 | 69 | 8/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable
67 | 70 | 10/26/1994 | Not Challenging | 14:26:00 |  | Known | 569 | 569 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out | Portable
68 | 71 | 3/1/1995 | Undetermined (PC‐CH) |  | 03:35:00 | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable
69 | 72 | 4/14/1995 | Challenging | 05:10:00 | 05:10:00 | Known | 19 | 19 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: CO2,Other: Water
70 | 73 | 6/1/1995 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable
71 | 74 | 6/10/1995 | Challenging | 08:57:00 | 08:57:00 | Known | 136 | 136 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify],Other: Water
72 | 75 | 8/22/1995 | Potentially Challenging | 11:25:00 |  | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable
73 | 76 | 10/21/1995 | Challenging | 09:38:00 |  | Known | 30 | 30 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other:AFFF foam
74 | 77 | 12/10/1995 | Not Challenging |  |  | Estimated | 13 | 13 | Unknown | Unknown | Unknown | Portable:
75 | 78 | 1/24/1996 | Challenging | 06:15:00 |  | Known | 13 | 13 | Fire Watch | Plant area had installed detection which actuated | Hose stream or hose reel | Portable: Water
76 | 79 | 2/5/1996 | Challenging | 15:45:00 |  | Known | 37 | 37 | Unknown | Unknown | Unknown | Portable:
77 | 80 | 2/29/1996 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
78 | 81 | 3/25/1996 | Undetermined (NC‐PC) |  | 20:10:00 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
79 | 82 | 3/27/1996 | Potentially Challenging |  | 20:00:00 | Known | 14 | 14 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off) | Portable:
80 | 83 | 4/4/1996 | Potentially Challenging | 17:00:00 | 17:00:00 | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable:
81 | 84 | 4/19/1996 | Potentially Challenging | 10:19:00 |  | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
82 | 85 | 5/13/1996 | Not Challenging | 18:48:00 | 18:48:00 | Known | 13 | 13 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
83 | 86 | 6/23/1996 | Challenging | 17:14:00 |  | Known | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
84 | 87 | 8/19/1996 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
85 | 88 | 10/5/1996 | Challenging | 13:13:00 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
86 | 89 | 10/15/1996 | Potentially Challenging | 13:15:00 |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g.open circuit breaker) | Portable:
87 | 90 | 10/17/1996 | Challenging | 16:07:00 |  | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: CO2，Other: Water
88 | 91 | 11/19/1996 | Undetermined (NC‐PC) | 14:59:00 |  | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
89 | 92 | 11/22/1996 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable:
90 | 93 | 3/4/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
91 | 94 | 8/1/1997 | Potentially Challenging |  | 00:02:00 | Estimated | 18 | 18 | Fire Watch | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: CO2
92 | 95 | 10/9/1997 | Potentially Challenging | 23:02:00 |  | Known | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher，Other (specify in comments | Portable: CO2
93 | 96 | 10/28/1997 | Not Challenging | 08:45:00 | 08:45:00 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)，Fuel supply removed (simple manual action e.g. valve turn off) | Portable:
94 | 97 | 6/10/1998 | Potentially Challenging | 02:00:00 | 02:10:00 | Known | 39 | 39 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
95 | 98 | 10/8/1998 | Potentially Challenging |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed | Portable:
96 | 99 | 10/10/1998 | Not Challenging | 13:12:00 | 13:12:00 | Known | 18 | 18 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable:
97 | 100 | 5/15/2000 | Challenging | 00:25:00 | 00:25:00 | Known | 78 | 78 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2，Other: CO2
98 | 101 | 9/3/2000 | Undetermined (PC‐CH) | 14:40:00 | 14:40:00 | Known | 29 | 29 | Dedicated Fire Watch | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water
99 | 102 | 9/4/2000 | Challenging | 11:32:00 |  | Known | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
100 | 103 | 9/22/2000 | Challenging | 03:46:00 |  | Known | 16 | 16 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
101 | 104 | 10/14/2000 | Potentially Challenging |  | 18:15:00 | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
102 | 105 | 11/10/2000 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
103 | 106 | 2/3/2001 | Challenging | 15:14:00 |  | Known | 156 | 156 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
104 | 107 | 3/21/2001 | Potentially Challenging | 22:11:00 |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
105 | 108 | 4/6/2001 | Not Challenging | 00:00:00 | 00:00:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Portable:
106 | 109 | 4/24/2001 | Undetermined (PC‐CH) | 01:48:00 | 01:48:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection，capability | Hose stream or hose reel | Other: Water
107 | 110 | 6/25/2001 | Potentially Challenging | 04:33:00 |  | Known | 16 | 16 | Unknown | Unknown | Unknown | Portable:
108 | 111 | 8/2/2001 | Challenging | 08:23:00 |  | Known | 22 | 22 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
109 | 112 | 8/3/2001 | Undetermined (PC‐CH) | 08:40:00 | 08:40:00 | Known | 90 | 90 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown | Portable:
110 | 113 | 6/12/2002 | Challenging | 13:45:00 | 13:45:00 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown | Portable:
111 | 114 | 8/21/2002 | Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
112 | 115 | 8/22/2002 | Challenging | 16:32:00 | 16:32:00 | Known | 18 | 18 | Ultraviolet flame detector | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified，Multiple portable fire extinguishers，Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water，Other: Water
113 | 116 | 3/18/2003 | Not Challenging | 20:37:00 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
114 | 117 | 10/9/2002 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Unknown | Unknown | Unknown | Portable:
115 | 118 | 1/15/2003 | Challenging | 20:10:00 | 20:10:00 | Known | 35 | 35 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
116 | 119 | 3/18/2003 | Not Challenging | 20:37:00 |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
117 | 120 | 4/7/2003 | Potentially Challenging | 22:01:00 |  | Known | 33 | 33 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other (specify in comments) | Portable:
118 | 121 | 4/26/2003 | Undetermined (NC‐PC) | 17:46:00 | 17:46:00 | Known | 37 | 37 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart)，Single Portable fire extinguisher | Portable:
119 | 122 | 4/29/2003 | Challenging | 02:58:00 |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression ‐ manually actuated，Hose stream or hose reel | Portable: Other [specify]，Other: CO2
120 | 123 | 10/16/2003 | Challenging |  |  | Estimated | 23 | 23 | Unknown | Unknown | Hose stream or hose reel，Single Portable fire extinguisher | Portable: Dry Chemical，Other: AFFF foam
121 | 124 | 10/28/2003 | Potentially Challenging | 01:30:00 | 01:30:00 | Known | 317 | 317 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
122 | 125 | 1/6/2004 | Challenging | 12:40:00 | 12:40:00 | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
123 | 126 | 5/21/2004 | Undetermined (PC‐CH) | 21:09:00 | 21:09:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown | Portable:
124 | 127 | 6/18/2004 | Challenging | 06:40:00 | 06:40:00 | Known | 71 | 71 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
125 | 128 | 8/31/2004 | Potentially Challenging | 07:15:00 | 07:15:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
126 | 129 | 11/6/2004 | Potentially Challenging | 02:52:00 |  | Known | 18 | 18 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable:
127 | 130 | 12/14/2004 | Potentially Challenging | 11:40:00 |  | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable:
128 | 131 | 1/14/2005 | Undetermined (PC‐CH) | 09:53:00 | 09:53:00 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not，actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Water
129 | 132 | 3/4/2005 | Undetermined (NC‐PC) | 14:47:00 | 14:47:00 | Estimated | 64 | 64 | Other plant personnel (in vicinity or passerby) |  | Unknown | Portable:
130 | 133 | 5/4/2005 | Potentially Challenging | 14:10:00 | 14:10:00 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable:
131 | 134 | 6/27/2005 | Challenging | 03:16:00 |  | Known | 27 | 27 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: Water
132 | 135 | 8/25/2005 | Potentially Challenging | 11:25:00 | 11:25:00 | Known | 112 | 112 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel，Multiple portable fire extinguishers
133 | 136 | 10/25/2005 | Potentially Challenging | 21:40:00 | 21:40:00 | Known | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Portable:
134 | 137 | 10/29/2005 | Challenging | 13:30:00 | 13:30:00 | Known | 28 | 28 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
135 | 138 | 2/11/2006 | Potentially Challenging | 15:06:00 |  | Known | 154 | 154 | Other plant personnel (in vicinity or passerby | Unknown | Unknown | Portable:
136 | 139 | 2/24/2006 | Potentially Challenging | 08:36:00 | 08:36:00 | Known | 153 | 153 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable:
137 | 140 | 3/20/2006 | Undetermined (NC‐PC) |  | 07:56:00 | Known | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
138 | 141 | 5/1/2006 | Undetermined (PC‐CH) | 04:39:00 | 04:39:00 | Estimated | 11 | 11 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: Dry Chemical
139 | 142 | 5/24/2006 | Challenging |  |  | Estimated | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: CO2
140 | 143 | 8/15/2006 | Potentially Challenging | 17:59:00 | 17:59:00 | Known | 36 | 36 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Hose stream or hose reel
141 | 144 | 10/30/2006 | Potentially Challenging | 12:38:00 | 12:44:00 | Known | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
142 | 145 | 11/11/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
143 | 146 | 2/27/2007 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
144 | 147 | 4/5/2007 | Not Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention) | Portable: None
145 | 148 | 4/6/2007 | Challenging | 11:09:00 | 11:09:00 | Known | 12 | 12 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water
146 | 149 | 4/8/2007 | Potentially Challenging | 13:30:00 | 13:30:00 | Known | 9 | 9 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher | Portable: CO2
147 | 150 | 4/25/2007 | Challenging | 16:33:00 |  | Known | 28 | 28 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Unknown
148 | 151 | 8/1/2007 | Not Challenging | 01:52:00 | 01:52:00 | Known | 21 | 21 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Dry Chemical
149 | 152 | 10/23/2007 | Potentially Challenging | 22:58:00 | 22:58:00 | Known | 6 | 6 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
150 | 153 | 8/16/2008 | Challenging | 23:57:00 |  | Known | 125 | 125 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
151 | 154 | 9/20/2008 | Challenging | 20:05:00 | 20:05:00 | Known | 23 | 23 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Fixed suppression ‐ manually actuated | Other: Water
152 | 155 | 11/17/2008 | Undetermined (NC‐PC) | 09:11:00 | 09:11:00 | Known | 24 | 24 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
153 | 156
154 | 157 | 2/1/2009 | Challenging | 21:56:00 | 21:56:00 | Known | 31 | 31 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel | Other: Water
155 | 158 | 6/26/2009 | Potentially Challenging | 19:49:00 | 19:49:00 | Known | 17 | 17 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
156 | 159 | 1/16/1990 | Potentially Challenging | 17:24:00 | 17:30:00 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Unknown
157 | 160 | 2/7/2009 | Challenging | 10:46:00 | 10:46:00 | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Hose stream or hose reel | Other: Water
158 | 161 | 4/22/2009 | Potentially Challenging | 04:30:00 | 05:00:00 | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
159 | 162 | 8/5/2009 | Challenging | 07:50:00 | 07:50:00 | Estimated | 46 | 46 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
160 | 163 | 10/12/2009 | Potentially Challenging | 15:51:00 | 15:51:00 | Known | 22 | 22 | Fire Watch | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Unknown
161 | 164 | 3/28/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Water
162 | 165
163 | 166
164 | 167
165 | 168 | 11/13/2003 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
166 | 169 | 11/13/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
167 | 170 | 11/21/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
168 | 171
169 | 172 | 12/7/2003 | Not Challenging |  | 01:50:00 | Known | 130 | 130 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Multiple portable fire extinguishers
170 | 173 | 12/13/2003 | Not Challenging | 23:16:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed
171 | 174 | 12/30/2003 | Not Challenging | 18:00:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
172 | 175 | 11/22/2009 | Challenging | 15:41:00 | 15:41:00 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers
173 | 176 | 12/12/2009 | Potentially Challenging |  |  | Estimated | 23 | 23 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown | Other: Water
174 | 177
175 | 178
176 | 179
177 | 180
178 | 181 | 2/13/1997 | Potentially Challenging |  |  | Estimated | 10 | 10 | Gas Ionization | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
179 | 182
180 | 183
181 | 184 | 6/27/1997 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify]
182 | 185 | 3/23/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
183 | 186 | 5/14/1998 | Not Challenging | 14:40:00 |  | Known | 14 | 14 | Roving Firewatch | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
184 | 187 | 8/16/1999 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
185 | 188 | 8/24/1999 | Potentially Challenging |  |  | Estimated | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Unknown,Power supply removed (simple manual action e.g. open circuit,breaker)
186 | 189 | 10/14/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
187 | 190 | 3/18/1998 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
188 | 191 | 11/11/1998 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
189 | 192 | 5/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
190 | 193 | 7/31/1991 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
191 | 194 | 5/22/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
192 | 195 | 3/21/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not,actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
193 | 196
194 | 197
195 | 198
196 | 199 | 1/22/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
197 | 200 | 2/6/1990 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
198 | 201 | 3/8/1990 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
199 | 202 | 3/23/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
200 | 203 | 4/6/1990 | Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
201 | 204 | 4/9/1990 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
202 | 205
203 | 206 | 6/11/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
204 | 207 | 7/15/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
205 | 208 | 8/8/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
206 | 209 | 8/22/1990 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
207 | 210 | 10/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 85 | 85 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Dry Chemical
208 | 211 | 11/2/1990 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
209 | 212 | 12/5/1990 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
210 | 213
211 | 214 | 3/8/1991 | Potentially Challenging |  |  | Estimated | 8 | 8 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Multiple portable fire extinguishers
212 | 215 | 3/11/1991 | Not Challenging |  |  | Unknown | 0 | 0 |  |  | Unknown
213 | 216 | 7/12/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
214 | 217 | 7/19/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
215 | 218 | 9/12/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
216 | 219 | 9/27/1991 | Undetermined (PC‐CH) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
217 | 220 | 10/20/1991 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
218 | 221 | 10/23/1991 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
219 | 222 | 2/1/1992 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
220 | 223 | 3/3/1992 | Not Challenging |  |  | Estimated | 10 | 10 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
221 | 224 | 3/8/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
222 | 225 | 3/23/1992 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
223 | 226 | 4/17/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
224 | 227 | 6/9/1992 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed
225 | 228 | 8/14/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Automatic fixed ‐ actuation not specified | Other: Water
226 | 229 | 8/21/1992 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby)
227 | 230 | 8/31/1992 | Potentially Challenging |  |  | Estimated | 85 | 85 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Supervised burn out,Fuel supply removed (simple manual action e.g. valve turn off)
228 | 231 | 10/22/1992 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
229 | 232 | 10/27/1992 | Not Challenging |  |  | Estimated | 46 | 46 | Unknown | Unknown | Unknown
230 | 233 | 11/29/1992 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
231 | 234 | 12/16/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
232 | 235 | 12/30/1992 | Potentially Challenging |  |  | Estimated | 25 | 25 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
233 | 236 | 1/6/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
234 | 237 | 3/19/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Other: Water
235 | 238 | 4/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
236 | 239 | 7/14/1993 | Potentially Challenging |  |  | Estimated | 25 | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
237 | 240 | 7/19/1993 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Hose stream or hose reel | Other: Water
238 | 241 | 11/3/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
239 | 242 | 11/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
240 | 243 | 12/1/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
241 | 244 | 12/7/1993 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart)
242 | 245 | 12/16/1993 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
243 | 246 | 1/12/1994 | Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Hose stream or hose reel | Other: Water
244 | 247 | 1/12/1994 | Undetermined (PC‐CH) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Portable: Other [specify]
245 | 248 | 3/5/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
246 | 249 | 3/7/1994 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed
247 | 250 | 7/19/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed ‐ thermally actuated | Other: Water
248 | 251 | 10/11/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
249 | 252 | 3/18/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Automatic fixed ‐ thermally actuated
250 | 253 | 7/6/1995 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
251 | 254 | 9/25/1995 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
252 | 255 | 11/19/1995 | Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
253 | 256 | 7/22/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
254 | 257 | 10/22/1997 | Not Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
255 | 258 | 11/3/1997 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
256 | 259 | 12/26/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Other [specify]
257 | 260 | 2/3/1998 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
258 | 261 | 5/11/1998 | Not Challenging | 19:50:00 | 19:50:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
259 | 262 | 2/19/1999 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
260 | 263 | 4/25/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
261 | 264 | 10/20/2001 | Not Challenging | 11:01:00 | 11:01:00 | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
262 | 265 | 9/23/2006 | Not Challenging | 09:40:00 | 09:40:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
263 | 266 | 11/9/2006 | Potentially Challenging |  | 11:30:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
264 | 267 | 6/1/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
265 | 268 | 4/7/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Single Portable fire extinguisher
266 | 269 | 12/12/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
267 | 270 | 11/18/2005 | Potentially Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
268 | 271 | 10/5/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
269 | 272 | 4/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
270 | 273 | 5/10/2002 | Not Challenging |  |  | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
271 | 274 | 5/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Water,Other: Water
272 | 275 | 10/14/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Unknown | Portable: Water
273 | 276 | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify]
274 | 277 | 11/2/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Other [specify]
275 | 278 | 1/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
276 | 279
277 | 280 | 11/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
278 | 281
279 | 282 | 4/23/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown | Other: Water
280 | 283 | 11/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
281 | 284 | 11/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown | Portable: Water
282 | 285 | 12/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
283 | 286 | 4/20/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
284 | 287 | 8/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
285 | 288 | 10/10/2006 | Potentially Challenging |  |  | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
286 | 289 | 5/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
287 | 290 | 8/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) | Portable: Water
288 | 291
289 | 292 | 10/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments)
290 | 293 | 10/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
291 | 294 | 10/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Fuel supply removed (simple manual action e.g. valve turn off) | Portable: Water
292 | 295 | 10/22/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
293 | 296 | 10/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
294 | 297 | 11/30/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
295 | 298 | 12/16/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
296 | 299 | 3/4/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments) | Portable: Water
297 | 300 | 3/16/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
298 | 301
299 | 302 | 12/21/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
300 | 303 | 3/1/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
301 | 304
302 | 305 | 6/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments)
303 | 306 | 1/24/2002 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
304 | 307 | 10/17/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2
305 | 308 | 10/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
306 | 309 | 10/23/2005 | Not Challenging | 07:30:00 | 07:30:00 | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
307 | 310 | 11/18/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
308 | 311 | 12/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
309 | 312 | 10/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
310 | 313 | 11/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
311 | 314 | 2/10/2000 | Not Challenging |  | 07:58:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
312 | 315
313 | 316 | 8/17/2000 | Not Challenging | 16:47:00 | 16:47:00 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
314 | 317 | 9/27/2003 | Not Challenging | 14:18:00 | 14:18:00 | Known | 3 | 3 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: None
315 | 318 | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Unknown
316 | 319 | 10/5/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
317 | 320 | 10/24/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: CO2
318 | 321 | 10/31/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
319 | 322 | 3/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
320 | 323
321 | 324 | 1/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
322 | 325 | 3/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
323 | 326 | 3/25/2005 | Not Challenging | 03:55:00 | 03:55:00 | Known | 16 | 16 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
324 | 327 | 1/1/2006 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
325 | 328 | 9/24/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
326 | 329 | 9/25/2006 | Not Challenging |  | 16:29:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Air supply cut off (smothered, covered)
327 | 330 | 9/27/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
328 | 331
329 | 332 | 4/15/2007 |  |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
330 | 333 | 5/11/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
331 | 334
332 | 335 | 8/3/2007 | Potentially Challenging | 11:04:00 |  | Known | 6 | 6 | Ultraviolet flame detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
333 | 336
334 | 337 | 8/18/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
335 | 338 | 7/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments)
336 | 339
337 | 340 | 8/7/2009 | Not Challenging |  | 22:40:00 | Known | 22 | 22 | Installed Fire detector ‐ Type not specified | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
338 | 341 | 2/18/2008 | Not Challenging | 21:24:00 | 21:25:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
339 | 342 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
340 | 343 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
341 | 344 | 10/26/2006 | Not Challenging | 13:27:00 | 13:27:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
342 | 345 | 4/25/2005 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical
343 | 346 | 3/1/2002 | Potentially Challenging |  | 20:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguishe
344 | 347
345 | 348
346 | 349 | 4/5/2007 | Not Challenging |  | 05:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
347 | 350 | 7/11/2002 | Potentially Challenging |  | 08:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
348 | 351 | 9/26/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
349 | 352 | 2/28/2003 | Not Challenging |  | 09:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
350 | 353 | 1/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
351 | 354 | 10/1/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
352 | 355 | 3/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
353 | 356 | 4/19/2006 | Potentially Challenging |  | 19:15:00 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker)
354 | 357 | 1/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
355 | 358 | 5/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
356 | 359 | 3/6/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
357 | 360 | 7/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
358 | 361 | 2/4/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
359 | 362 | 4/16/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown
360 | 363 | 5/27/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
361 | 364 | 10/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
362 | 365 | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
363 | 366 | 1/25/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
364 | 367 | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
365 | 368 | 10/24/2006 | Not Challenging | 05:19:00 | 05:19:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
366 | 369
367 | 370
368 | 371
369 | 372 | 9/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Unknown | Power Supply Removed
370 | 373 | 10/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
371 | 374 | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
372 | 375 | 10/16/2009 | Potentially Challenging | 20:52:00 | 20:52:00 | Known | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
373 | 376 | 6/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
374 | 377 | 8/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
375 | 378 | 6/24/2002 | Not Challenging |  | 12:00:00 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
376 | 379 | 10/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
377 | 380 | 10/29/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
378 | 381 | 3/6/2005 | Potentially Challenging |  |  | Estimated | 13 | 13 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
379 | 382
380 | 383
381 | 384 | 3/23/2007 | Not Challenging | 00:20:00 | 00:20:00 | Known | 3 | 3 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
382 | 385 | 4/14/2006 | Not Challenging |  | 02:00:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
383 | 386 | 6/3/2008 | Not Challenging |  | 11:01:00 | Known | 685 | 685 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon
384 | 387 | 7/24/2008 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)Fuel supply removed (simple manual action e.g. valve turn off)
385 | 388 | 7/25/2005 | Not Challenging |  | 14:22:00 | Known | 1025 | 1025 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Portable manual system (e.g. CO2 cart) | Other: AFFF foam
386 | 389 | 10/17/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: CO2
387 | 390 | 10/29/2007 | Not Challenging |  | 07:40:00 | Known | 462 | 462 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed by maintenance staff (craft activity required) | Portable: CO2
388 | 391
389 | 392 | 10/30/2002 | Not Challenging | 14:45:00 | 14:53:00 | Known | 11 | 11 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel,Single Portable fire extinguisher | Portable: CO2
390 | 393 | 10/30/2004 | Not Challenging |  | 05:00:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circui tbreaker) | Portable: Dry Chemical
391 | 394 | 2/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
392 | 395
393 | 396
394 | 397 | 5/2/2000 | Not Challenging |  | 07:30:00 | Estimated | 13 | 13 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
395 | 398 | 7/7/2000 | Not Challenging |  |  | Known | 0 | 0 | Sprinkler or fire‐water system flow alarm | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Automatic fixed ‐ actuation not specified | Other: Water
396 | 399 | 12/24/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
397 | 400 | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
398 | 401 | 6/13/2001 | Not Challenging |  | 12:32:00 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
399 | 402
400 | 403
401 | 404 | 6/12/2001 | Not Challenging |  | 05:45:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
402 | 405 | 8/13/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
403 | 406 | 6/12/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
404 | 407 | 12/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
405 | 408 | 6/1/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
406 | 409 | 9/21/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
407 | 410 | 7/25/2005 | Not Challenging |  |  | Known | 533 | 533 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
408 | 411 | 3/8/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
409 | 412 | 7/15/2009 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
410 | 413
411 | 414
412 | 415
413 | 416 | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
414 | 417
415 | 418 | 10/8/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
416 | 419 | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
417 | 420 | 6/24/2001 | Undetermined (NC‐PC) |  | 08:05:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed,Unknown | Portable: Water
418 | 421 | 7/1/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
419 | 422 | 3/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
420 | 423 | 6/23/2003 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
421 | 424 | 3/10/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Hose stream or hose reel
422 | 425
423 | 426 | 9/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
424 | 427 | 2/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
425 | 428 | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
426 | 429 | 3/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
427 | 430 | 10/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
428 | 431 | 4/3/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
429 | 432
430 | 433
431 | 434
432 | 435
433 | 436 | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers
434 | 437 | 2/3/2001 | Challenging | 15:14:00 | 15:14:00 | Known | 177 | 177 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel,Multiple portable fire extinguishers | Portable: Other [specify]
435 | 438 | 6/24/2001 | Challenging |  | 11:02:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
436 | 439 | 10/2/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
437 | 440 | 1/2/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
438 | 441 | 11/23/2003 | Not Challenging |  | 15:16:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
439 | 442 | 2/4/2004 | Potentially Challenging |  | 07:35:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
440 | 443 | 3/3/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
441 | 444 | 6/28/2004 | Challenging |  |  | Unknown |  |  |  | Unknown | Multiple portable fire extinguishers | Portable: Halon
442 | 445 | 8/30/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
443 | 446 | 10/5/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
444 | 447 | 10/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
445 | 448 | 11/17/2004 | Not Challenging |  | 11:58:00 | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments)
446 | 449 | 12/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
447 | 450 | 12/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
448 | 451 | 12/13/2004 | Not Challenging |  | 19:45:00 | Unknown | 0 | 0 | Fire Watch | Unknown | Unknown
449 | 452 | 12/18/2004 | Not Challenging |  | 11:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
450 | 453 | 6/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention),Unknown
451 | 454 | 6/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
452 | 455 | 6/6/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
453 | 456 | 7/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
454 | 457 | 2/17/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
455 | 458 | 5/4/2006 | Not Challenging | 16:00:00 | 16:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water
456 | 459 | 5/10/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
457 | 460 | 9/7/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
458 | 461 | 10/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
459 | 462 | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Other (specify in comments)
460 | 463 | 11/1/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
461 | 464 | 12/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
462 | 465 | 1/31/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments)
463 | 466 | 2/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Hose stream or hose reel | Other: Water
464 | 467 | 2/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
465 | 468 | 2/20/2007 | Undetermined (NC‐PC) |  | 15:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
466 | 469 | 3/19/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
467 | 470 | 6/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
468 | 471 | 7/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
469 | 472 | 7/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
470 | 473 | 8/4/2007 | Potentially Challenging | 10:03:00 | 10:04:00 | Known | 147 | 147 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
471 | 474 | 8/21/2007 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
472 | 475 | 9/27/2007 | Potentially Challenging |  |  | Estimated | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Other (specify in comments)
473 | 476 | 12/6/2007 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments)
474 | 477 | 2/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
475 | 478 | 3/30/2008 | Not Challenging |  | 18:31:00 | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
476 | 479 | 3/17/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
477 | 480 | 4/7/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
478 | 481 | 6/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
479 | 482 | 2/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
480 | 483 | 11/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
481 | 484 | 11/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
482 | 485 | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed
483 | 486 | 8/27/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
484 | 487 | 1/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
485 | 488 | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
486 | 489
487 | 490
488 | 491 | 4/12/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
489 | 492 | 10/19/2000 | Undetermined (NC‐PC)
490 | 493
491 | 494 | 3/8/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
492 | 495 | 3/20/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
493 | 496 | 5/19/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Unknown
494 | 497 | 8/14/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
495 | 498 | 12/19/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
496 | 499 | 12/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
497 | 500 | 3/12/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  |  |  | Unknown
498 | 501 | 1/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
499 | 502 | 11/18/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
500 | 503 | 5/14/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
501 | 504 | 10/9/2002 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
502 | 505 | 9/13/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
503 | 506 | 9/12/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
504 | 507
505 | 508 | 3/14/2005 | Not Challenging | 19:17:00 | 19:17:00 | Known | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
506 | 509 | 1/19/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
507 | 510
508 | 511 | 7/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed
509 | 512 | 7/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Power Supply Removed
510 | 513 | 11/18/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
511 | 514 | 4/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
512 | 515 | 10/5/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
513 | 516 | 10/25/2005 | Potentially Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
514 | 517 | 3/23/2006 | Undetermined (PC‐CH) | 00:34:00 | 00:39:00 | Known | 20 | 20 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers,Power Supply Removed,Other (specify in comments)
515 | 518 | 3/30/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
516 | 519 | 5/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
517 | 520 | 6/6/2006 | Potentially Challenging | 01:16:00 | 01:19:00 | Known | 11 | 11 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
518 | 521 | 12/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
519 | 522 | 9/19/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
520 | 523 | 9/27/2006 | Not Challenging |  |  | Known | 52 | 52 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
521 | 524 | 10/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
522 | 525
523 | 526 | 1/30/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
524 | 527 | 11/10/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
525 | 528
526 | 529 | 11/28/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
527 | 530 | 3/5/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
528 | 531 | 8/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
529 | 532
530 | 533 | 1/27/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
531 | 534 | 4/10/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
532 | 535 | 6/16/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
533 | 536 | 8/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
534 | 537 | 10/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
535 | 538 | 10/20/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
536 | 539 | 10/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
537 | 540 | 10/23/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Other (specify in comments)
538 | 541 | 10/24/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
539 | 542 | 3/4/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None,Other: None
540 | 543 | 8/27/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
541 | 544 | 12/13/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
542 | 545 | 6/5/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
543 | 546 | 10/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
544 | 547 | 11/5/2002 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
545 | 548 | 11/13/2002 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Self‐extinguished (no plant staff intervention)
546 | 549 | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
547 | 550 | 2/2/2005 | Undetermined (NC‐PC) | 05:58:00 | 05:58:00 | Known | 9 | 9 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
548 | 551 | 2/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
549 | 552 | 7/31/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
550 | 553 | 6/24/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
551 | 554 | 6/2/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
552 | 555 | 7/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
553 | 556 | 10/14/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
554 | 557 | 11/2/2005 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
555 | 558 | 12/13/2005 | Potentially Challenging |  |  | Estimated | 10 | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher
556 | 559 | 9/12/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
557 | 560 | 5/20/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
558 | 561 | 1/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown
559 | 562 | 10/9/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
560 | 563 | 10/18/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
561 | 564 | 3/13/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
562 | 565 | 4/25/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
563 | 566 | 7/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
564 | 567 | 7/31/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
565 | 568 | 1/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
566 | 569 | 5/15/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
567 | 570 | 6/3/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed
568 | 571 | 9/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
569 | 572 | 12/23/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
570 | 573 | 1/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
571 | 574
572 | 575 | 5/18/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
573 | 576 | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
574 | 577 | 9/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
575 | 578 | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
576 | 579 | 3/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
577 | 580 | 1/6/2003 | Not Challenging | 06:30:00 | 06:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
578 | 581 | 4/17/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
579 | 582 | 9/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
580 | 583
581 | 584 | 10/8/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
582 | 585 | 12/10/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
583 | 586 | 5/5/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
584 | 587 | 5/13/2003 | Not Challenging | 00:00:00 |  | Known | 30 | 30 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
585 | 588 | 11/30/2006 | Challenging |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Water
586 | 589
587 | 590 | 2/20/2005 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
588 | 591 | 7/19/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) |  | Single Portable fire extinguisher,Power Supply Removed
589 | 592 | 6/11/2009 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Fuel supply removed
590 | 593 | 10/16/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
591 | 594 | 1/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
592 | 595 | 2/13/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
593 | 596 | 6/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
594 | 597 | 7/22/2000 | Not Challenging | 17:30:00 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
595 | 598 | 10/12/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
596 | 599 |  | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
597 | 600 | 1/17/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
598 | 601 | 10/28/2004 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
599 | 602 | 9/29/2006 | Potentially Challenging |  | 22:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
600 | 603 | 11/14/2007 | Potentially Challenging | 16:18:00 | 16:18:00 | Known | 10 | 10 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
601 | 604 | 9/8/2000 | Not Challenging |  | 17:40:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
602 | 605 | 9/14/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
603 | 606 | 10/31/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
604 | 607 | 11/13/2008 | Undetermined (NC‐PC) | 09:50:00 | 09:52:00 | Known | 19 | 19 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
605 | 608
606 | 609 |  | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
607 | 10273 | 10/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
608 | 10274 | 10/21/2000 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed
609 | 10275
610 | 10276 | 12/15/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
611 | 10277 | 12/22/2000 | Not Challenging | 17:24:00 | 18:35:00 |  |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
612 | 10278 | 4/4/2001 | Not Challenging | 08:45:00 | 08:45:00 | Known | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
613 | 10279 | 4/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
614 | 10280 | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
615 | 10281
616 | 10282 | 8/12/2001 |  | 15:00:00 | 16:30:00 | Known | 150 | 150 | Thermal detector (e.g., temperature or rate of rise) | Unknown | Other (specify in comments)
617 | 10283 | 2/10/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
618 | 10284 | 3/10/2004 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed
619 | 10285 | 4/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
620 | 10286 | 5/10/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
621 | 10287 | 5/19/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
622 | 10288 | 5/22/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
623 | 10289 | 5/28/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments),Fuel supply removed (simple manual action e.g. valve turn off)
624 | 10290 | 6/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
625 | 10291 | 9/18/2004 | Undetermined (PC‐CH) |  | 17:35:00 | Known | 104 | 104 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel,Multiple portable fire extinguishers | ortable: Dry Chemical,Other: None
626 | 10292 | 1/13/2005 | Not Challenging | 10:32:00 | 10:32:00 | Known | 23 | 23 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) | Portable: None
627 | 10293 | 8/16/2005 | Undetermined (PC‐CH) | 22:28:00 | 22:28:00 | Known | 5 | 5 | Fire Watch | Unknown | Other (specify in comments)
628 | 10294 | 10/9/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
629 | 10295 | 10/18/2005 | Not Challenging | 22:52:00 | 22:52:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Single Portable fire extinguisher
630 | 10296 | 8/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
631 | 10297 | 12/14/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
632 | 10298 | 2/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
633 | 10299 | 2/19/2009 | Not Challenging |  | 10:21:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
634 | 10300 | 6/25/2009 | Not Challenging | 10:40:00 | 10:40:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
635 | 10301
636 | 10302 | 3/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
637 | 10303 | 5/18/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
638 | 10304 | 4/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
639 | 10305 | 10/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
640 | 10306
641 | 10307 | 10/3/2003 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed
642 | 10308 | 9/19/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
643 | 10309 | 4/18/2006 | Not Challenging | 14:25:00 | 14:25:00 | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
644 | 10310 | 1/29/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
645 | 10311 | 1/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
646 | 10312 | 2/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
647 | 10313 | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
648 | 10314
649 | 10315 | 10/18/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
650 | 10316 | 11/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
651 | 10317 | 9/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
652 | 10318 | 10/16/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
653 | 10319 | 1/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
654 | 10320 | 5/25/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
655 | 10321 | 6/1/2005 | Not Challenging |  |  | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
656 | 10322 | 12/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
657 | 10323 | 12/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
658 | 10324 | 12/30/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
659 | 10325
660 | 10326 | 1/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
661 | 10327 | 6/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
662 | 10328 | 7/17/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
663 | 10329 | 9/22/2008 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown
664 | 10330 | 9/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
665 | 10331 | 3/24/2009 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
666 | 10332
667 | 10333
668 | 10334 | 3/30/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
669 | 10335
670 | 10336 | 10/2/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
671 | 10337 | 10/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
672 | 10338 | 9/13/2001 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
673 | 10339 | 8/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
674 | 10340
675 | 10341 | 5/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
676 | 10342
677 | 10343 | 8/25/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
678 | 10344 | 10/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
679 | 10345 | 1/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
680 | 10346
681 | 10347
682 | 10348
683 | 10349 | 9/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
684 | 10350 | 1/21/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
685 | 10351
686 | 10352 | 12/11/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
687 | 10353 | 1/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
688 | 10354 | 7/2/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
689 | 10355 | 4/26/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
690 | 10356 | 10/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
691 | 10357 | 7/1/2005 | Potentially Challenging |  | 16:50:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
692 | 10358 | 7/3/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
693 | 10359 | 11/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
694 | 10360 | 10/13/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
695 | 10361 | 5/5/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
696 | 10362 | 10/28/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
697 | 10363 | 11/5/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
698 | 10364 | 6/30/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
699 | 10365 | 8/22/2008 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
700 | 10366
701 | 10367 | 10/22/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
702 | 10368 | 6/28/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2
703 | 10369 | 10/4/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
704 | 10370 | 4/11/2008 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
705 | 10371 | 10/20/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
706 | 10372 | 10/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
707 | 10373 | 4/14/2005 | Potentially Challenging |  | 10:58:00 | Known | 1 | 1 | Fire Watch | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
708 | 10374 | 7/11/2003 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
709 | 10375
710 | 10376 | 3/23/2004 | Challenging |  |  | Estimated | 10 | 10 | Unknown |  | Hose stream or hose reel
711 | 10377 | 3/10/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
712 | 10378 | 3/18/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
713 | 10379 | 3/22/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
714 | 10380 | 9/23/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
715 | 10381 | 10/24/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
716 | 10382 | 3/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
717 | 10383 | 4/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
718 | 10384 | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
719 | 10385 | 2/12/2002 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Self‐extinguished (no plant staff intervention)
720 | 10386 | 3/1/2003 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
721 | 10387 | 3/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
722 | 10388
723 | 10389 | 9/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
724 | 10390
725 | 10391
726 | 10392 | 4/5/2004 | Not Challenging |  | 13:30:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
727 | 10393 | 11/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
728 | 10394 | 2/22/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
729 | 10395 | 7/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
730 | 10396 | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
731 | 10397 | 10/12/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
732 | 10398
733 | 10399 | 1/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
734 | 10400
735 | 10401 | 5/9/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
736 | 10402 | 6/27/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker),Fuel supply removed (simple manual action e.g. valve turn off)
737 | 10403 | 10/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
738 | 10404 | 12/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
739 | 10405 | 1/20/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
740 | 10406 | Unknown | Not Challenging |  | Known | Known | 80 | 80 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Plant area did not have installed detection capability,Power supply removed (simple manual action e.g. open circuit breaker)
741 | 10407 | 6/3/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Potentially Challenging | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Potentially Challenging
742 | 10408
743 | 10409 | 12/12/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed,Self‐extinguished (no plant staff intervention)
744 | 10410 | 2/13/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Not Challenging,Self‐extinguished (no plant staff intervention)
745 | 10411 | 3/8/2008 | Not Challenging |  |  | Unknown |  |  | Not Challenging | Plant area did not have installed detection capability | Not Challenging
746 | 10412 | 2/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did no actuate, fire was detected visually or by other means – no indication of system failure
747 | 10413 | 5/17/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
748 | 10414 | 8/31/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
749 | 10415
750 | 10416 | 4/1/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
751 | 10417 | 4/17/2007 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed
752 | 10418 | 2/15/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
753 | 10419 | 4/12/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
754 | 10420 | 4/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
755 | 10421 | 6/20/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
756 | 10422 | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
757 | 10423 | 9/3/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
758 | 10424 | 10/19/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
759 | 10425 | 11/6/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: CO2
760 | 10426 | 4/29/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
761 | 10427 | 5/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
762 | 10428 | 6/1/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
763 | 10429 | 9/21/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
764 | 10430 | 12/21/2000 | Potentially Challenging |  | 22:22:00 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
765 | 10431
766 | 10432 | 10/22/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
767 | 10433 | 12/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
768 | 10434 | 5/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
769 | 10435 | 7/8/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
770 | 10436 | 8/11/2004 | Not Challenging |  | 10:20:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
771 | 10437 | 5/9/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
772 | 10438
773 | 10439
774 | 10440
775 | 10441 | 3/4/2009 | Potentially Challenging |  | 00:00:00 | Unknown |  |  | Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher
776 | 10442 | 3/9/2009 | Potentially Challenging |  | 07:40:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed
777 | 10443 | 7/25/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
778 | 10444 | 10/13/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power Supply Removed
779 | 10445 | 2/7/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
780 | 10446 | 4/11/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
781 | 10447 | 3/9/2000 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
782 | 10448 | 10/23/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
783 | 10449 | 5/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
784 | 10450 | 6/19/2001 | Potentially Challenging | 20:00:00 |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
785 | 10451 | 6/5/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
786 | 10452 | 9/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
787 | 10453 | 11/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
788 | 10454 | 2/17/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
789 | 10455 | 3/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
790 | 10456 | 7/19/2002 | Potentially Challenging |  | 11:15:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
791 | 10457 | 10/22/2002 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
792 | 10458 | 1/7/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Supervised burn out
793 | 10459 | 2/7/2003 | Not Challenging |  | 10:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
794 | 10460 | 4/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
795 | 10461 | 3/6/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
796 | 10462 | 2/5/2004 | Undetermined (NC‐PC) |  | 22:54:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed,Unknown
797 | 10463 | 3/1/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
798 | 10464 | 3/30/2005 | Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression ‐ manually actuated,Single Portable fire extinguisher,Power Supply Removed | Portable: Other [specify],Other: Other [specify]
799 | 10465 | 9/30/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
800 | 10466 | 8/31/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power Supply Removed | Portable: CO2
801 | 10467 | 4/7/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
802 | 10468 | 10/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
803 | 10469 | 3/23/2006 | Not Challenging |  | 22:23:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
804 | 10470 | 5/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
805 | 10471 | 12/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed，Other (specify in comments)
806 | 10472 | 9/25/2007 | Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) |  | Power Supply Removed
807 | 10473 | 1/23/2007 | Not Challenging |  |  | Unknown |  |  |  |  | Unknown
808 | 10474 | 2/23/2007 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
809 | 10475 | [7 empty] | Other plant personnel (in vicinity or passerby)
810 | 10476 | 4/10/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
811 | 10477 | 6/7/2007 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments)
812 | 10478 | 7/10/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed，Other (specify in comments)
813 | 10479 | 7/23/2008 | Not Challenging |  | 09:22:00 | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
814 | 10480 | 7/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
815 | 10481
816 | 10482 | 10/22/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
817 | 10483 | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
818 | 10484 | 4/16/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
819 | 10485 | 4/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
820 | 10486 | 7/28/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
821 | 10487 | 9/4/2007 | Not Challenging |  | 08:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
822 | 10488 | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
823 | 10489 | 4/6/2008 | Challenging |  | 07:27:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Fuel supply removed (simple manual action e.g. valve turn off) | Other: Water
824 | 10490 | 4/9/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
825 | 10491 | 4/29/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
826 | 10492 | 9/30/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
827 | 10493 | 10/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
828 | 10494
829 | 10495
830 | 10496 | 5/14/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
831 | 10497 | 7/31/2009 | Not Challenging |  | 06:50:00 | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
832 | 10498 | 9/26/2009 | Not Challenging |  | 20:42:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
833 | 10499 | 10/16/2009 | Not Challenging |  | 17:46:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
834 | 10500
835 | 10501
836 | 10502
837 | 10503
838 | 10504 | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
839 | 10505 | 3/16/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
840 | 10506
841 | 10507 | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
842 | 10508 | 3/28/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
843 | 10509 | 4/1/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
844 | 10510 | 4/10/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
845 | 10511
846 | 10512 | 6/22/2001 | Not Challenging |  | 22:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker)
847 | 10513 | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
848 | 10514 | 8/26/2001 | Potentially Challenging |  | 23:38:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
849 | 10515 | 9/30/2001 | Potentially Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers
850 | 10516 | 11/20/2001 | Potentially Challenging |  | 12:43:00 | Estimated | 10 | 10 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
851 | 10517 | 8/5/2002 | Not Challenging |  | 11:46:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
852 | 10518 | 8/26/2002 | Not Challenging | 22:15:00 | 22:15:00 | Known | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
853 | 10519 | 9/25/2002 | Not Challenging |  | 03:45:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
854 | 10520 | 11/26/2002 | Not Challenging |  | 14:45:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical，Other: Water
855 | 10521 | 9/10/2003 | Not Challenging |  | 02:15:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention) | Portable: CO2
856 | 10522 | 11/2/2003 | Potentially Challenging |  | 23:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
857 | 10523 | 11/9/2003 | Not Challenging |  | 12:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
858 | 10524 | 1/7/2004 | Potentially Challenging |  | 18:27:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
859 | 10525 | 5/10/2004 | Not Challenging |  | 13:49:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
860 | 10526 | 5/30/2004 | Not Challenging |  | 23:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
861 | 10527
862 | 10528 | 9/8/2004 | Not Challenging |  | 12:55:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
863 | 10529 | 1/25/2006 | Not Challenging |  | 17:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
864 | 10530 | 3/15/2006 | Not Challenging |  | 14:30:00 | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
865 | 10531 | 3/31/2006 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
866 | 10532 | 6/28/2006 | Not Challenging |  | 12:15:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Power supply removed (simple manual action e.g. open circuit breaker)
867 | 10533 | 2/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
868 | 10534 | 3/21/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
869 | 10535 | 3/31/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
870 | 10536 | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
871 | 10537 | 2/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
872 | 10538 | 4/1/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
873 | 10539 | 1/19/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
874 | 10540 | 2/4/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
875 | 10541 | 3/24/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
876 | 10542 | 7/9/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
877 | 10543 | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
878 | 10544 | 1/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water
879 | 10545 | 5/9/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
880 | 10546 | 3/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
881 | 10547 | 1/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
882 | 10548 | 6/25/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
883 | 10549 | 10/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
884 | 10550 | 9/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Single Portable fire extinguisher
885 | 10551 | 7/14/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
886 | 10552 | 7/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
887 | 10553 | 4/17/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
888 | 10554 | 5/3/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
889 | 10555 | 5/5/2004 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher
890 | 10556 | 5/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
891 | 10557 | 1/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
892 | 10558 | 1/19/2005 | Potentially Challenging | 16:54:00 | 16:54:00 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
893 | 10559 | 3/7/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
894 | 10560 | 3/29/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
895 | 10561 | 4/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
896 | 10562 | 5/23/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
897 | 10563 | 7/11/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
898 | 10564 | 8/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
899 | 10565 | 8/15/2005 | Not Challenging |  | 12:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
900 | 10566 | 9/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
901 | 10567 | 12/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
902 | 10568 | 1/12/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Single Portable fire extinguisher
903 | 10569 | 2/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
904 | 10570 | 2/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
905 | 10571 | 3/5/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
906 | 10572 | 4/13/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
907 | 10573 | 7/5/2006 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
908 | 10574 | 7/17/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
909 | 10575 | 7/18/2006 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
910 | 10576 | 7/26/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered)
911 | 10577 | 10/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
912 | 10578
913 | 10579 | 4/4/2008 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
914 | 10580 | 4/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
915 | 10581 | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
916 | 10582 | 12/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers
917 | 10583 | 9/1/2006 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
918 | 10584 | 7/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
919 | 10585 | 4/24/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
920 | 10586 | 1/19/2000 | Not Challenging |  | 15:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
921 | 10587 | 8/10/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fixed suppression ‐ manually actuated | Other: Other [specify]
922 | 10588 | 11/21/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
923 | 10589 | 2/3/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
924 | 10590 | 10/3/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
925 | 10591 | 10/8/2002 | Not Challenging |  | 08:15:00 | Known | 517 | 517 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
926 | 10592 | 1/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
927 | 10593 | 7/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
928 | 10594 | 1/25/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
929 | 10595 | 2/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
930 | 10596 | 11/4/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
931 | 10597
932 | 10598 | 1/3/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
933 | 10599 | 3/25/2006 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
934 | 10600 | 2/18/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
935 | 10601 | 2/16/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
936 | 10602 | 2/13/2008 | Not Challenging |  | 02:55:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
937 | 10603
938 | 10604 | 5/14/2001 | Potentially Challenging | 08:22:00 | 08:22:00 | Known | 14 | 14 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
939 | 10605 | 1/31/2006 | Potentially Challenging | 15:29:00 | 15:29:00 | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
940 | 10606 | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
941 | 10607 | 12/27/2004 | Not Challenging |  | 00:02:00 | Known | 49 | 49 | Installed Fire detector ‐ Type not specified | Hose stream or hose reel,Multiple portable fire extinguishers | Plant area had installed detection which actuated | Portable: Dry Chemical,Other: Water
942 | 10608
943 | 10609 | 9/7/2008 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Other (specify in comments)
944 | 10610
945 | 10611 | 8/20/2009 | Potentially Challenging |  | 15:49:00 | Estimated | 10 | 10 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Dry Chemical
946 | 10612
947 | 10613
948 | 10614 | 2/25/2004 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown
949 | 10615 | 10/15/2005 | Undetermined (NC‐PC) |  |  | Unknown | 0 | 0 |  |  | Unknown
950 | 10616
951 | 10617 | 2/14/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
952 | 10618 | 2/15/2000 | Undetermined (PC‐CH) | 16:17:00 | 16:17:00 | Known | 13 | 13 | Roving Firewatch | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
953 | 10619 | 5/24/2000 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
954 | 10620 | 8/9/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
955 | 10621 | 8/22/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
956 | 10622 | 6/25/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown
957 | 10623 | 8/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
958 | 10624 | 10/26/2001 | Not Challenging |  |  | Estimated | 18 | 18 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Unknown
959 | 10625 | 9/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
960 | 10626 | 12/11/2002 | Potentially Challenging | 03:05:00 | 03:05:00 | Known | 67 | 67 | Main control room staff (e.g., control/instrumentation failures) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
961 | 10627 | 12/12/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
962 | 10628 | 12/30/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
963 | 10629
964 | 10630 | 6/6/2007 | Potentially Challenging | 15:36:00 | 15:36:00 | Known |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
965 | 10631 | 11/28/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
966 | 10632 | 3/3/2000 | Challenging | 11:45:00 | 11:45:00 | Known | 275 | 275 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic) | Other: Halon
967 | 10633 | 3/7/2000 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
968 | 10634
969 | 10635
970 | 10636 | 9/26/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed
971 | 10637
972 | 10638 | 3/5/2001 | Potentially Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
973 | 10639 | 2/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
974 | 10640
975 | 10641 | 3/11/2001 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
976 | 10642 | 3/14/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Other: Water
977 | 10643 | 5/22/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
978 | 10644 | 11/3/2002 | Potentially Challenging |  |  | Known | 7 | 7 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
979 | 10645 | 4/11/2003 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed
980 | 10646 | 7/17/2003 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
981 | 10647 | 8/22/2003 | Potentially Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed
982 | 10648 | 3/12/2004 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) |  | Self‐extinguished (no plant staff intervention)
983 | 10649 | 3/15/2004 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
984 | 10650 | 3/20/2004 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
985 | 10651
986 | 10652 | 3/10/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
987 | 10653 | 4/3/2005 | Not Challenging |  | 04:43:00 | Known | 334 | 334 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
988 | 10654 | 2/5/2007 | Not Challenging |  | 11:08:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
989 | 10655
990 | 10656 | 2/22/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
991 | 10657 | 6/29/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: CO2
992 | 10658 | 12/29/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
993 | 10659
994 | 10660 | 11/6/2009 | Not Challenging |  | 22:20:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
995 | 10661
996 | 10662
997 | 10663
998 | 10664 | 10/2/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
999 | 10665 | 11/3/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
1000 | 10666 | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
1001 | 10667 | 4/26/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
1002 | 10668 | 4/22/2001 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
1003 | 10669 | 5/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1004 | 10670 | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
1005 | 10671 | 6/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1006 | 10672 | 6/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 |  |  | Unknown
1007 | 10673 | 9/4/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Fuel supply removed,Unknown
1008 | 10674 | 12/5/2002 | Not Challenging | 06:45:00 | 06:45:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
1009 | 10675 | 12/31/2002 | Not Challenging |  | 14:15:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
1010 | 10676 | 3/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
1011 | 10677 | 4/4/2003 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention)
1012 | 10678 | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)
1013 | 10679 | 1/9/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1014 | 10680 | 7/10/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1015 | 10681 | 11/12/2004 | Not Challenging |  | 14:55:00 | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown
1016 | 10682 | 4/2/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1017 | 10683 | 4/5/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1018 | 10684 | 4/6/2005 | Potentially Challenging |  |  | Known | 0 | 0 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1019 | 10685 | 4/11/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1020 | 10686 | 4/13/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1021 | 10687 | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1022 | 10688 | 10/31/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1023 | 10689 | 1/26/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1024 | 10690 | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
1025 | 10691 | 2/25/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed,Unknown
1026 | 10692
1027 | 10693 | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
1028 | 10694 | 7/10/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1029 | 10695 | 7/27/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Unknown
1030 | 10696 | 8/30/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1031 | 10697 | 2/25/2008 | Not Challenging |  | 09:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1032 | 10698 | 4/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1033 | 10699 | 4/24/2008 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1034 | 10700 | 7/18/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1035 | 10701 | 8/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1036 | 10702 | 2/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1037 | 10703 | 11/21/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1038 | 10704 | 3/28/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1039 | 10705 | 12/3/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
1040 | 10706 | 12/4/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1041 | 10707 | 8/8/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1042 | 10708 | 9/22/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1043 | 10709 | 2/1/2005 | Not Challenging | 07:20:00 | 07:20:00 | Known | 5 | 5 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1044 | 10710 | 11/21/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1045 | 10711 | 1/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1046 | 10712 | 10/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1047 | 10713 | 3/25/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1048 | 10714
1049 | 10715 | 2/5/2009 | Potentially Challenging |  | 04:30:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
1050 | 10716 | 7/26/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1051 | 10717 | 4/12/2003 | Not Challenging |  | 01:35:00 | Unknown | 2 | 2 | Other plant personnel (in vicinity or passerby) |  | Power Supply Removed,Self‐extinguished (no plant staff intervention)
1052 | 10718 | 5/20/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher
1053 | 10719 | 6/1/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1054 | 10720 | 4/8/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher
1055 | 10721 | 8/26/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1056 | 10722 | 9/3/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1057 | 10723 | 10/4/2007 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1058 | 10724 | 10/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1059 | 10725 | 10/29/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1060 | 10726 | 11/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1061 | 10727 | 2/5/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
1062 | 10728 | 8/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1063 | 10729 | 4/3/2009 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers
1064 | 10730 | 3/16/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Self‐extinguished (no plant staff intervention) |  | Unknown
1065 | 10731 | 6/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1066 | 10732 | 4/22/2002 | Not Challenging |  | 01:35:00 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
1067 | 10733 | 4/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1068 | 10734 | 4/27/2004 | Not Challenging |  | 15:30:00 | Known |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1069 | 10735 | 4/28/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1070 | 10736 | 12/6/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
1071 | 10737 | 11/30/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1072 | 10738 | 8/22/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1073 | 10739 | 4/24/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Self‐extinguished (no plant staff intervention)
1074 | 10740 | 10/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1075 | 10741 | 9/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1076 | 10742 | 4/11/2004 | Not Challenging | 10:00:00 | 10:00:00 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin |  | Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
1077 | 10743 | 4/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out
1078 | 10744 | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1079 | 10745 | 7/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1080 | 10746 | 5/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1081 | 10747 | 1/15/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1082 | 10748 | 5/29/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1083 | 10749 | 9/10/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1084 | 10750 | 2/28/2009 | Not Challenging |  | 05:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed | Portable: Dry Chemical
1085 | 10751 | 1/28/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
1086 | 10752
1087 | 10753
1088 | 10754
1089 | 20264 | 1/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Unknown | Unknown | Single Portable fire extinguisher | Portable: CO2
1090 | 20265 | 2/2/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1091 | 20266 | 2/19/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Unknown | Unknown | Unknown
1092 | 20267 | 3/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1093 | 20268 | 4/19/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1094 | 20269 | 4/30/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1095 | 20270 | 6/7/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1096 | 20271 | 7/9/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1097 | 20272 | 9/10/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1098 | 20273 | 9/18/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1099 | 20274 | 10/9/1990 | Potentially Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
1100 | 20275 | 10/11/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1101 | 20276 | 10/12/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1102 | 20277 | 11/16/1990 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1103 | 20278 | 11/24/1990 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
1104 | 20279 | 11/28/1990 | Potentially Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1105 | 20280 | 12/5/1990 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1106 | 20281 | 6/24/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1107 | 20282 | 9/17/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1108 | 20283 | 10/3/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1109 | 20284 | 10/14/1991 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1110 | 20285 | 10/25/1991 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
1111 | 20286 | 1/23/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1112 | 20287 | 2/29/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1113 | 20288 | 3/9/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1114 | 20289 | 3/16/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1115 | 20290 | 4/26/1992 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
1116 | 20291 | 4/28/1992 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1117 | 20292 | 6/25/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1118 | 20293 | 9/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1119 | 20294 | 10/5/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1120 | 20295 | 10/12/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1121 | 20296 | 10/23/1992 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Unknown
1122 | 20297 | 11/17/1992 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1123 | 20298 | 1/11/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1124 | 20299 | 3/9/1993 | Not Challenging |  |  | Known | 1 | 1 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1125 | 20300 | 3/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1126 | 20301 | 4/13/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1127 | 20302 | 7/25/1993 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1128 | 20303 | 10/14/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify]
1129 | 20304 | 11/2/1993 | Potentially Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1130 | 20305 | 11/18/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1131 | 20306 | 12/30/1993 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1132 | 20307 | 1/25/1994 | Not Challenging |  |  | Known | 0 | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
1133 | 20308 | 3/9/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1134 | 20309 | 3/11/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
1135 | 20310 | 3/26/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1136 | 20311 | 4/4/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1137 | 20312 | 7/27/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
1138 | 20313 | 9/29/1994 | Undetermined (NC‐PC) |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1139 | 20314 | 12/19/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1140 | 20315 | 2/20/1995 | Not Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1141 | 20316 | 2/24/1995 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1142 | 20317 | 4/10/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1143 | 20318 | 8/9/1995 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Other [specify]
1144 | 20319 | 8/15/1995 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power Supply Removed | Portable: Other [specify]
1145 | 20320 | 3/21/1996 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1146 | 20321 | 7/10/1996 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1147 | 20322 | 9/13/1996 | Undetermined (NC‐PC) |  |  | Estimated | 46 | 46 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
1148 | 20323 | 1/8/1997 | Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments) | Portable: Other [specify]
1149 | 20324 | 8/12/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1150 | 20325 | 1/16/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify
1151 | 20326 | 10/12/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1152 | 20327 | 11/2/1998 | Not Challenging | 05:55:00 | 05:55:00 | Known | 7 | 7 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1153 | 20328 | 5/6/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Other [specify]
1154 | 20329 | 9/1/1999 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Other (specify in comments)
1155 | 20330 | 10/3/1999 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1156 | 20331 | 11/4/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
1157 | 20332 | 12/14/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1158 | 20333 | 1/12/1990 | Not Challenging |  |  | Known | 1 | 1 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
1159 | 20334 | 2/20/1990 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1160 | 20335 | 4/13/1990 | Not Challenging |  |  | Unknown | 2 | 2 | Fire Watch | Unknown | Unknown
1161 | 20336 | 2/14/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
1162 | 20337 | 4/21/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1163 | 20338 | 10/11/1991 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Unknown
1164 | 20339
1165 | 20340 | 12/1/1992 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1166 | 20341 | 3/31/1993 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1167 | 20342 | 4/30/1993 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1168 | 20343 | 8/13/1993 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Air supply cut off (smothered, covered)
1169 | 20344 | 2/20/1994 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1170 | 20345 | 3/28/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
1171 | 20346 | 3/30/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1172 | 20347 | 4/15/1994 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1173 | 20348 | 4/16/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1174 | 20349 | 4/23/1994 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Other [specify]
1175 | 20350 | 6/9/1994 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1176 | 20351 | 6/21/1994 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
1177 | 20352 | 6/23/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2
1178 | 20353 | 7/13/1994 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1179 | 20354 | 10/8/1994 | Not Challenging |  |  | Known |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1180 | 20355 | 10/31/1994 | Not Challenging | 09:22:00 | 09:22:00 | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed
1181 | 20356 | 2/19/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1182 | 20357 | 5/24/1995 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1183 | 20358 | 1/23/1996 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1184 | 20359 | 3/3/1996 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
1185 | 20360 | 5/25/1996 | Undetermined (PC‐CH) |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Self‐extinguished (no plant staff intervention),Power supply removed (simple manual action e.g. open circuit breaker)
1186 | 20361 | 1/7/1997 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1187 | 20362 | 3/2/1997 | Potentially Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1188 | 20363 | 7/27/1997 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Power Supply Removed
1189 | 20364 | 12/4/1997 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1190 | 20365 | 1/13/1998 | Potentially Challenging |  |  | Estimated | 23 | 23 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1191 | 20366 | 2/6/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1192 | 20367 | 2/24/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1193 | 20368 | 6/7/1998 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1194 | 20369 | 6/14/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1195 | 20370 | 7/1/1998 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1196 | 20371 | 9/9/1998 | Undetermined (NC‐PC) |  |  | Unknown |  |  |  |  | Unknown
1197 | 20372 | 11/23/1998 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1198 | 20373 | 3/16/1999 | Potentially Challenging |  |  | Estimated | 10 | 10 | Fire Watch | Unknown | Self‐extinguished (no plant staff intervention)
1199 | 20374 | 3/19/1999 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1200 | 20375 | 3/29/1999 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Dry Chemical
1201 | 20376 | 7/29/1999 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1202 | 20377 | 2/8/2000 | Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water
1203 | 20378 | 2/25/2000 | Potentially Challenging | 23:33:00 | 23:33:00 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers | Portable: Other [specify]
1204 | 20379 | 6/20/2000 | Challenging |  |  | Estimated | 2 | 2 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
1205 | 20380 | 8/16/2000 | Potentially Challenging | 15:48:00 | 15:48:00 | Known | 21 | 21 | Gas Ionization | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
1206 | 20381 | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Multiple portable fire extinguishers | Portable: Other [specify]
1207 | 20382 | 10/23/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1208 | 20383 | 11/5/2000 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1209 | 20384
1210 | 20385 | 12/27/2000 | Undetermined (PC‐CH) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers | Portable: CO2
1211 | 30265 | 8/5/2008 | Not Challenging | 02:26:00 | 02:26:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1212 | 30266 | 1/20/2009 | Potentially Challenging | 19:26:00 | 19:26:00 | Known | 5 | 5 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: CO2
1213 | 30267
1214 | 30268 | 8/9/2000 | Not Challenging | 12:36:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1215 | 30269 | 8/14/2002 | Not Challenging | 15:41:00 |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power Supply Removed
1216 | 30270 | 3/16/2003 | Potentially Challenging | 11:35:00 | 11:35:00 | Known | 5 | 5 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1217 | 30271 | 9/11/2003 | Undetermined (PC‐CH) | 02:46:00 | 02:46:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1218 | 30272 | 7/9/2004 | Not Challenging | 08:30:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown | Other: Water
1219 | 30273
1220 | 30274
1221 | 30275 | 1/13/2006 | Not Challenging | 08:56:00 |  | Unknown |  |  | Unknown | Unknown | Power Supply Removed
1222 | 30276 | 7/24/2006 | Potentially Challenging | 19:10:00 | 19:10:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed
1223 | 30277 | 12/3/2007 | Potentially Challenging | 16:59:00 | 16:59:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
1224 | 30278 | 10/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical,Other: Other [specify]
1225 | 30279 | 5/12/2002 | Not Challenging | 11:30:00 |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1226 | 30280
1227 | 30281 | 6/5/2008 | Potentially Challenging | 13:13:00 |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other，means – no indication of system failure | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1228 | 30282 | 11/26/2001 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1229 | 30283 | 3/20/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1230 | 30284 | 3/12/2004 | Not Challenging |  |  | Known | 22 | 22 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Power Supply Removed
1231 | 30285 | 11/2/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1232 | 30286 | 6/18/2009 | Potentially Challenging | 16:18:00 |  | Estimated | 2 | 2 | Fire Watch |  | Single Portable fire extinguisher | Portable: Other [specify]
1233 | 30287 | 10/1/2009 | Potentially Challenging |  |  | Known | 9 | 9 | Fire Watch | Unknown | Single Portable fire extinguisher
1234 | 30288 | 4/14/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
1235 | 30289 | 7/8/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Single Portable fire extinguisher | Portable: Dry Chemical
1236 | 30290 | 1/20/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments) | Portable: CO2
1237 | 30291 | 3/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical
1238 | 30292 | 6/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1239 | 30293 | 8/20/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1240 | 30294 | 11/7/2001 | Not Challenging | 10:30:00 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1241 | 30295 | 3/15/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1242 | 30296 | 11/22/2002 | Potentially Challenging |  |  | Known | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1243 | 30297 | 8/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1244 | 30298 | 4/13/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: Water
1245 | 30299 | 4/25/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1246 | 30300 | 5/13/2006 | Not Challenging | 13:13:00 |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1247
1248 | 40730 | 10/27/2000 | Not Challenging |  | 14:00:00 | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1249 | 40731 | 2/13/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
1250 | 40732 | 3/8/2001 | Not Challenging |  | 15:50:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments
1251 | 40733 | 3/14/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g. valve turn off)
1252 | 40734 | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1253 | 40735 | 4/4/2001 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered | Portable: Other [specify]
1254 | 40736 | 4/15/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1255 | 40737 | 4/17/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
1256 | 40738 | 6/5/2002 | Not Challenging |  | 03:00:00 | Known | 105 | 105 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water
1257 | 40739 | 7/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power Supply Removed
1258 | 40740 | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1259 | 40741 | 4/16/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
1260 | 40742 | 7/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1261 | 40743 | 10/7/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Other [specify]
1262 | 40744 | 3/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1263 | 40745 | 10/20/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1264 | 40746 | 8/15/2006 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher,Other (specify in comments) | Portable: CO2
1265 | 40747 | 4/17/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1266 | 40748 | 11/28/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1267 | 40749 | 6/13/2008 | Not Challenging |  |  | Known | 9 | 9 | Dedicated Fire Watch | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified,Multiple portable fire extinguishers | Portable: CO2,Other: Water
1268 | 40750 | 11/16/2009 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1269
1270 | 50356 | 1/11/2000 | Not Challenging |  | 10:30:00 | Known | 0 | 0 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1271 | 50357 | 3/21/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power Supply Removed | Other: None
1272 | 50358 | 6/1/2000 | Not Challenging |  | 10:11:00 | Estimated | 45 | 45 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Hose stream or hose reel,Supervised burn out | Other: Water
1273 | 50359 | 8/24/2000 | Not Challenging |  | 14:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1274 | 50360 | 12/20/2000 | Not Challenging |  | 03:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1275 | 50361 | 4/11/2001 | Potentially Challenging |  | 18:10:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments),Power supply removed (simple manual action e.g. open circuit breaker)
1276 | 50362 | 7/16/2001 | Not Challenging |  | 15:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1277 | 50363
1278 | 50364 | 10/4/2001 | Not Challenging |  | 10:00:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed | Portable: None
1279 | 50365 | 3/4/2002 | Not Challenging |  | 02:10:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments)
1280 | 50366 | 3/8/2002 | Not Challenging |  | 15:00:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments)
1281 | 50367 | 3/14/2002 | Not Challenging | 21:30:00 | 21:30:00 | Known | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Other (specify in comments)
1282 | 50368 | 6/6/2002 | Not Challenging | 04:08:00 | 04:08:00 | Known | 1 | 1 | Smoke detector | Plant area had installed detection which actuated | Unknown
1283 | 50369 | 8/14/2002 | Not Challenging |  | 03:50:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1284 | 50370 | 10/23/2002 | Not Challenging |  | 13:18:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
1285 | 50371 | 11/1/2002 | Not Challenging |  | 17:12:00 | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1286 | 50372 | 5/9/2003 | Not Challenging |  | 00:30:00 | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power Supply Removed,Other (specify in comments)
1287 | 50373 | 10/7/2003 | Not Challenging |  | 10:36:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention) | Portable: Dry Chemical
1288 | 50374 | 4/22/2004 | Not Challenging |  | 07:50:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
1289 | 50375 | 9/30/2004 | Not Challenging |  | 05:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1290 | 50376 | 3/24/2005 | Not Challenging |  | 08:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1291 | 50377 | 7/2/2005 | Not Challenging |  | 10:15:00 | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1292 | 50378 | 7/27/2005 | Potentially Challenging | 12:53:00 | 12:55:00 | Known | 12 | 12 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
1293 | 50379 | 2/24/2006 | Not Challenging | 08:05:00 | 08:05:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power Supply Removed
1294 | 50380 | 8/31/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1295 | 50381 | 12/14/2006 | Not Challenging |  | 08:30:00 | Estimated | 13 | 13 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1296 | 50382 | 1/29/2007 | Not Challenging | 12:10:00 | 12:10:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1297 | 50383 | 3/1/2007 | Not Challenging | 02:00:00 | 02:00:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1298 | 50384 | 3/22/2007 | Not Challenging |  | 00:21:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1299 | 50385 | 5/30/2007 | Not Challenging |  | 11:30:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
1300 | 50386
1301 | 50387 | 3/29/2008 | Not Challenging |  | 14:19:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1302 | 50388 | 6/8/2008 | Not Challenging |  | 00:44:00 | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power Supply Removed
1303 | 50389 | 6/23/2008 | Not Challenging | 12:25:00 | 12:25:00 | Known | 6 | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1304 | 50390 | 10/1/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Air supply cut off (smothered, covered)
1305 | 50391 | 7/2/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
1306 | 50392 | 8/13/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Power Supply Removed,Self‐extinguished (no plant staff intervention)
1307 | 50393 | 10/17/2000 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1308 | 50394 | 4/21/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1309 | 50395 | 4/16/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Other (specify in comments)
1310 | 50396 | 5/1/2001 | Not Challenging |  | 23:05:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1311 | 50397 | 1/13/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1312 | 50398 | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1313 | 50399 | 2/26/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1314 | 50400 | 8/7/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments)
1315 | 50401 | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1316 | 50402 | 11/8/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed,Fuel supply removed,Other (specify in comments)
1317 | 50403 | 11/8/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Water
1318 | 50404 | 11/25/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1319 | 50405 | 3/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1320 | 50406 | 8/21/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1321 | 50407 | 3/11/2008 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1322 | 50408
1323 | 50409 | 10/5/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Fire Watch | Unknown | Single Portable fire extinguisher
1324 | 50410 | 9/29/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
1325 | 50411 | 7/9/2005 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1326 | 50412
1327 | 50413
1328 | 50414
1329 | 50415
1330 | 50416
1331 | 50417
1332 | 50418
1333 | 50419
1334 | 50420
1335 | 50421
1336 | 50422
1337 | 50423 | 2/28/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1338 | 50424 | 3/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other simple: (e.g. blown out, stamped out; specify in comments)
1339 | 50425 | 3/16/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Multiple portable fire extinguishers,Other (specify in comments)
1340 | 50426 | 5/2/2000 | Potentially Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g. open circuit breaker)
1341 | 50427 | 8/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1342 | 50428 | 9/20/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1343 | 50429 | 3/19/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1344 | 50430 | 2/18/2000 | Not Challenging |  | 06:21:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
1345 | 50431
1346 | 50432 | 3/19/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1347 | 50433 | 8/17/2001 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
1348 | 50434 | 10/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1349 | 50435 | 7/22/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1350 | 50436 | 8/12/2002 | Not Challenging |  |  | Unknown |  |  | Fire Watch | Unknown | Unknown
1351 | 50437
1352 | 50438 | 1/7/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Power Supply Removed
1353 | 50439 | 3/3/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1354 | 50440 | 10/13/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1355 | 50441 | 10/23/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1356 | 50442 | 11/8/2004 | Potentially Challenging | 21:23:00 | 21:23:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1357 | 50443 | 3/20/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1358 | 50444 | 4/27/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1359 | 50445 | 4/28/2005 | Not Challenging | 16:00:00 | 16:00:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1360 | 50446 | 7/14/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1361 | 50447 | 9/14/2005 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1362 | 50448 | 10/11/2005 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments)
1363 | 50449 | 2/21/2006 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown
1364 | 50450 | 2/28/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Single Portable fire extinguisher
1365 | 50451 | 7/15/2006 | Not Challenging |  |  | Known | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1366 | 50452 | 8/18/2006 | Undetermined (NC‐PC) |  | 13:00:00 | Known | 4 | 4 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
1367 | 50453 | 8/22/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1368 | 50454 | 11/8/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1369 | 50455 | 11/30/2006 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1370 | 50456 | 2/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1371 | 50457 | 7/28/2007 | Not Challenging | 16:05:00 | 16:05:00 | Known | 12 | 12 | Other plant personnel (in vicinity or passerby) | Unknown | Fixed suppression system ‐ deluge (automatic),Hose stream or hose reel,Multiple portable fire extinguishers,Power supply removed (simple manual action e.g. open circuit breaker) | Other: Water
1372 | 50458 | 8/15/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1373 | 50459 | 2/8/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power Supply Removed
1374 | 50460 | 4/16/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher,Other (specify in comments)
1375 | 50461 | 4/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1376 | 50462 | 6/12/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher,Other (specify in comments) | Portable: Water
1377 | 50463 | 4/11/2000 | Not Challenging |  |  | Estimated | 10 | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1378 | 50464 | 4/26/2000 | Not Challenging |  |  | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1379 | 50465
1380 | 50466 | 2/4/2005 | Not Challenging |  |  | Unknown |  |  |  | Plant area had installed detection which actuated | Unknown
1381 | 50467 | 2/4/2006 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1382 | 50468 | 11/2/2007 | Not Challenging |  |  | Unknown |  |  |  | Unknown | Unknown
1383 | 50469 | 7/28/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1384 | 50470 | 11/19/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention)
1385 | 50471 | 12/2/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1386 | 50472 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1387 | 50473 | 6/26/2000 | Potentially Challenging |  | 15:13:00 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1388 | 50474 | 8/29/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1389 | 50475 | 10/11/2000 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1390 | 50476 | 12/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1391 | 50477 | 3/18/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
1392 | 50478 | 3/19/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1393 | 50479 | 3/22/2000 | Potentially Challenging |  | 07:15:00 | Known | 19 | 19 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Other (specify in comments) | Portable: Dry Chemical
1394 | 50480 | 4/7/2000 | Not Challenging | 19:35:00 | 19:35:00 | Known | 4 | 4 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1395 | 50481 | 11/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which actuated | Other (specify in comments)
1396 | 50482 | 3/8/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1397 | 50483 | 3/11/2008 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1398 | 50484 | 3/23/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1399 | 50485
1400 | 50486 | 4/20/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
1401 | 50487 | 3/6/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1402 | 50488 | 5/27/2009 | Not Challenging | 15:55:00 | 15:55:00 | Known | 5 | 5 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1403 | 50489 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1404 | 50490 | 9/16/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1405 | 50491 | 10/16/2009 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1406 | 50492 | 11/2/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1407 | 50493
1408 | 50494 | 2/5/2009 | Not Challenging | 18:28:00 | 18:28:00 | Known | 16 | 16 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Multiple portable fire extinguishers | Portable: CO2
1409 | 50495 | 11/11/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1410 | 50496 | 1/21/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1411 | 50497 | 8/15/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1412 | 50498
1413 | 50499 | 4/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1414 | 50500
1415 | 50501 | 11/6/2001 | Not Challenging |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1416 | 50502 | 10/16/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1417 | 50503 | 6/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1418 | 50504 | 5/20/2002 | Potentially Challenging | 08:54:00 | 08:54:00 | Estimated | 2 | 2 | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1419 | 50505
1420 | 50506 | 12/9/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
1421 | 50507 | 11/15/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Other [specify]
1422 | 50508 | 11/26/2005 | Not Challenging | 00:40:00 |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Water
1423 | 50509
1424 | 50510 | 4/19/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
1425 | 50511 | 5/15/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: None
1426 | 50512 | 5/31/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1427 | 50513 | 8/27/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1428 | 50514 | 4/29/2009 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
1429 | 50515 | 11/30/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1430 | 50516 | 10/5/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1431 | 50517 | 10/8/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: CO2
1432 | 50518 | 11/18/2001 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Multiple portable fire extinguishers | Portable: CO2
1433 | 50519 | 10/19/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1434 | 50520 | 12/7/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1435 | 50521 | 2/1/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1436 | 50522 | 9/8/2003 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1437 | 50523 | 9/19/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1438 | 50524 | 1/23/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1439 | 50525 | 12/18/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1440 | 50526 | 12/7/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1441 | 50527 | 6/23/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Water
1442 | 50528 | 6/19/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1443 | 50529 | 3/31/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
1444 | 50530 | 10/21/2008 | Potentially Challenging |  | 08:56:00 | Known | 540 | 540 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1445 | 50531
1446 | 50532
1447 | 50533
1448 | 50534 | 1/7/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
1449 | 50535 | 1/8/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1450 | 50536 | 3/21/2002 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1451 | 50537 | 3/23/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1452 | 50538 | 3/27/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Fuel supply removed
1453 | 50539 | 5/22/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1454 | 50540 | 5/25/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Power Supply Removed
1455 | 50541 | 4/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed
1456 | 50542 | 7/30/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1457 | 50543 | 3/27/2001 | Potentially Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
1458 | 50544
1459 | 50545 | 9/18/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1460 | 50546 | 12/1/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1461 | 50547 | 4/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1462 | 50548 | 6/9/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1463 | 50549 | 1/21/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1464 | 50550 | 6/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1465 | 50551 | 10/6/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1466 | 50552 | 3/23/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1467 | 50553 | 5/2/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: Halon
1468 | 50554 | 5/19/2003 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1469 | 50555 | 6/25/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1470 | 50556 | 2/25/2005 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1471 | 50557 | 1/16/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1472 | 50558 | 1/2/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other (specify in comments)
1473 | 50559
1474 | 50560
1475 | 50561
1476 | 50562 | 5/28/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1477 | 50563 | 11/16/2005 | Undetermined (PC‐CH) |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1478 | 50564 | 1/15/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
1479 | 50565 | 8/26/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1480 | 50566 | 9/17/2008 | Not Challenging | 09:30:00 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1481 | 50567
1482 | 50568
1483 | 50569 | 3/24/2004 | Not Challenging | 01:25:00 |  | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
1484 | 50570 | 6/21/2004 | Undetermined (NC‐PC) |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1485 | 50571 | 7/22/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
1486 | 50572 | 10/8/2003 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
1487 | 50573 | 8/24/2004 | Not Challenging | 08:37:00 | 08:38:00 | Known | 31 | 31 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Power Supply Removed，Self‐extinguished (no plant staff intervention)
1488 | 50574 | 9/16/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1489 | 50575 | 9/14/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1490 | 50576 | 9/17/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: Dry Chemical
1491 | 50577 | 10/23/2004 | Not Challenging | 00:00:00 |  | Estimated | 0 | 0 | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
1492 | 50578 | 11/23/2004 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention)
1493 | 50579 | 5/4/2005 | Not Challenging |  |  | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
1494 | 50580 | 10/9/2004 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1495 | 50581 | 6/24/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
1496 | 50582 | 8/22/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
1497 | 50583 | 9/3/2005 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1498 | 50584 | 6/27/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1499 | 50585 | 10/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1500 | 50586 | 9/28/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
1501 | 50587 | 2/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1502 | 50588 | 2/4/2006 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
1503 | 50589 | 4/15/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed by maintenance staff (craft activity required)
1504 | 50590 | 5/6/2006 | Not Challenging | 05:50:00 |  | Known | 5 | 5 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
1505 | 50591 | 5/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1506 | 50592 | 7/11/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1507 | 50593 | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1508 | 50594 | 10/5/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Plant area did not have installed detection capability | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1509 | 50595 | 10/28/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Plant area did not have installed detection capability | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1510 | 50596 | 1/5/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1511 | 50597 | 12/18/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1512 | 50598 | 3/10/2008 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed by maintenance staff (craft activity required)
1513 | 50599 | 3/31/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1514 | 50600 | 12/2/2008 | Not Challenging |  |  | Estimated | 18 | 18 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required)
1515 | 50601 | 8/30/2009 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1516 | 50602
1517 | 50603 | 2/24/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1518 | 50604 | 11/27/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1519 | 50605 | 10/4/2009 | Not Challenging |  | 23:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
1520 | 50606 | 10/8/2001 | Not Challenging |  | 04:30:00 | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1521 | 50607 | 3/1/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1522 | 50608 | 5/28/1997 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1523 | 50609 | 11/23/2000 | Not Evaluated |  |  | Estimated | 0 | 0 | Smoke detector | Unknown | Self‐extinguished (no plant staff intervention)
1524 | 50610 | 5/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1525 | 50611 | 3/19/2008 | Not Challenging | 13:07:00 | 13:07:00 | Known | 1 | 1 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1526 | 50612 | 10/21/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1527 | 50613 | 7/3/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1528 | 50614 | 3/9/2004 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Fuel supply removed (simple manual action e.g. valve turn off)
1529 | 50615 | 3/11/2004 | Not Evaluated |  | 17:30:00 | Estimated | 0 | 0 | Dedicated Fire Watch | Unknown | Unknown
1530 | 50616 | 3/21/2004 | Not Evaluated |  | 03:00:00 | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
1531 | 50617 | 3/29/2005 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1532 | 50618 | 9/14/2005 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Power supply removed by maintenance staff (craft activity required)
1533 | 50619 | 2/8/2006 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1534 | 50620 | 3/27/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1535 | 50621 | 9/11/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1536 | 50622 | 11/8/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1537 | 50623 | 12/15/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1538 | 50624 | 5/14/2003 | Not Challenging |  |  | Estimated | 10 | 10 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed by maintenance staff (craft activity required)
1539 | 50625 | 1/8/2001 | Not Challenging |  | 12:03:00 | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Unknown
1540 | 50626
1541 | 50627 | 3/24/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1542 | 50628 | 3/9/2000 | Not Challenging |  |  | Unknown | 0 | 0 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1543 | 50629 | 10/16/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1544 | 50630 | 10/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1545 | 50631 | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1546 | 50632 | 10/27/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1547 | 50633 | 11/12/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1548 | 50634 | 3/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Self‐extinguished (no plant staff intervention)
1549 | 50635 | 12/12/2000 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1550 | 50636 | 2/10/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1551 | 50637 | 4/18/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1552 | 50638 | 5/14/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1553 | 50639 | 11/10/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1554 | 50640 | 12/23/2001 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)，Power supply removed (simple manual action e.g. open circuit breaker)
1555 | 50641 | 3/4/2002 | Not Challenging |  | 18:33:00 | Known | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1556 | 50642 | 4/16/2002 | Not Challenging | 10:30:00 |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off)
1557 | 50643 | 4/18/2002 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
1558 | 50644 | 6/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1559 | 50645 | 12/23/2002 | Not Challenging |  |  | Unknown |  |  | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
1560 | 50646 | 3/7/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
1561 | 50647 | 8/12/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1562 | 50648 | 12/2/2003 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1563 | 50649 | 4/22/2003 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1564 | 50650 | 9/26/2003 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1565 | 50651 | 10/17/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
1566 | 50652 | 3/18/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1567 | 50653 | 10/4/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1568 | 50654 | 9/24/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1569 | 50655 | 12/4/2007 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Smoke detector | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1570 | 50656 | 8/18/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1571 | 50657 | 3/2/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1572 | 50658 | 4/24/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
1573 | 50659 | 8/11/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1574 | 50660 | 9/24/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
1575 | 50661 | 4/25/2001 | Not Evaluated |  |  | Unknown |  |  | Unknown | Unknown | Unknown | Unknown
1576 | 50662 | 6/5/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1577 | 50663 | 8/12/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1578 | 50664 | 6/29/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1579 | 50665 | 9/17/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1580 | 50666 | 3/22/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Self‐extinguished (no plant staff intervention)
1581 | 50667 | 3/28/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1582 | 50668 | 4/16/2005 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1583 | 50669 | 1/3/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1584 | 50670 | 10/12/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1585 | 50671 | 10/20/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Unknown | Supervised burn out
1586 | 50672 | 4/5/2002 | Not Evaluated |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1587 | 50673 | 4/5/2002 | Not Evaluated | 09:58:00 | 09:58:00 | Known | 14 | 14 | Other plant personnel (Roving watchstander or passerby) | Unknown | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Dry Chemical
1588 | 50674 | 9/23/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1589 | 50675 | 8/12/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
1590 | 50676 | 11/29/2005 | Not Challenging |  |  | Estimated | 8 | 8 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1591 | 50677 | 9/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Unknown | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1592 | 50678 | 3/28/2006 | Not Challenging | 02:28:00 |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1593 | 50679 | 10/4/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1594 | 50680 | 8/24/2006 | Not Challenging |  | 11:45:00 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required)，Other simple: (e.g. blown out, stamped out; specify in comments)
1595 | 50681 | 11/22/2000 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1596 | 50682 | 4/10/2007 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1597 | 50683 | 5/18/2004 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1598 | 50684 | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1599 | 50685 | 3/30/2007 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
1600 | 50686 | 4/4/2007 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1601 | 50687 | 7/23/2007 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1602 | 50688 | 5/28/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
1603 | 50689 | 10/17/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Unknown | Unknown | Single Portable fire extinguisher，Fuel supply removed (simple manual action e.g. valve turn off)
1604 | 50690 | 10/24/2005 | Not Evaluated | 16:55:00 | 16:55:00 | Known | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher
1605 | 50691 | 2/15/2008 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required)
1606 | 50692 | 3/24/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Fuel supply removed (simple manual action e.g. valve turn off)
1607 | 50693 | 10/13/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1608 | 50694 | 10/24/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1609 | 50695
1610 | 50696 | 4/21/2008 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1611 | 50697 | 7/16/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Other (specify in comments)
1612 | 50698 | 3/17/2009 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1613 | 50699 | 4/7/2000 | Not Challenging |  | 14:25:00 | Estimated | 8 | 8 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Multiple portable fire extinguishers | Portable: Water，Other: Water
1614 | 50700 | 5/13/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Unknown | Portable: Water
1615 | 50701 | 5/24/2000 | Not Challenging |  |  | Estimated |  |  | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Fixed suppression system ‐ deluge (automatic)，Hose stream or hose reel | Other: AFFF foam
1616 | 50702 | 6/25/2000 | Not Challenging |  |  | Unknown |  |  | Smoke detector | Plant area had installed detection which actuated | Unknown
1617 | 50703 | 8/22/2000 | Not Challenging |  |  | Estimated |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
1618 | 50704 | 12/22/2000 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1619 | 50705 | 4/15/2001 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Multiple portable fire extinguishers | Portable: Water
1620 | 50706 | 4/17/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1621 | 50707 | 4/25/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1622 | 50708 | 5/17/2001 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1623 | 50709 | 10/26/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1624 | 50710 | 11/19/2001 | Not Challenging |  |  | Unknown |  |  | Installed Fire detector ‐ Type not specified | Plant area had installed detection which actuated | Unknown
1625 | 50711 | 11/20/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1626 | 50712 | 12/14/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | Other (specify in comments)
1627 | 50713 | 1/1/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1628 | 50714 | 1/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1629 | 50715 | 1/16/2002 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1630 | 50716 | 1/24/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1631 | 50717 | 5/21/2002 | Not Challenging |  |  | Estimated | 13 | 13 | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1632 | 50718 | 3/20/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1633 | 50719 | 8/1/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1634 | 50720 | 8/4/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel，Supervised burn out | Other: Water
1635 | 50721 | 8/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1636 | 50722 | 10/10/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker)
1637 | 50723 | 1/8/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Self‐extinguished (no plant staff intervention)
1638 | 50724 | 3/5/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown
1639 | 50725 | 3/10/2004 | Not Challenging |  |  | Unknown
1640 | 50726 | 10/14/2003 | Not Challenging | 03:15:00 | 03:15:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which actuated | Other simple: (e.g. blown out, stamped out; specify in comments)
1641 | 50727
1642 | 50728 | 1/20/2009 | Potentially Challenging | 19:26:00 | 19:26:00 | Known | 5 | 5 | Roving Firewatch | Unknown | Single Portable fire extinguisher | Portable: CO2
1643 | 50729 | 4/4/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1644 | 50730 | 3/1/2006 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which actuated | Automatic fixed ‐ actuation not specified | Other: Halon
1645 | 50731 | 2/11/2005 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1646 | 50732 | 11/7/2002 | Undetermined (NC‐PC) |  |  | Estimated | 10 | 10 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1647 | 50733 | 4/23/2004 | Undetermined (NC‐PC) |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1648 | 50734
1649 | 50735 | 4/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher | Portable: Dry Chemical
1650 | 50736 | 4/10/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1651 | 50737
1652 | 50738 | 3/13/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Power Supply Removed，Self‐extinguished (no plant staff intervention)
1653 | 50739 | 3/28/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1654 | 50740 | 5/16/2000 | Undetermined (NC‐PC) | 08:16:00 |  | Unknown |  |  | Other plant personnel (Roving watchstander or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1655 | 50741 | 9/18/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Unknown
1656 | 50742 | 10/4/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (Roving watchstander or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1657 | 50743 | 7/17/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1658 | 50744 | 8/3/2001 | Potentially Challenging | 18:25:00 |  | Estimated | 10 | 10 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
1659 | 50745 | 9/22/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1660 | 50746 | 5/6/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Unknown
1661 | 50747 | 2/9/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out; specify in comments)
1662 | 50748 | 9/22/2000 | Not Challenging |  |  | Unknown |  |  | Unknown | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1663 | 50749 | 10/28/2008 | Challenging | 20:10:00 | 20:10:00 | Known | 40 | 40 | Smoke detector | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated
1664 | 50750 | 1/10/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Hose stream or hose reel | Other: Water
1665 | 50751 | 11/17/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1666 | 50752
1667 | 50753 | 12/11/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1668 | 50754 | 1/23/2009 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1669 | 50755
1670 | 50756 | 9/21/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1671 | 50757 | 9/7/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1672 | 50758 | 6/14/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1673 | 50759 | 7/29/2006 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1674 | 50760 | 11/8/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1675 | 50761 | 1/25/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker)
1676 | 50762 | 10/1/2001 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1677 | 50763 | 11/14/2008 | Undetermined (NC‐PC) |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed by maintenance staff (craft activity required)
1678 | 50764 | 1/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1679 | 50765 | 10/12/2004 | Not Challenging |  |  | Unknown |  |  | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1680 | 50766 | 8/18/2000 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
1681 | 50767 | 6/1/2001 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1682 | 50768 | 1/1/2002 | Potentially Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1683 | 50769 | 12/6/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed by maintenance staff (craft activity required)
1684 | 50770 | 1/30/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1685 | 50771 | 5/6/2003 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1686 | 50772 | 7/2/2003 | Challenging | 10:35:00 | 10:35:00 | Known | 215 | 215 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Hose stream or hose reel，Portable manual system (e.g. CO2 cart)，Multiple portable fire extinguishers，Power supply removed by maintenance staff (craft activity required)，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2，Other: Water
1687 | 50773 | 9/11/2003 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1688 | 50774 | 1/7/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
1689 | 50775 | 2/13/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1690 | 50776 | 5/6/2004 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1691 | 50777 | 8/5/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1692 | 50778 | 10/11/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1693 | 50779 | 10/25/2004 | Not Challenging |  |  | Unknown | 0 | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1694 | 50780 | 1/6/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1695 | 50781 | 3/10/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1696 | 50782 | 3/11/2005 | Not Challenging |  | 10:35:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Other simple: (e.g. blown out, stamped out; specify in comments) | Portable: Water
1697 | 50783 | 6/27/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1698 | 50784 | 11/20/2005 | Undetermined (NC‐PC) | 01:53:00 | 01:53:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1699 | 50785 | 12/3/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1700 | 50786 | 3/10/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1701 | 50787 | 1/4/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Water
1702 | 50788 | 3/8/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1703 | 50789 | 3/4/2007 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1704 | 50790 | 6/7/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1705 | 50791 | 10/25/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1706 | 50792 | 11/6/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1707 | 50793 | 11/18/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1708 | 50794 | 3/4/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1709 | 50795 | 7/12/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher
1710 | 50796 | 11/4/2009 | Potentially Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1711 | 50797 | 11/8/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
1712 | 50798 | 12/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
1713 | 50799 | 12/12/2009 | Not Challenging |  |  | Known | 365 | 365 | Other plant personnel (in vicinity or passerby) | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)
1714 | 50800
1715 | 50801
1716 | 50802
1717 | 50803 | 12/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
1718 | 50804 | 1/13/2004 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1719 | 50805 | 2/12/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
1720 | 50806 | 8/30/2004 | Not Challenging |  |  | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1721 | 50807 | 8/24/2007 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1722 | 50808 | 3/21/2006 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
1723 | 50809 | 11/9/2000 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
1724 | 50810 | 6/25/2000 | Not Challenging |  |  | Estimated | 2 | 2 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Single Portable fire extinguisher
1725 | 50811 | 1/9/2001 | Potentially Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
1726 | 50812 | 6/11/2001 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1727 | 50813 | 9/3/2002 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1728 | 50814 | 5/31/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1729 | 50815 | 5/19/2005 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Supervised burn out，Power supply removed (simple manual action e.g. open circuit breaker)
1730 | 50816 | 11/16/2005 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
1731 | 50817 | 2/13/2006 | Not Challenging |  |  | Unknown |  |  | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Air supply cut off (smothered, covered)
1732 | 50818 | 3/21/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other simple: (e.g. blown out, stamped out; specify in comments)
1733 | 50819 | 6/13/2008 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
1734 | 50820 | 10/23/2008 | Potentially Challenging | 16:08:00 | 16:08:00 | Known | 7 | 7 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher，Power supply removed by maintenance staff (craft activity required) | Portable: Dry Chemical
1735 | 50821 | 10/30/2008 | Potentially Challenging | 12:30:00 | 12:45:00 | Known | 33 | 33 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers | Portable: CO2
1736 | 50822 | 11/7/2008 | Not Challenging | 13:04:00 | 13:04:00 | Known | 48 | 48 | Gas Ionization | Plant area had installed detection which actuated | Automatic fixed ‐ smoke detector actuated | Other: Halon
1737 | 50823 | 4/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Self‐extinguished (no plant staff intervention)
1738 | 50824 | 9/13/2009 | Not Challenging |  | 16:20:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1739 | 50825 | 10/1/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1740 | 50826 | 12/9/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g. open circuit breaker)
1741 | 50827 | 4/27/2002 | Not Challenging |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1742 | 50828 | 10/2/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1743 | 50829 | 9/11/2004 | Not Challenging | 00:10:00 | 00:10:00 | Estimated | 45 | 45 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1744 | 50830
1745 | 50831
1746 | 50832
1747 | 50833 | 9/23/2008 | Potentially Challenging |  | 04:42:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1748 | 50834 | 9/24/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Self‐extinguished (no plant staff intervention)
1749 | 50835 | 10/1/2009 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Air supply cut off (smothered, covered)
1750 | 50836
1751 | 50837 | 7/9/2001 | Not Evaluated | 17:15:00 | 17:15:00 | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1752 | 50838 | 11/19/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
1753 | 50839 | 11/26/2001 | Not Evaluated |  |  | Unknown |  |  | Dedicated Fire Watch | Unknown | Unknown
1754 | 50840 | 11/28/2001 | Not Evaluated |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1755 | 50841 | 11/29/2001 | Not Evaluated |  |  | Estimated | 2 | 2 | Roving Firewatch | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
1756 | 50842 | 8/23/2002 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1757 | 50843 | 3/22/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
1758 | 50844 | 7/24/2003 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1759 | 50845 | 12/13/2003 | Not Evaluated |  |  | Unknown |  |  | Staff conducting test/maintenance on equipment of fire origin | Unknown | Unknown
1760 | 50846 | 1/24/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Single Portable fire extinguisher
1761 | 50847 | 1/27/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Fire Watch | Unknown | Unknown
1762 | 50848 | 1/30/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1763 | 50849 | 3/8/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1764 | 50850 | 4/1/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1765 | 50851 | 4/27/2005 | Not Evaluated | 09:41:00 | 09:41:00 | Known | 6 | 6 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker) | Portable: CO2
1766 | 50852 | 5/25/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher，Power supply removed (simple manual action e.g. open circuit breaker)
1767 | 50853 | 11/28/2005 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1768 | 50854 | 9/18/2006 | Not Evaluated |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other simple: (e.g. blown out, stamped out; specify in comments)，Fuel supply removed (simple manual action e.g. valve turn off)
1769 | 50855 | 4/26/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher
1770 | 50856 | 1/31/2008 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1771 | 50857 | 11/6/2009 | Not Evaluated |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
1772 | 50858
1773 | 50859
1774 | 50860 | 12/14/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1775 | 50861 | 12/20/2004 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1776 | 50862 | 2/9/2006 | Not Challenging |  |  | Unknown |  |  | Roving Firewatch | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1777 | 50863 | 9/30/2008 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Other (specify in comments)，Other simple: (e.g. blown out, stamped out; specify in comments)
1778 | 50864 | 9/24/2009 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments)
1779 | 50865 | 1/31/2000 | Not Challenging | 10:05:00 | 10:05:00 | Known | 0 | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1780 | 50866 | 3/28/2001 | Potentially Challenging |  | 06:40:00 | Estimated | 8 | 8 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | Unknown
1781 | 50867 | 10/31/2000 | Not Challenging | 09:45:00 | 09:45:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Single Portable fire extinguisher | Portable: CO2
1782 | 50868 | 7/3/2001 | Not Challenging |  | 21:15:00 | Known | 1289 | 1289 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1783 | 50869 | 10/25/2001 | Not Challenging |  | 16:28:00 | Unknown |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers
1784 | 50870 | 1/8/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Unknown
1785 | 50871 | 1/24/2002 | Potentially Challenging |  | 17:00:00 | Estimated | 13 | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher | Portable: CO2
1786 | 50872 | 3/31/2002 | Not Challenging |  | 02:05:00 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher
1787 | 50873 | 5/9/2002 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Unknown | Self‐extinguished (no plant staff intervention)
1788 | 50874 | 7/12/2002 | Potentially Challenging |  |  | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Unknown | Unknown
1789 | 50875 | 11/10/2002 | Not Challenging |  | 17:35:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher | Portable: Dry Chemical
1790 | 50876 | 11/13/2002 | Potentially Challenging |  | 03:00:00 | Estimated | 25 | 25 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
1791 | 50877
1792 | 50878 | 11/12/2002 | Potentially Challenging |  | 11:56:00 | Estimated | 13 | 13 | Dedicated Fire Watch | Plant area did not have installed detection capability | Unknown
1793 | 50879 | 11/15/2002 | Not Challenging |  | 04:39:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
1794 | 50880 | 11/15/2002 | Not Challenging |  | 10:18:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Unknown
1795 | 50881 | 12/31/2002 | Not Challenging |  | 14:25:00 | Estimated | 25 | 25 | Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Unknown | Unknown
1796 | 50882 | 1/20/2003 | Not Challenging |  | 05:44:00 | Estimated | 2 | 2 | Main control room staff (e.g., control/instrumentation failures) | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1797 | 50883 | 4/18/2003 | Not Challenging |  | 02:25:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Unknown | Single Portable fire extinguisher，Air supply cut off (smothered, covered) | Portable: Dry Chemical
1798 | 50884 | 2/23/2004 | Undetermined (NC‐PC) |  | 17:00:00 | Estimated | 8 | 8 | Smoke detector | Plant area had installed detection which actuated | Hose stream or hose reel | Other: Water
1799 | 50885 | 6/17/2003 | Not Challenging |  |  | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments)
1800 | 50886 | 2/27/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water，Other: Water
1801 | 50887 | 3/7/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Dry Chemical
1802 | 50888 | 7/16/2004 | Not Challenging |  |  | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
1803 | 50889 | 3/22/2005 | Not Challenging |  | 11:32:00 | Estimated | 2 | 2 | Unknown | Unknown | Power supply removed (simple manual action e.g. open circuit breaker)
1804 | 50890 | 4/3/2005 | Not Challenging |  | 02:00:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1805 | 50891 | 4/8/2005 | Not Challenging |  | 10:30:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1806 | 50892 | 4/12/2005 | Not Challenging |  | 12:00:00 | Estimated | 2 | 2 | Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1807 | 50893 | 12/2/2005 | Potentially Challenging |  | 00:05:00 | Estimated | 13 | 13 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
1808 | 50894 | 3/12/2006 | Not Challenging |  | 03:00:00 | Unknown |  |  | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher
1809 | 50895 | 5/13/2007 | Potentially Challenging |  | 03:13:00 | Estimated | 45 | 45 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel | Other: Water
1810 | 50896 | 5/13/2007 | Undetermined (NC‐PC) |  | 16:15:00 | Estimated | 85 | 85 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1811 | 50897 | 12/22/2007 | Not Challenging |  | 09:30:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher
1812 | 50898 | 2/29/2008 | Not Challenging |  | 04:06:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: CO2
1813 | 50899 | 10/27/2008 | Challenging |  | 02:44:00 | Estimated | 2 | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Unknown
1814 | 50900 | 5/1/2009 | Not Challenging |  | 14:22:00 | Estimated | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher | Portable: Water
1815 | 50901 | 8/28/2009 | Not Challenging |  | 11:33:00 | Estimated | 2 | 2 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self‐extinguished (no plant staff intervention)
1816 | 50907 | 1/9/2010 | Potentially Challenging |  | 19:25:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Multiple portable fire extinguishers
1817 | 50908 | 1/20/2010 | Challenging |  | 13:17:00 | 1 |  | 98 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1818 | 50909 | 3/7/2010 | Challenging |  | 11:16:00 | 1 |  | 0 | Installed Fire detector - Type not specified, Plant employee | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1819 | 50910 | 3/28/2010 | Challenging |  | 18:52:00 | 1 |  | 249 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1820 | 50911 | 4/18/2010 | Potentially Challenging |  | 04:00:00 | 2 | 2 | 2 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher Supervised burn out |  |  |  | <5 minutes | Initial Suppression Method Successful
1821 | 50912 | 5/5/2010 | Challenging |  | 09:39:00 | 1 |  | 211 | Thermal detector (e.g., temperature or rate of rise) | Plant area did not have installed detection capability | Automatic fixed - actuation not specified Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1822 | 50913 | 5/12/2010 | Potentially Challenging |  |  | 3 |  | 0 | Plant employee | Unknown | Supervised burn out,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful
1823 | 50914 | 6/8/2010 | Potentially Challenging |  | 11:21:00 | 1 |  | 3 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1824 | 50916 | 7/13/2010 | Potentially Challenging |  | 15:49:00 | 1 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1825 | 50917 | 7/13/2010 | Potentially Challenging |  | 00:46:00 | 1 |  | 24 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1826 | 50919 | 8/22/2010 | Undetermined (PC-CH) |  | 15:29:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Hose stream or hose reel Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1827 | 50921 | 10/11/2010 | Potentially Challenging |  | 08:24:00 | 1 |  | 7 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1828 | 50922 | 11/7/2010 | Challenging |  | 18:38:00 | 3 |  | 1 | Plant employee, Main control room staff (e.g.,control/instrumentation failures), Failed EquipmentA | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic) |  |  |  |  | Initial Suppression Method Successful
1829 | 50923 | 12/19/2010 | Undetermined (NC-PC) |  | 23:51:00 | 1 |  | 45 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1830 | 50925 | 2/8/2011 | Potentially Challenging |  |  | 1 |  | 8 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful
1831 | 50926 | 2/12/2011 | Challenging |  | 12:13:00 | 1 |  | 56 | Smoke detector | Plant area had installed detection which actuated | Other (specify in comments)Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1832 | 50928 | 3/23/2011 | Potentially Challenging |  | 14:00:00 | 1 |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1833 | 50930 | 3/29/2011 | Potentially Challenging |  | 00:56:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1834 | 50931 | 5/1/2011 | Potentially Challenging |  | 02:44:00 | 1 |  | 6 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1835 | 50935 | 6/7/2011 | Challenging |  | 09:30:00 | 1 |  | 223 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Gas Ionization | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1836 | 50936 | 6/25/2011 | Challenging |  | 07:38:00 | 1 |  | 37 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1837 | 50939 | 10/4/2011 | Potentially Challenging |  | 05:55:00 | 1 |  | 6 | Smoke detector | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1838 | 50942 | 11/1/2011 | Potentially Challenging |  | 10:26:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1839 | 50944 | 11/16/2011 | Potentially Challenging |  | 02:14:00 | 1 |  | 19 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1840 | 50945 | 12/21/2011 | Potentially Challenging |  | 10:02:00 | 1 |  | 10 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1841 | 50946 | 1/23/2012 | Potentially Challenging |  | 17:50:00 | 1 |  | 29 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1842 | 50949 | 4/2/2012 | Potentially Challenging |  | 19:29:00 | 1 |  | 49 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful
1843 | 50950 | 5/21/2012 | Undetermined (PC-CH) |  | 14:57:00 | 1 |  | 18 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1844 | 50951 | 5/24/2012 | Undetermined (NC-PC) |  | 13:50:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1845 | 50952 | 6/21/2012 | Potentially Challenging |  | 14:51:00 | 1 |  | 17 | Smoke detector | Plant area had installed detection which actuated | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1846 | 50956 | 10/22/2012 | Challenging |  | 18:46:00 | 1 |  | 22 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1847 | 50968 | 4/18/2012 | Potentially Challenging |  | 13:35:00 | 1 |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1848 | 50969 | 11/11/2012 | Challenging |  | 03:56:00 | 1 |  | 162 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.), Thermal detector (e.g.,temperatur | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful
1849 | 50977 | 1/8/2013 | Challenging |  | 16:40:00 | 1 |  | 16 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated | Automatic fixed - thermally actuated Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful
1850 | 50982 | 12/20/2010 | Challenging |  | 00:45:00 | 1 |  | 15 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful
1851 | 50983 | 9/22/2010 | Challenging |  | 21:35:00 | 1 |  | 19 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful | None
1852 | 50985 | 3/26/2012 | Potentially Challenging |  | 22:45:00 | 1 |  | 58 | Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure
1853 | 50986 | 3/28/2010 | Challenging |  | 18:18:00 | 1 |  | 184 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Hose stream or hose reel,Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful
1854 | 50992 | 11/17/2010 | Potentially Challenging |  | 11:00:00 | 3 |  | 0 | Very early smoke detection system (incipient detection) | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1855 | 50994 | 2/13/2013 | Potentially Challenging |  | 22:05:00 | 1 |  | 2 | Dedicated Fire Watch | Fuel supply removed (simple manual action e.g valve turn off) | [5 empty] | Initial Suppression Method Successful
1856 | 51002 | 11/10/2010 | Not Challenging/Undeter |  | 13:58:00 | 1 |  | 1 | Plant employee | Unknown | Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful
1857 | 51005 | 4/30/2010 | Potentially Challenging |  | 15:35:00 | 1 |  | 4 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) |  |  |  |  | Initial Suppression Method Successful
1858 | 51007 | 1/6/2013 | Potentially Challenging |  | 09:01:00 | 1 |  | 19 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Staff conducting test/maintenance on equipment of fire origin |  |  |  |  | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g.valve turn off) | Initial Suppression Method Successful
1859 | 51013 | 11/29/2010 | Undetermined (NC-PC) |  |  | 3 |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1860 | 51014 | 3/27/2012 | Undetermined (NC-PC) |  | 16:49:00 | 1 |  | 2 | Unknown | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1861 | 51026 | 3/30/2010 | Potentially Challenging |  | 04:20:00 | 1 |  | 6 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1862 | 51027 | 5/24/2010 | Potentially Challenging |  |  | 2 | 2 | 2 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Unknown | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful
1863 | 51032 | 5/2/2010 | Undetermined (NC-PC) |  |  | 1 |  | 525 | Staff conducting test/maintenance on equipment of fire origin | Unknown | [5 empty] | Initial Suppression Method Successful
1864 | 51040 | 4/11/2012 | Challenging |  | 18:10:00 | 1 |  | 37 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1865 | 51044 | 3/11/2010 | Potentially Challenging |  | 12:20:00 | 11 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Initial Suppression Method Successful |  |  |  |  | Initial Suppression Method Successful
1866 | 51048 | 3/24/2010 | Potentially Challenging |  | 01:10:00 | 1 |  | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Fuel Supply Removed,Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1867 | 51051 | 4/6/2011 | Undetermined (NC-PC) |  | 02:07:00 | 1 |  | 0 |  | Unknown | [5 empty] | Initial Suppression Method Successful
1868 | 51057 | 5/2/2011 | Potentially Challenging |  | 09:54:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.gopen circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1869 | 51081 | 12/14/2010 | Potentially Challenging |  | 15:00:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Unknown | Other (specify in comments),Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful
1870 | 51082 | 4/4/2011 | Undetermined (NC-PC) |  | 04:00:00 | 3 |  | 0 | Plant employee | Unknown | Unknown |  |  |  |  | Initial Suppression Method Successful
1871 | 51085 | 4/27/2012 | Potentially Challenging |  | 10:22:00 | 1 |  | 10 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1872 | 51088 | 4/5/2011 | Potentially Challenging |  | 09:39:00 | 1 |  | 10 | Smoke detector, Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1873 | 51090 | 2/15/2013 | Potentially Challenging |  | 08:59:00 | 1 |  | 9 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g. open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1874 | 51092 | 3/20/2013 | Potentially Challenging |  | 02:12:00 | 1 |  | 48 | Smoke detector, Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g. open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1875 | 51093 | 1/17/2013 | Challenging |  | 14:25:00 | 1 |  | 34 | Plant employee, Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Hose stream or hose reel Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1876 | 51109 | 10/15/2010 | Undetermined (NC-PC) |  |  | 3 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Unknown | [5 empty] | Initial Suppression Method Successful
1877 | 51111 | 11/2/2010 | Undetermined (NC-PC) |  |  | 3 |  |  | Other plant personnel (in vicinity or passerby) | Unknown | Unknown |  |  |  |  | Initial Suppression Method Successful
1878 | 51113 | 10/5/2010 | Potentially Challenging |  | 08:50:00 | 1 |  | 5 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1879 | 51117 | 3/11/2013 | Potentially Challenging |  | 14:50:00 | 2 | 2 | 2 | Other plant personnel (in vicinity or passerby), Plan employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful
1880 | 51118 | 4/12/2011 | Potentially Challenging | 15:20:00 |  | 1 | 4 | 4 | Other plant personnel (in vicinity or passerby) | Unknown | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1881 | 51125 | 12/31/2011 | Potentially Challenging |  | 13:25:00 | 1 |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1882 | 51132 | 4/2/2012 | Potentially Challenging |  | 16:03:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1883 | 51135 | 3/12/2013 | Undetermined (NC-PC) |  | 10:55:00 | 1 |  | 10 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1884 | 51136 | 1/19/2011 | Potentially Challenging |  |  | 1 |  | 163 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1885 | 51140 | 11/4/2010 | Potentially Challenging |  | 09:43:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Other simple: (e.g. blown out, stamped out;specify in comments) |  |  |  |  | Initial Suppression Method Successful
1886 | 51146 | 4/3/2013 | Potentially Challenging | 06:32:00 | 07:00:00 | 1 | 20 | 20 | Smoke detector, Failed Equipment Alarm (Tripped pump, Ground, Low Lube Oil etc.) | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1887 | 51152 | 4/11/2013 | Challenging |  | 14:55:00 | 1 |  | 113 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful
1888 | 51153 | 1/28/2010 | Potentially Challenging |  | 17:20:00 | 1 |  | 9 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure | [5 empty] | Initial Suppression Method Successful
1889 | 51154 | 8/2/2012 | Potentially Challenging |  | 03:20:00 | 1 |  | 119 | Plant employee | Plant area did not have installed detection capability | Fuel supply removed (simple manual action e.g valve turn off) |  |  |  |  | Initial Suppression Method Successful
1890 | 51157 | 9/20/2010 | Undetermined (NC-PC) |  | 12:00:00 | 1 |  | 0 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful
1891 | 51158 | 10/4/2012 | Potentially Challenging |  | 04:00:00 | 1 |  | 3 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Air supply cut off (smothered, covered |  |  |  |  | Initial Suppression Method Successful
1892 | 51160 | 9/25/2010 | Challenging |  | 09:35:00 | 1 |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1893 | 51162 | 10/10/2010 | Potentially Challenging |  | 10:00:00 | 3 |  | 0 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1894 | 51164 | 9/19/2011 | Undetermined (NC-PC) |  | 20:00:00 | 3 |  |  | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1895 | 51166 | 6/10/2012 | Potentially Challenging |  | 16:45:00 | 1 |  | 3 | Dedicated Fire Watch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1896 | 51168 | 12/3/2012 | Undetermined (NC-PC) |  | 21:45:00 | 1 |  | 0 | Roving Firewatch | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1897 | 51171 | 7/13/2012 | Potentially Challenging |  | 09:35:00 | 3 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful
1898 | 51172 | 3/21/2013 | Potentially Challenging |  | 11:00:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful
1899 | 51176 | 5/4/2013 | Potentially Challenging |  | 07:43:00 | 1 |  | 7 | Smoke detector | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1900 | 51180 | 5/16/2010 | Potentially Challenging |  | 16:05:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Air supply cut off (smothered, covered |  |  |  |  | Initial Suppression Method Successful
1901 | 51181 | 9/14/2010 | Potentially Challenging |  | 22:22:00 | 3 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1902 | 51184 | 12/2/2011 | 12/2/2011 |  | 13:00:00 | 3 |  | 0 | Dedicated Fire Watch | Plant area did not have installed detection capability | [5 empty] | Initial Suppression Method Successful
1903 | 51186 | 4/20/2013 | Potentially Challenging |  | 10:00:00 | 1 |  | 0 | Dedicated Fire Watch, Other plant personnel (in vicinity or passerby), Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1904 | 51187 | 4/17/2013 | Challenging |  | 20:29:00 | 1 |  | 7 | Main control room staff (e.g.,control/instrumentation failures), Plant employee,Failed Equipment A | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Hose stream or hose reel,Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1905 | 51188 | 5/20/2013 | Undetermined (PC-CH) |  | 03:50:00 | 1 |  | 27 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Multiple portable fire extinguishers |  |  |  |  | Initial Suppression Method Successful
1906 | 51190 | 4/2/2012 | Potentially Challenging |  | 06:24:00 | 1 |  | 9 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1907 | 51191 | 4/27/2013 | Potentially Challenging |  | 10:10:00 | 1 |  | 16 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1908 | 51193 | 5/21/2013 | Potentially Challenging |  | 21:59:00 | 1 |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1909 | 51194 | 7/2/2013 | Challenging |  | 20:26:00 | 1 |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1910 | 51196 | 7/11/2013 | Potentially Challenging |  | 10:29:00 | 2 | 2 | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  | <5 minutes | Initial Suppression Method Successful
1911 | 51199 | 7/26/2013 | Challenging |  | 23:35:00 | 1 |  | 33 | Smoke detector, Other plant personnel (in vicinity or passerby), Failed Equipment Alarm (Tripped pum | Plant area had installed detection which actuated | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1912 | 51201 | : 8/8/2013 | Challenging |  | 03:00:00 | 2 | 2 | 2 | Plant employee, Very early smoke detection system,(incipient detection), Main control room staff (e. | Plant area had installed detection which did not actuate, fire was detected visually or by other means – system failure indicated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  | <5 minutes | Initial Suppression Method Successful
1913 | 51207 | 9/2/2013 | Potentially Challenging |  | 19:22:00 | 2 | 25 | 25 | Other plant personnel (in vicinity or passerby) | Unknown | Multiple portable fire extinguishers |  |  |  | 20 to <30 minu | Initial Suppression Method Successful
1914 | 51209 | 7/31/2013 | Undetermined (NC-PC) |  | 13:02:00 | 1 |  | 0 | Other plant personnel (in vicinity or passerby) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Unknown,Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1915 | 51216 | 1/3/2010 | Potentially Challenging |  |  | 3 |  |  | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1916 | 51219 | 2/12/2010 | Potentially Challenging |  | 02:30:00 | 1 |  | 1 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g.open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1917 | 51220 | 3/26/2010 | Undetermined (NC-PC) |  | 22:45:00 | 1 |  | 25 | Dedicated Fire Watch | Plant area had installed detection which actuated | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1918 | 51221 | 7/20/2011 | Potentially Challenging |  | 13:19:00 | 1 |  | 17 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Other (specify in comments)Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1919 | 51222 | 10/12/2011 | Challenging |  | 05:30:00 | 1 |  | 10 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1920 | 51231 | 4/7/2014 | Undetermined (NC-PC) |  | 09:43:00 | 1 |  | 4 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1921 | 51254 | 10/13/2012 | Potentially Challenging |  | 14:15:00 | 1 |  | 10 | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1922 | 51256 | 6/13/2013 | Undetermined (NC-PC) |  | 14:31:00 | 1 |  | 0 | Main control room staff (e.g.,control/instrumentation failures) | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1923 | 51257 | 5/16/2011 | Potentially Challenging |  | 10:00:00 | 3 |  |  |  | Unknown | [5 empty] | Initial Suppression Method Successful
1924 | 51258 | 7/10/2013 | Challenging |  | 01:00:00 | 1 |  | 60 | Plant employee | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1925 | 51265 | 8/24/2012 | Potentially Challenging |  | 04:50:00 | 1 |  | 1 | Plant employee | Plant area did not have installed detection capability | Other (specify in comments) |  |  |  |  | Initial Suppression Method Successful
1926 | 51273 | 4/2/2013 | Undetermined (NC-PC) |  | 17:07:00 | 1 |  | 0 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1927 | 51274 | 12/9/2012 | Potentially Challenging |  | 05:00:00 | 3 |  |  | Main control room staff (e.g.,control/instrumentation failures) | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1928 | 51276 | 8/14/2013 | Potentially Challenging |  | 16:15:00 | 1 |  | 0 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Self-extinguished (no plant staff intervention) |  |  |  |  | Initial Suppression Method Successful
1929 | 51278 | 11/5/2013 | Challenging |  | 17:48:00 | 1 |  | 42 | Sprinkler or fire-water system flow alarm | Plant area did not have installed detection capability | Automatic fixed - thermally actuated |  |  |  |  | Initial Suppression Method Successful
1930 | 51280 | 12/21/2014 | Potentially Challenging |  | 09:15:00 | 3 |  |  | Plant employee | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1931 | 51287 | 10/6/2013 | Potentially Challenging |  | 16:00:00 | 1 |  | 3 | Staff conducting test/maintenance on equipment of fire origin | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1932 | 51289 | 10/26/2013 | Potentially Challenging |  | 08:15:00 | 1 |  | 6 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1933 | 51291 | 12/9/2013 | Challenging |  | 07:48:00 | 1 |  | 89 | Thermal detector (e.g., temperature or rate of rise) | Plant area had installed detection which actuated | Automatic fixed - thermally actuated,Fixed suppression system - deluge (automatic),Hose stream or hose reel |  |  |  |  | Initial Suppression Method Successful
1934 | 51293 | 11/6/2013 | Potentially Challenging |  | 20:10:00 | 1 |  | 10 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1935 | 51295 | 11/1/2013 | Potentially Challenging |  | 20:56:00 | 1 |  | 134 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | [5 empty] | Initial Suppression Method Successful
1936 | 51296 | 11/30/2013 | Potentially Challenging |  | 13:50:00 | 1 |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1937 | 51304 | 1/18/2014 | Potentially Challenging |  | 03:45:00 | 1 |  | 26 | Installed Fire detector - Type not specified | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1938 | 51308 | 4/7/2012 | Potentially Challenging |  | 08:00:00 | 1 |  | 2 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1939 | 51309 | 3/7/2014 | Potentially Challenging |  | 04:55:00 | 1 |  | 8 | Plant employee | Plant area did not have installed detection capability | Self-extinguished (no plant staff intervention),Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1940 | 51310 | 4/17/2014 | Potentially Challenging |  | 11:00:00 | 1 |  | 2 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1941 | 51315 | 3/20/2014 | Potentially Challenging |  | 14:01:00 | 1 |  | 5 | Plant employee | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1942 | 51316 | 4/12/2014 | Potentially Challenging |  | 22:00:00 | 1 |  | 1 | Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1943 | 51317 | 4/2/2014 | Challenging |  | 12:47:00 | 1 |  | 91 | Sprinkler or fire-water system flow alarm | Plant area had installed detection which actuated | Automatic fixed - thermally actuated |  |  |  |  | Initial Suppression Method Successful
1944 | 51318 | 4/3/2014 | Potentially Challenging |  | 13:55:00 | 1 |  | 1 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1945 | 51322 | 6/19/2014 | Undetermined (NC-PC) |  | 15:26:00 | 1 |  | 0 | Plant employee | Plant area did not have installed detection capability | [5 empty] | Initial Suppression Method Successful
1946 | 51324 | 5/23/2014 | Potentially Challenging |  | 19:41:00 | 1 |  | 13 | Smoke detector | Plant area had installed detection which actuated | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1947 | 51328 | 7/27/2014 | Potentially Challenging |  | 12:44:00 | 1 |  | 15 | Smoke detector | Plant area had installed detection which actuated | [5 empty] | Initial Suppression Method Successful
1948 | 51331 | 9/4/2014 | Potentially Challenging |  | 10:10:00 | 1 |  | 0 | Dedicated Fire Watch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1949 | 51332 | 10/6/2014 | Challenging |  | 13:26:00 | 1 |  | 2 | Staff conducting test/maintenance on equipment of fire origin | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher,Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1950 | 51335 | 9/15/2014 | Potentially Challenging |  | 19:36:00 | 1 |  | 3 | Roving Firewatch | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1951 | 51339 | 9/28/2014 | Potentially Challenging |  | 15:45:00 | 1 |  | 5 | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1952 | 51354 | 3/28/2010 | Potentially Challenging |  | 23:30:00 | 1 |  | 3 | Failed Equipment Alarm (Tripped pump, Ground,Low Lube Oil etc.) | Plant area did not have installed detection capability | Single Portable fire extinguisher |  |  |  |  | Initial Suppression Method Successful
1953 | 51366 | 4/21/2010 | Potentially Challenging |  | 13:47:00 | 1 |  | 10 | Other plant personnel (in vicinity or passerby) | Plant area did not have installed detection capability | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1954 | 51374 | 3/1/2014 | Undetermined (NC-PC) |  |  | 3 |  |  | Plant employee | Plant area had installed detection which did not actuate, fire was detected visually or by other means – no indication of system failure system failure | Power supply removed (simple manual action e.g open circuit breaker) |  |  |  |  | Initial Suppression Method Successful
1955 | 51377 | 12/12/2013 | Potentially Challenging |  | 14:16:00 | 1 |  | 2 | Plant employee | Plant area did not have installed detection capability | Portable manual system(e_g_ CO2 cart) |  |  |  |  | Initial Suppression Method Successful